WATERLINE REVIEW SHEET

| Project Name: |  | PTLog #: |  |
| --- | --- | --- | --- |
| Waterworks Name: |  | PWSID # |  |
| Reviewed By: |  | Date: |  |

| Materials (12VAC5-590-1110)1 |
| --- |
| Pipe Material | Specification | Acceptable1 | Joint Material | Specification | Acceptable1 |
|  |  | Yes No |  |  | Yes No |
|  |  | Yes No |  |  | Yes No |
|  |  | Yes No |  |  | Yes No |

1.  Material must meet AWWA or NSF standards.

Pipe Sizes and Length

| Minimum Pipe Size (12VAC5-590-1120) |
| --- |
| Minimum distribution system pipe size is 4 inches | Yes No |
| 2-inch pipe does not exceed 300 feet | Yes No N/A |
| 3-inch pipe does not exceed 600 feet | Yes No N/A |
| Minimum 6 inch diameter pipe where fire protection is provided | Yes No N/A |
| COMMENTS: |  |

| System Design and Waterline installation (12VAC5-590-1130 & 1220) |
| --- |
| Dead ends minimized by looping | Yes No N/A |
| Blow-offs at dead ends | Yes No N/A |
| Adequate support provided1,2 | Yes No |
| Proper bedding1,3 | Yes No |
| Pressure test specification provided and adequate1 | Yes No |
| Leakage test specification provided and adequate1 | Yes No |
| Adequate cover provided to prevent freezing5 | Yes No |
| Non metallic pipe has provisions for being located | Yes No N/A |
| Meters provided for new service connections6 | Yes No N/A |
| PRVs provided for pressures exceeding 80 psi7 | Yes No N/A |
| COMMENTS: |  |

- See AWWA Standards C600 (DIP) and C605 (PVC). Specifications are to reference either AWWA Standard or manufacturer’s installation procedures.

- i.e. thrust blocks, pipe timber supports, valve supports

- Stones to be removed to a minimum depth of 6” below pipe.

- See AWWA Standards C600 (DIP) and C605 (PVC) for testing procedures and leakage allowances

- A minimum of 3 feet of cover is typical in Virginia.

- Recommendation until adoption of revised Waterworks Regulations.

- Recommendation for distribution system, however, pressures may be higher for some waterworks. Please note, USBC requires PRV for building connections exceeding 80 psi.

| Separation of water mains and sanitary sewers (12VAC5-590-1130) |
| --- |
| 10 feet horizontal separation from sanitary sewers, manholes, septic tanks, and drainfields provided1 | Yes No N/A |
| 18 inch vertical separation provided; sewer under water2 | Yes No N/A |
| If sewer crossing over waterline, 18 inch vertical separation provided2 | Yes No N/A |
| COMMENTS: |  |

- If 10 feet horizontal cannot provided, then sewer shall be constructed to pressure-rated (force main or AWWA water line) standards. No water pipe shall pass through or come into contact with a manhole.

- If 18” vertical separation cannot provided, then sewer must be constructed to pressure-rated (force main or AWWA water line) standards, and pressure tested in place without leakage.

| Valves, air relief, meter, blowoff chambers, and hydrants (12VAC5-590-1160 & 1170) |
| --- |
| Chamber, pit, blowoffs, air relief valves have acceptable drainage1 | Yes No N/A |
| Air relief valve provided 2 | Yes No N/A |
| Air/vacuum/combination release valves installed appropriately3 | Yes No N/A |
| Fire hydrants and blowoff valves adequately drained4 | Yes No N/A |
| COMMENTS: |  |

- Where water table is high, sump pump may be needed.

- Recommendation for air relief pipe to extend one foot above grade (may be impractical), or the chamber be   vented, or else the valve be manually operated in high groundwater areas.

- Installed at a) pipeline high points, b) significant grade changes, c) minimum ½ mile intervals on long ascending or descending lines, d) upgradient from blowoffs & drains per WM 782 recommendations.

- Weep holes to be provided only when hydrants are located above the high water table.

| Surface Water Crossing (12VAC5-590-1180) |
| --- |
| Water mains crossing above water bodies are: a) adequately supported and accessible b) protected from freezing, c) above 100 year flood level | Yes No N/A |
| Water mains crossing under water bodies are: a) provided with flexible watertight joints b) Valves are provided at both ends of the water crossing c) Sample taps are provided at both ends of the water crossing d) Permanent taps provided for testing and locating leaks | Yes No N/A |
| COMMENTS: |  |

| Water Main Disinfection and Testing (12VAC5-590-1180)1 |
| --- |
| All water mains are disinfected prior to being placed in service | Yes No |
| Disinfection method specified | Yes No |
| All mains flushed prior to disinfection @ minimum 3.0 fps, with valves operated | Yes No |
| Acceptable methods of chlorine application, chlorine dosage, and contact times specified | Yes No |
| Final flushing following disinfection and satisfactory disposal of the highly chlorinated water specified | Yes No |
| Bacteriological testing following disinfection specified | Yes No |
| Minimum of two samples collected 16 hours apart at 1,200 ft intervals2 | Yes No |
| If AWWA referenced as disinfection specification, contractor to maintain a copy of the referenced specification on the job site | Yes No N/A |
| COMMENTS: |  |

- See AWWA Standard C651-14 and WM 918.

- Waterworks Regulations requirement of min 2,000 ft intervals is allowable until regulations are revised.

| Hydraulic Model (12VAC5-590-1200)1 |
| --- |
| Summary and certification submitted and acceptable2 | Yes No N/A |
| Model covers the scope of project and design basis is appropriate | Yes No N/A |
| Effective storage is determined correctly | Yes No N/A |
| Minimum pressures are met during max day +fire flow | Yes No N/A |
| COMMENTS: |  |

1. 20 psi shall be maintained under all flow conditions.

2. Spot check for consistency between the report and the Summary.

Comments:

Calculations:

(Provide simple calculations on this page, or attach calculations and spreadsheet calculator outputs. Additional calculations may not be necessary if hydraulic model submitted by engineer.)