DRY CHEMICAL FEED SYSTEM CHECKLIST

12VAC5-590-860 C

| Project Name: |  |  |  |
| --- | --- | --- | --- |
| Reviewed By: |  | Date: |  |

| GENERAL- HOUSING & SAFETY PROVISIONS |  |
| --- | --- |
| Describe reasons for this treatment: Click or tap here to enter text. |  |
| Chemical name/type: Click or tap here to enter text. |  |
| NSF maximum use level: Click or tap here to enter text. |  |
| Application point (appropriate?): Click or tap here to enter text. | Yes ☐ No ☐ |
| Location of feeders, piping layout, application points: - Feeders close to point of application - Feeders, piping, injectors accessible | Yes ☐ No ☐ Yes ☐ No ☐ |
| Floors impervious, slip-proof, slope > 1/8-in/ft | Yes ☐ No ☐ |
| No direct connection between sewer & drain or overflow | Yes ☐ No ☐ |
| Facilities provided for washing face, gloves, protective equipment | Yes ☐ No ☐ |
| Electrical equipment provided for activated carbon meets National Electric Code for Class II, Division 2, Group F hazardous location requirements, including NEMA enclosures type 3, 3S, 3SX, 3X, 5, 9, 12, 12K, or 13 | Yes ☐ No ☐ N/A ☐ |
| Activated carbon stored away from strong oxidants (ozone, chlorine, permanganate)? | Yes ☐ No ☐ N/A ☐ |
| Space for > 30 day supply (less if local supplier, conditions allow) | Yes ☐ No ☐ N/A ☐ |
| FEED EQUIPMENT |  |
| Where chemical feed is necessary for the treatment of the source water, such as chlorination, coagulation, or other essential processes : - Minimum 2 feeders required - 100% Standby capacity unit, or capacity with largest unit out of service | Yes ☐ No ☐ N/A ☐ Yes ☐ No ☐ N/A ☐ |
| Feeder able to supply chemical at an accurate rate throughout the range of feed at all times. | Yes ☐ No ☐ |
| DRY CHEMICAL FEEDERS: |  |
| Measure chemicals volumetrically or gravimetrically | Yes ☐ No ☐ |
| Volumetric feeders provided with weigh scales considered? | Yes ☐ No ☐ |
| Anti-bridging solution considered if appropriate? | Yes ☐ No ☐ N/A ☐ |
| Effective dissolution in the solution tank? | Yes ☐ No ☐ |
| Gravity feed from solution tank | Yes ☐ No ☐ N/A ☐ |
| Enclosed, fugitive dust emissions prevented - Vacuum / pneumatic equipment or closed conveyors - Special enclosures for empty containers - Exhaust fans & dust filters, bins under neg. pressure | Yes ☐ No ☐ N/A ☐ Yes ☐ No ☐ N/A ☐ Yes ☐ No ☐ N/A ☐ |
| CONTROLS |  |
| Manual or automatic control | Manual ☐ Auto ☐ Both ☐ |
| Manual startup available | Yes ☐ No ☐ |
| If Q not constant, proportional chemical feed | Yes ☐ No ☐ N/A ☐ |
| Automatic controls provided with alarms & recorders | Yes ☐ No ☐ N/A ☐ |
| DISSOLVING TANK (IF INCLUDED) |  |
| Construction material suitable for contents | Yes ☐ No ☐ |
| Continuous agitation of slurries | Yes ☐ No ☐ N/A ☐ |
| SOLUTION, SLURRY FEED LINES |  |
| Cleanable, scale formation & deposition prevented | Yes ☐ No ☐ |
| Freeze protection | Yes ☐ No ☐ |
| Durable; Corrosion resistant/potential reduced | Yes ☐ No ☐ |
| Vacuum relief, air gap, or other device provided to prevent siphoning of chemical | Yes ☐ No ☐ |
| PROCESS WATER SUPPLY FOR DISSOLUTION, DILUTION, TRANSPORT: |  |
| Safe & approved source | Yes ☐ No ☐ N/A ☐ |
| Provide one of the following: Air gap; RPZ; Vacuum relief | Yes ☐ No ☐ N/A ☐ |
| Adequate supply and pressure | Yes ☐ No ☐ N/A ☐ |
| Treated for hardness (where necessary) | Yes ☐ No ☐ N/A ☐ |
| SPECIAL SERVICE |  |
| Fluoride feeders provided with scales and loss-of-weight recorders (12VAC5-590-930 D) | Yes ☐ No ☐ N/A ☐ |

Comments:

Click or tap here to enter text.

Calculations:

Click or tap here to enter text.