PRESSURE STORAGE TANK CHECKLIST

12VAC5-590-1080 and 1082

| Project Name: |  |  |  |
| --- | --- | --- | --- |
| Reviewed By: |  | Date: |  |

| General Information |  |
| --- | --- |
| Type of tank(s): Hydropneumatic ☐ Pre-pressurized Diaphragm or Bladder ☐ |  |
| Materials of construction: |  |
| Complies with state and local laws/regulations for construction of unfired pressure vessels (applies to tanks ≥ 120 gal in volume) | Yes ☐ No ☐ N/A ☐ |
| Tank Dimensions (diameter, straight shell length for tanks ≥ 120 gal) | N/A ☐ |
| Nominal volume: | gallons |
| Effective volume (see ODW Permit Manual section 9.9.4): | gallons |
| Location |  |
| Located above normal ground surface? | Yes ☐ No ☐ |
| Top above 100 year flood elevation? | Yes ☐ No ☐ |
| Piping, pressure gauge, and other appurtenances inside building with climate controls to prevent & freezing? | Yes ☐ No ☐ |
| Adequate access for inspection, removal and replacement? | Yes ☐ No ☐ |
| Appurtenances |  |
| Bypass piping and valves to allow system operation during maintenance? | Yes ☐ No ☐ |
| If the tank is used for 4-log virus contact time, are assurances in place to ensure that contact time is always maintained during operation? Describe:_______________ | Yes ☐ No ☐ N/A ☐ |
| Access manway (Applicable to tanks ≥ 120 gal)? | Yes ☐ No ☐ N/A ☐ |
| Tank drain provided? Erosion protection at discharge (recommended)? Discharge to atmosphere and no cross connections? | Yes ☐ No ☐ Yes ☐ No ☐ N/A ☐ Yes ☐ No ☐ N/A ☐ |
| Pressure gauge provided with adequate range? | Yes ☐ No ☐ |
| Water sight glass (Applicable to tanks ≥ 120 gal)? | Yes ☐ No ☐ N/A ☐ |
| Automatic or manual air blowoff? (tanks ≥ 120 gal, non-bladder/diaphragm type)? | Yes ☐ No ☐ N/A ☐ |
| Pressure relief valve? | Yes ☐ No ☐ |
| Vacuum relief valve (Applicable to tanks ≥ 120 gal)? | Yes ☐ No ☐ N/A ☐ |
| Means to add air? (hydropneumatic only) Compressor uses food grade lubricant? Compressor drain line screened? | Yes ☐ No ☐ N/A ☐ Yes ☐ No ☐ N/A ☐ Yes ☐ No ☐ N/A ☐ |
| Sample tap provided (Applicable to tanks ≥ 120 gal, recommended)? | Yes ☐ No ☐ N/A ☐ |
| Separate inlet/outlet and interior piping to promote turnover (recommended for large pressure tanks)? | Yes ☐ No ☐ N/A ☐ |
| Controls |  |
| Describe controls: Adequate? | Yes ☐ No ☐ N/A ☐ |
| Pump cycle settings: low/cut in: psi high/cut out: psi Adequate? | Yes ☐ No ☐ N/A ☐ |
| Pump cycle time: seconds / minutes Sufficient to prevent short-cycling / overheating of pump per manufacturer recommendations? | Yes ☐ No ☐ N/A ☐ |
| Paints, Coatings, and other Interior Surfaces |  |
| Do interior surfaces (bladder and diaphragm) or paints/coatings (hydropneumatic) meet NSF/ANSI 61, or an approved equivalent requirement (such as FDA), where applicable? For large hydropneumatic tanks: Metal surfaces are protected by paints/coatings? Interior paints/coatings specified (describe): | Yes ☐ No ☐ N/A ☐ Yes ☐ No ☐ N/A ☐ |
| Cleaning and disinfection |  |
| Are adequate plans in place to ensure that the pressure tank will be disinfected? (recommend reference to AWWA C652 for large hydropneumatic tanks, or insurances that bladder/diaphragm tanks will be disinfected with disinfection of waterlines or the well) | Yes ☐ No ☐ N/A ☐ |