Comments on May 2021 Draft of FAST Track to Amend Sewage Handling and Disposal Regulation, 12VAC5-610.  Comments gathered from Sewage Handling and Disposal Regulation Advisory Committee meeting, emails, and VOWRA training event

880.B7 – Regarding height of control panel.

- The 30 to 42 inches from the ground surface is too specific.

- Suggest minimum of 30 inches from ground surface/final grade with no maximum

- Electrical code requires 28 inch minimum heigh from finish grade

- Some manufacturers will void warranty if less than 36 inches.

880.C – Pumps integral to treatment systems.  “Conveyance pumps that are located in units with multiple compartments are not considered integral to the treatment unit”

- Concern that the statement in red does not restrict the use of recirculation pumps that recirculate and discharge (dual purpose

- Intent is that often treatment units are sold with integral pump tanks for final dispersal. Those final dispersal/conveyance pumps are not integral to the treatment process and therefore are not eligible to be considered under this section.

- Consider “Pumps Integral to Treatment Systems including Recirculating/Discharge Combinations:”

800.D.2 – ¼ day emergency storage above high level alarm

- Recirculating media filters can store in the recirculation tank and this option should be considered and allowed.  Should consider also backing up in the upstream septic tank as well.

- Suggestion:  An alternative to quarter day storage can provided elsewhere in the treatment train, however backup into the septic tank is not recommended.  The purpose of the ¼ day storage in the pump tank is to all for flow to continue to accumulate without impacting the function of the septic tank.

950.C – installing below a restriction with treated effluent

- You can already go below a restriction with treated effluent.  This amendment would gain a slight reduction in separation distance.  Too controversial.  Suggest dropping it.

- SHADAC polled – no objection to dropping this modification.  No change to this section and will revert back to original language.

960.F. Alternate New Section – relating to dose volume

- This is for gravity dosing – make that clear.

- General agreement that a max of 6 doses per day is reasonable.

960.J. – Pad Construction

- Need to add minimum gravel depth like we have for trenches

- Is fabric required over gravel and distribution pipe?

- Does the distribution pipe need to be covered with gravel or just sit on top?  Standard pipe like used in trenches w/ holes down?

- Amount of pipe required?  right now the way I see it a 4" distribution pipe gets credit for 3' of dispersal area b/c that is what a gravel trench is.  I don't know what a good number is but 3 may be too small and 9 is probably too much to achieve even-dispersal across the pad.

- Above commenter noted that referenced section should cover, but still thinks there should be a specification on how far from the edge of the pad and how much pipe is required.  Suggests 4 feet of infiltrative surface (on either side) of 4 inch pipe.

- Cover should be 4 inches, not 6 inches.