03/27/2020 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump | Distribution Box | Aggregate Bed | None |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  | 12.2 | 8.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/27/2020 | Jan 1 1900 11:30AM
07/15/2020 |  | RoutineScheduled | 154-07-0109 | Louisa | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 | Approved | EHD - Blue Ridge | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 |  | 04/09/2021 | 03:25 PM
11/23/2020 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump | Drip | Elevated Sand Mound | UV Light |  | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  | 13.33 | 7.180000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 11/23/2020 | Jan 1 1900 12:05PM
01/03/2020 |  | Routine, Scheduled |  | Fluvanna County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Blue Ridge | CLARK, MICHAEL J | 1934000023 | MICHAEL | CLARK |  |  | Septic Tank Only | Septic Tank Only | None | None | None | None |  |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/14/2020 | 03:54 AM
12/30/2020 |  |  | 16-113-005 | Buchanan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 12/30/2020 |  | 37.200000 |  |  | 2.800000 |  |  | Attached to this report |  | BOD: 37.2 TSS: 2.80 SV | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12/30/2020 | Jan 1 1900 7:50AM
03/24/2020 |  | Routine, Scheduled |  | Loudoun County | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Paid | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | None | None | Pump | Manifold | [23 empty] | [Comments]: septic and pump tank need pumped | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 04/12/2020 | 02:21 PM
10/15/2020 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Gravity | Gravity |  | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Inspection of a conventional gravity septic system. The state requires that all conventional septic tanks must be pumped out EVERY 5 years and filed with the state and the county. The septic tank has a concrete riser on the inlet side. There are 2 lines coming in from the house. Both were camera snaked and were clear. The septic tank was pumped out and the conveyance line was camera snaked and was clear. The concrete splitter and both concrete d-boxes were dug up they were 18" under the ground. All 7 header lines were camera snaked and were clear. The drain field was probed and dry. At time of inspection all components that were inspected were in working condition. | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 |  | 04/14/2021 | 04:27 PM
11/17/2020 |  | RoutineScheduled | 88-184-169 | Scott | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Effluent Screens"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
05/13/2020 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Aquarobic Services | 1934000142 | Michael | Blake |  |  | none | none | Pump | Gravity | Mound | Not Applicable |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | Routine inspection. Air pre-filter cleaned. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 07/01/2022 | 10:30 AM
07/30/2020 | Alternative | RoutineScheduled | 128-05-303 | Essex | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Three Rivers |  |  | joel | pinnix | [9 empty] | ["Other"] | [] | [18 empty] | Need to replace riser/lid on septic tank. Need to repair drainfield leak from drip tube. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. |  |  | 12:00 AM
01/22/2020 |  | Routine, Scheduled | 14-183-038 | Russell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Cumberland Plateau | DEEL, DENNY M | 1942001097 | DENNY | DEEL |  |  |  | None | Gravity | Distribution Box | Aggregate Bed | None | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Effluent Screens"] |  | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/05/2020 | Jan 1 1900 5:14PM
04/01/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 | Approved | EHD - Loudoun | SES MidAtlantic LLC | 1942001203 | James | Green | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Dispersal System Operation"] | ["Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. Needs new compressor. Break in Zone 1. | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 |  | 04/15/2021 | 09:00 AM
12/18/2020 |  | Routine/Scheduled |  | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  |  |  | Pump |  |  |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  |  | 8.040000 | 3.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 12/18/2020 | Jan 1 1900 8:30AM
04/10/2020 |  | Routine, Scheduled |  | Albemarle County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Blue Ridge | CLARK, MICHAEL J | 1934000023 | MICHAEL | CLARK |  |  | Septic Tank Only | Septic Tank Only | None | None | None | None |  |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/12/2020 | 05:01 AM
07/22/2020 |  | Follow-Up |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | EcoPod | none | Gravity | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Audible alarm was replaced and the system appears to be functioning as designed. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/27/2021 | 01:26 PM
06/08/2020 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | sale inspection on a conventional pump septic system. the control panel is a demand dose. There is 1 pvc clean out. The pvc sewer line ws camera snaked and was clear. The septic tank was pumped out and the filter was cleaned. (JUST A NOTE the state requires the septic tank on all conventional be pumped out every 5 years and filed with the state and county. Also the filter manufacture recommends the filter be cleaned every 6 months. ) The pump tank, pump, floats and force main. The 7 port plastic d-box was dug up it was 12" under the ground. The 6 header line were camera snaked and were clear. The drain field was probed and dry. At time of inspection all components were in working condition. | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 |  | 04/14/2021 | 04:27 PM
01/21/2020 |  | Routine, Scheduled | 093-03-0098 | Isle of Wight County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Western Tidewater | R & K Septic, Inc. |  | John | Butt, Jr |  |  |  |  | Pump | Distribution Box |  | None |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] |  |  | 5.1 | 7.650000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/21/2020 | Jan 1 1900 2:15PM
09/15/2020 |  | Routine/Scheduled |  | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Western Tidewater | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 500 | Clearstream | None | Pump | Drip | Drip Tubing | None | 450.000000 |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | [17 empty] | Pumped 3 compartment tank empty to effect repairs. System Upgrade - Maintenance Pumped empty by Goodman's Septic. Replaced AquaWorx controls with new Orenco control panel, and float sensors Installed access riser on trash tank side of processing tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 09/16/2020 | Jan 1 1900 7:15AM
07/31/2020 |  | RoutineScheduled |  | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Soils, Inc. | 1942001004 | Markham | Smith | 1.000000 | 2000 | MicroFAST 0.9 |  | Gravity | Gravity | Trenches |  |  | [] | ["Attached Growth Medium","Control Operation","BlowerCompressorAerator Operation","SludgeScum Accumulation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 07/31/2020 | Jan 1 1900 3:00PM
01/28/2020 |  | Routine, Scheduled |  | Mathews County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Three Rivers | MEAGHER, WILLIAM J | 1942001190 | WILLIAM | MEAGHER | 1.000000 | 1000 | Septic Tank Only | Ecoflo | Pump | Distribution Box | Aggregate Trench | None | [22 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/03/2020 | 10:39 AM
07/17/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/14/2021 | 04:27 PM
07/29/2020 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  |  | Drip | Elevated Sand Mound | UV Light |  | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  |  | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 07/29/2020 | Jan 1 1900 9:00AM
02/26/2020 |  | RoutineScheduled | 02-100-1050 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Bundick Well & Pump | 1942001051 | Peter | Duer | 1.000000 | 1000 | Septic Tank | Purflo | Pump | Pressure | Pad | Not Applicable | 450.000000 | ["None"] | ["None"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 06/30/2020 | 01:00 PM
03/05/2020 |  | Routine, Scheduled | SWP-04-557 | Spotsylvania County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Biomicrobics MicroFAST | None | Pump | Drip | Drip Tubing |  |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | [18 empty] | [Comments]: The GeoFlow solenoid for the spin filter is not working and should be replaced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/06/2020 | 02:45 PM
06/24/2020 |  | Routine, Scheduled | 175-18-0067 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Biomicrobics MicroFAST |  |  |  |  | UV Light |  | ["Blower/Compressor/Aerator Operation","Disinfection"] | ["Blower/Compressor/Aerator Operation","Disinfection"] |  | Good | Clear | 6.160000 | 5.590000 | [13 empty] | Pump Amps 9.30 ETM 925 hrs 18 mins Cycles 6563 Septic Sludge 8" Scum 3" ATU Sludge 10" Scum 0 Pump Sludge 2" Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 06/24/2020 | 12:51 PM
06/10/2020 |  | Routine, Scheduled | 175-14-0150 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Puraflo |  |  |  |  | None |  | ["Effluent Screens"] | ["Effluent Screens"] | [18 empty] | Pump Amps 12.06 ETM 472.27 Cycles 39433 Septic Sludge 8" Scum 2" Pump Sludge 1" Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 06/10/2020 | 09:01 AM
10/08/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | SES MidAtlantic LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/15/2021 | 09:00 AM
12/02/2020 |  | RoutineScheduled | 13-197-048 | Wise | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | JET |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Effluent Screens"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
05/12/2020 |  | RoutineScheduled | 175-18-0299 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Prince William | Septic Works LLC | 1942001080 | michael | smith | 1.000000 |  | Orenco Advantex | none | Gravity | Pressure | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/25/2021 | 08:10 AM
06/05/2020 | Alternative | Routine/Scheduled | 151-12-0159 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1250 | Clearstream ATU | None | Pump | Drip | Drip Tubing | None |  |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | Septic Tank Riser was found below grade (which could lead to leaks/dirt intrusion); the Aeration Riser had evidence of dirt/water leaks, and the Floats are near/past their expected life; the Discharge Tank was found in High Level due to a clogged Spin Filter, and returned to Normal Level once the Spin Filter was cleaned, the Discharge Pump & Floats have met/exceeded their expected life, and the Riser had evidence of dirt/water leaks; | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 06/16/2020 | 09:36 AM
01/27/2020 |  | Routine, Scheduled |  | Loudoun County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | None | None | Pump | Manifold | [24 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/02/2020 | 04:43 AM
08/11/2020 |  | RoutineScheduled | 061-16-250 | Fauquier | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 5.000000 |  | Bio Barrier | Bio Barrier | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | ["Control Operation" ,"Distribution Pump Operation"] | NA | [7 empty] | 08/11/2020 |  | 6.000000 |  |  | 1.000000 | 21.910000 |  | Will be sent separately | Inspected | Biweekly inspection and scheduled/ routine effluent sampling. The following samples were collected from the drip pump tank: TKN = .813 mg/L, Nitrite-Nitrate = 21.1. D.O. tested at 5.3 mg/L @ 25.3 * C, and pH at 7.58. D.O. measured just .6 mg/L in the primary septic tank. Surge panel high level count at 14, peak count at 718. Effluent briefly surfaced in zone 2 near manifold during test cycle. Ground too wet to repair. In the past 18 days, an average of 4,387gals/ day at 663.5 gals/ dose (avg.) was pumped to the dripfield for a total of 78,966 gals. | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
02/24/2020 |  | Follow-Up | SD-04-455 | Culpeper County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Biomicrobics MicroFAST | None | Pump |  |  | Chlorine |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | [18 empty] | [Comments]: Replaced defective blower | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/02/2020 | 11:52 AM
08/07/2020 |  | RoutineScheduled | 196-06-082 | Westmoreland | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Distribution Pump Operation" ,"Dispersal System Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | NA | [15 empty] | Will be sent separately | Inspected | We replaced a broken air release valve. We recommend replacing the housing for this valve also. | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 |  | 04/09/2021 | 03:25 PM
04/10/2020 |  | Routine, Scheduled |  | Loudoun County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | None | Pump | Distribution Box | Aggregate Trench | [23 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/12/2020 | 02:21 PM
04/11/2020 |  | RoutineScheduled | SD-99-401 | Culpeper | This AOSS is functioning as designed and in accord | Approved | EHD - Rappahannock-Rapidan | Wastemaster |  | Douglas | Crooks | 2.000000 |  |  | Polishing Sandfilter | Pump |  | discharge | Chlorine |  | [] | [] |  | Low | Clear | 7.800000 |  |  | 1.900000 |  | 04/11/2020 |  | 5.000000 |  |  | 2.200000 |  |  | Attached to this report |  | Functioning as Designed | This AOSS is functioning as designed and in accord |  |  | 12:00 AM
04/10/2020 |  | Routine, Scheduled | 16-160-0003 | Montgomery County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - New River | KING, WILLIAM M, II | 1942001112 | WILLIAM | KING | 2.000000 | 1500 |  | Septic Tank Only | Pump | Distribution Box | Aggregate Trench | None | 200.000000 | ["None"] | ["None"] | [18 empty] | [Comments]: System is working correctly. No sludge - system does not need to be pumped. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/11/2020 | 08:40 AM
09/16/2020 |  | RoutineScheduled | 133 13 0105 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 500 | Delta, DF Series |  | Gravity | Gravity | Trenches |  |  | ["None"] | ["None"] | [18 empty] | 12" of solids in septic tank. Cleaned blower filter. 6" on top of septic tank. Adequate aeration. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 09/24/2020 | 07:03 PM
12/10/2020 |  | Routine/Scheduled | 12-142-0237 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Old Dominion Onsite, Inc. | 1942001549 | Russell | Revis | [9 empty] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump"] | N/A | [17 empty] | Cleaned effluent filter. Flushed manifold. Checked float and pump function. Middle discharge float initially read as "stuck down" but upon inspection corrected itself. System appears to be operating normally. Client reported installation of new well since our last visit, which is located over 100' away from all septic system components. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12/10/2020 | Jan 1 1900 1:10PM
01/20/2020 |  | Routine, Scheduled | 14-142-0073 | Hanover County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chickahominy | SHAW, WILLIAM A, JR. | 1934000449 | WILLIAM | SHAW |  |  | Septic Tank Only | Septic Tank Only | None | None | None | None |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/24/2020 | Jan 1 1900 9:47AM
11/18/2020 |  | RoutineScheduled | 109-88-1110 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1000 |  |  | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | NA | [16 empty] | Inspected | Sludge level-minimal scum-7" sludge in Septic tank - Pump tank 3-4" sludge, Pump Ran when tested. Replaced the cement riser lid on pump tank with plastic lid. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 11/28/2020 | 09:30 AM
08/05/2020 | Alternative | Reportable Incident | 157-10-0226 | Mathews | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | Serviced system. Checked the floats and panel (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. Installed a new sewage pump and new float tree. The UV is not working. Pumped out the pump tank and trash out of the Clearstream tank. The septic tank has over 2' of sludge - no crust. The timer is set to 1 minute every 3 hours. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. |  | 08/05/2020 | 12:00 PM
10/07/2020 |  | RoutineScheduled | 177-11-0009-SWP | Spotsylvania | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Attached Growth Medium"] | ["Attached Growth Medium" ,"Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/09/2021 | 03:25 PM
06/22/2020 |  | RoutineScheduled | 14-142-0192 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Old Dominion Onsite, Inc. | 1942001134 | John | Ewing | 1.000000 | 1000 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 150.000000 |  |  | NA | [9 empty] | 4.000000 | [7 empty] | Sample taken for BOD compliance testing | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 08/01/2020 | Jan 1 1900 1:51PM
11/13/2020 |  | Follow-Up |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Gravity | Gravity |  | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Installed new d-box LCH inspected. Septic system is in working condition at this time | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 |  | 04/14/2021 | 04:27 PM
05/01/2020 |  | Reportable Incident | 033-13-0022-SP | Caroline | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | EcoPod | none | Pump | Gravity | Drip | Not Applicable |  | ["Distribution Pump Operation" ,"Control Operation"] | ["Control Operation" ,"Distribution Pump Operation"] | NA | [15 empty] | Will be sent separately | Inspected | High level alarm, both tanks full into the risers even though though tanks were pumped out yesterday. Heavy rain yesterday is a good indicator that tanks are leaking. Tanks will need pumped out again to inspect for leaks. Alarm bulbs not lit for drip panel or atu panel. Panel would not run a complete test cycle. Unplugged and plugged in X and Y harnesses from the motherboard. Panel then completed 2 cycles, but may have other issues. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
12/11/2020 |  | RoutineScheduled | 154-06-0007 | Louisa | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Blue Ridge | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Recirculation Pump"] | ["Recirculation Pump" ,"Attached Growth Medium"] | NA | [15 empty] | Will be sent separately | Inspected | We recommend replacing the damaged EZ Set riser & lid and repairing the broken cleanout pipe neck to the distribution box. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/09/2021 | 03:25 PM
07/27/2020 |  | RoutineScheduled | {FIPSCode}-STS-23547 | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | ["None"] | ["None"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 07/28/2020 | 12:00 AM
03/24/2020 |  | Routine, Scheduled | 047-18-334 | Culpeper County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Clearstream | None | Gravity | Distribution Box | Aggregate Trench |  |  | ["BlowerCompressorAerator Operation","Level Sensor Operation"] | ["BlowerCompressorAerator Operation","Level Sensor Operation"] |  | YES | YES | [15 empty] | [Comments]: Annual inspection. Recommend pump out by year end. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/01/2020 | 06:33 AM
12/07/2020 |  | Follow-Up | 179-13-0174-SWP | Stafford | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [7 empty] | 12/07/2020 |  | 19.000000 | [5 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
11/24/2020 | Alternative | RoutineScheduled | 171-09-0022 | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Onsite Wastewater Services - May Supply | 1942001627 | Drew | Shull | 1.000000 |  | Biomicrobics MicroFAST | Biomicrobics MicroFAST | Pump | Pressure | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | inspection by Ds | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 05/28/2021 | 05:41 AM
05/14/2020 |  | RoutineScheduled | 2006-143-0252 | Henrico | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Henrico | Stamie E. Lyttle Co. | 1942001470 | Eric | Tambourine | [9 empty] | [] | [] | [19 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 05/17/2020 | 12:00 AM
03/02/2020 |  | Routine, Scheduled | 01-197-416 | Wise County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Lenowisco | DEEL, DENNY M | 1942001097 | DENNY | DEEL |  |  | Norweco Singulair ATU | None | Pump | Distribution Box | Aggregate Bed | None | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation"] |  | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/03/2020 | Jan 1 1900 10:49AM
05/01/2020 |  | RoutineScheduled | 07-142-0176 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | [10 empty] | ["Control Operation","Disinfection","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | NA | [17 empty] | At the time of maintenance, the service expert found that all tanks were found at normal level. All pumps and floats were tested during this visit and were functioning properly. The laterals within the treatment tank were flushed and brushed and the sheets were cleaned during this visit. When inspecting the distribution box, he found that the box was at normal level and functioning properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 05/01/2020 | Jan 1 1900 10:32AM
05/20/2020 |  | Routine, Scheduled | 175-01-0722 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Puraflo |  |  |  |  | None |  | ["Effluent Screens"] | ["Effluent Screens"] | [18 empty] | Pump Amps 11.23 ETM 399.08 Cycles 12280 Septic Sludge 12" Scum 1" Pump Sludge 2" Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 05/20/2020 | 02:00 PM
09/25/2020 |  | Routine/Scheduled | 11-120-0236A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. |  |  | Hoot |  | Pump |  |  |  |  | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 09/25/2020 | Jan 1 1900 10:00AM
03/11/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Biomicrobics MicroFAST |  | Pump |  |  | None |  | ["BlowerCompressorAerator Operation","Control Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation"] |  | Good | Brown | [15 empty] | [Comments]: Pump 1 Amps 9.80 ETM 184h 57m Cycles 38725Pump 2 Amps 10.5 ETM 177h Cycles 39741Water Meter Reading 1941830Septic Sludge 18" Scum 12"Pump Sludge 2" Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/11/2020 | Jan 1 1900 1:57PM
09/16/2020 |  | RoutineScheduled | 139-06-0087 | Greene | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | RCWWS | 1942001335 | Randy | Gray | 1.000000 | 1000 | Puroflo |  | Gravity | Pressure | Trenches |  | 100.000000 | ["None","None"] | [] | [18 empty] | 1050 Garth Road | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 09/22/2020 | 07:03 PM
04/20/2020 |  | Routine/Scheduled |  | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Three Rivers | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | Ecoflo | None | Pump | Distribution Box | Aggregate Trench | None |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | Septic Tank Riser had root intrusion, and the outdated Filter was found broken; Ecoflo Module was found with a large crack/hole, and the Biofilter (peat moss) was deteriorated and had heavy root intrusion; the Floats in the Discharge Tank were near/past their expected life, and the Alarm Light was not functioning; a Seal in the Distribution Box was broken allowing dirt intrusion | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/22/2020 | 4:19PM
09/14/2020 |  | Routine/Scheduled | 196-12-125 | Westmoreland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 3.000000 | 2600 | Clearstream |  | Pump | Distribution Box | Aggregate Bed |  |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 09/14/2020 | 05:00 PM
08/12/2020 |  | RoutineScheduled | 101-02-0288 | Albemarle | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Blue Ridge | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Auxiliary Filter" ,"Attached Growth Medium" ,"BlowerCompressorAerator Operation" ,"SludgeScum Accumulation"] | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Attached Growth Medium"] | NA | [15 empty] | Will be sent separately | Inspected | We recommend pumping the Septic Tank and the Aerobic Treatment Unit due to scum & solids accumulation. We replaced the union on the pump and repaired the broken air line. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/09/2021 | 03:25 PM
11/02/2020 |  | Routine/Scheduled | 19-120-0024AR | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. |  |  | Clearstream |  | Pump |  |  |  |  | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 11/02/2020 | Jan 1 1900 2:00AM
05/25/2020 |  | RoutineScheduled |  | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Soils, Inc. | 1940001392 | Markham | Smith | 2.000000 | 1500 | Mirofast 0.50 in a Hanover 1500 top seam tank | 2 Zones | Pump | Pressure | Drip | UV |  | [] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Distribution Pump Operation","Dispersal System Operation","Control Operation","SludgeScum Accumulation"] | NA | [17 empty] | Recommendation for pumping was done, the client care it. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 07/03/2020 | Jan 1 1900 3:45PM
01/01/2020 |  | Routine, Scheduled | 08-113-148 | Buchanan County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Cumberland Plateau | DEEL, DENNY M | 1942001097 | DENNY | DEEL |  |  |  | Septic Tank Only | None | None | None | None | [11 empty] | 01/01/2020 | [7 empty] | Attached to this report |  | [Lab Comments]: 2020 YEARLY MONITORING RESULTS [Comments]: USING MONITORING DATE TO UPLOAD MONITORING ONLY VENIS File Names: SamanthaLee2020.pdf | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/22/2020 | Jan 1 1900 2:31PM
08/05/2020 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump | Drip | Elevated Sand Mound | UV Light |  | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  |  | 7.000000 | 3.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 08/05/2020 | Jan 1 1900 4:30PM
03/20/2020 |  | Follow-Up |  | Fairfax | This AOSS is functioning as designed and in accord | Approved | EHD - Fairfax | Soils, Inc. | 1942001004 | Markham | Smith | 2.000000 |  |  |  | Pump | Gravity | Trenches |  |  | ["None","None"] | [] | false | Low | [15 empty] | Inspected | Follow up to ensure peat was properly replaced in Puraflo pods | This AOSS is functioning as designed and in accord |  | 05/14/2020 | Jan 1 1900 4:10PM
04/14/2020 |  | Routine, Scheduled |  | Loudoun County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Loudoun | Aquarobic Services | 1934000142 | Michael | Blake |  |  | None | None | Pump | Drip | Drip Tubing |  |  | ["Auxiliary Filter","Control Operation","Level Sensor Operation"] | ["Auxiliary Filter","Control Operation","Level Sensor Operation"] |  | YES | YES | [15 empty] | [Comments]: Dripfield still soft in areas, hard to tell if problematic or due to (frequent) recent rains. Cut grass and removed overgrown weeds. Seeded bare spots and covered with straw. Applied weed-n-feed to remaining area. Will re-evaluate in early May. Cleaned spin filter and replaced air filter. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/18/2020 | 03:54 PM
04/23/2020 |  | Routine/Scheduled | {FIPSCode}-STS-3091 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | Serviced system. Checked the pump, panel, & floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. The septic tank needs pumping as well as the Clearstream. There is visible wetness on the drainfield - need to keep an eye on it - need to promote good drainage around the drainfield. The timer is set to 3 minutes every 2 hours. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 04/23/2020 | Jan 1 1900 12:00PM
03/17/2020 |  | Routine, Scheduled | 107-05-0332 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | INBODEN, TERRY J | 1934000088 | TERRY | INBODEN |  | 1500 | Orenco Advantex | Septic Tank Only | Pump | None | Drip Tubing | None |  | ["None"] | ["None"] | [18 empty] | [Comments]: System functioning in accordance with regulations. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 04/14/2020 | 01:50 PM
07/25/2020 |  | Routine/Scheduled |  | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Ecoflo |  | Pump |  |  | None |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  |  | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 07/25/2020 | Jan 1 1900 1:00PM
05/12/2020 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Aquarobic Services | 1934000142 | Michael | Blake |  |  | none | none | Gravity | Gravity |  | Chlorination |  | ["Auxiliary Filter" ,"Control Operation" ,"Disinfection"] | ["Auxiliary Filter" ,"Control Operation" ,"Disinfection"] | NA | [15 empty] | Will be sent separately | Inspected | Annual inspection. Air pre-filter replaced as maintenance. Pushed blower and pump settings back 1 hour to accommodate homeowner's schedule. Note: chlorinator has been removed and replaced with a UV of engineer's choice. Components list needs updated. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 07/01/2022 | 10:30 AM
08/27/2020 |  | Reportable Incident | 01-190-042 (L) Vick | Surry | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Crater | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 2.000000 | 2000 | None | None | Pump | Manifold | Elevated Sand Mound | None | 600.000000 | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Septic Tank Baffles"] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | Pungent | Discolored | [15 empty] | Pumpout conducted by Goodman's Septic Service. Initial Visit - Alarm condition Primary septic tank - high level - riser access leaking Secondary septic tank - high level - riser access leaking Pump Tank - no access riser present - Alarm box only, no motor controls - piggy back operation Mound walked - no indication of surfacing System pumped to operating level by Goodman's Septic service - Repair / upgrade recomendations made. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 08/28/2020 | Jan 1 1900 3:00PM
02/12/2020 |  | Routine, Scheduled | 800-07-0234 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Western Tidewater | R & K Septic, Inc. |  | John | Butt, Jr |  |  |  |  | Pump |  |  | None |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] |  |  |  | 7.300000 | 3.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/12/2020 | Jan 1 1900 9:00AM
11/09/2020 |  | RoutineScheduled | 061-19-084 | Fauquier | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Annual inspection. Switch was off on blower panel. Turned it back on, no apparent problem. Probably was not off too long as treatment still looked good. Settling around tanks has been mostly filled in, acceptable now. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
12/02/2020 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump | Distribution Box |  | None |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  | 14 | 4.930000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 12/02/2020 | Jan 1 1900 12:30PM
07/21/2020 |  | RoutineScheduled | 179-07-0336-SP | Stafford | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/09/2021 | 03:25 PM
07/15/2020 |  | Follow-Up | S 800-18-0155 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | 7/11/2020 - Owner called due to the alarm going off at night. Need to pump and clean pump tank and flush drainfield. 7/15/2020 - Serviced system. Meet with the pumping company and pump and cleaned out the pump tank and pumped trash out of the Clearstream tank, flushed out the tubing, replaced gauge on pump, set pressures to 30 on the pump and 15 on the return. Draw down test = 702 GPD, but Clearstream was low from cleaning it. Checked the pump, panel, & floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream, changed the filter in the aerator, and changed the mesh screen in the spinfilter. The timer was set at 7 minutes every 2 hours now set at 8 minutes every 2 hours. Could not take initial samples. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 07/15/2020 | Jan 1 1900 12:00PM
12/24/2020 |  | Initial Visit |  | Rockbridge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Central Shenandoah | Onsite Wastewater Services - May Supply | 1942001627 | Drew | Shull |  |  | none | none | Gravity | Gravity |  | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation" ,"Attached Growth Medium"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Attached Growth Medium"] | NO | None | Clear | [13 empty] | Will be sent separately | Inspected | SYSTEM STARTUP COMPLETED ON 12/24/2020 BY DKS, 180 DAY LABS DUE JUNE 2021. ALTERNATIVE SEPTIC O&M IS TO BE CONTINUED ANNUALLY, EVERY DECEMBER. THE NEXT ANNUAL INSPECTION IS DUE DECEMBER 2021. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/01/2022 | 12:13 PM
05/14/2020 |  | RoutineScheduled | 08-165-0101 | Northampton | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | MSA P.C. | 1940001046 | Jason | Fulbright | 1.000000 | 4500 | Septic Tank Only | Delta Environmental Products, DF Series | Pump | Gravity | Trenches | UV |  | [] | [] | YES | Musty | Clear | 7.670000 | 4.800000 |  |  |  | 05/14/2020 | [10 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 07/13/2020 | 12:00 AM
02/03/2020 |  | Routine, Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Chesapeake | R & K Septic, Inc. |  | John | Butt, Jr |  |  | Clearstream ATU |  | Pump | Drip | Elevated Sand Mound | UV Light |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] |  |  | 2.04 | 7.670000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/03/2020 | Jan 1 1900 12:45PM
11/21/2020 |  | RoutineScheduled | 175-09-0136 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Wastemaster Inc |  | Timothy | Jenkins | 2.000000 |  | ATU | Spray Irrigation, Effluent Filter | Pump | Gravity | Discharge | UV |  | [] | [] |  | Musty | Clear | 7.400000 | [14 empty] | No air to ATU. ATU and #1 pump tank require pumping. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12/09/2020 | 01:05 PM
07/02/2020 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Eco Virginia | 1942001235 | William | Poindexter | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Effluent Screens"] | ["Effluent Screens" ,"Control Operation"] | YES | [15 empty] | Will be sent separately | Inspected | Repaired effluent filter replaced bulb | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 |  | 06/03/2021 | 05:53 AM
08/31/2020 |  | RoutineScheduled |  | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - New River | MONTGOMERY SANITATION |  | Tim | Conner |  |  | ECOFLO 1000 GALLONS |  | Pump | Gravity | Trenches | Not Applicable |  | ["on"] | ["on"] | YES | Septic | Clear | [5 empty] | 09/04/2020 | Sample Chamber | [6 empty] | Attached to this report | Inspected | EVERYTHING FUNCTIONING AT THIS TIME. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 09/04/2020 | 12:00 PM
06/18/2020 | Alternative | Routine/Scheduled | 157-09-0111 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | Serviced system. Checked the pump, panel, & floats (ok). Cleaned the filter in the Clearstream and cleaned the filter in the aerator. Changed the diffuser in the Clearstream and changed the mesh screen in the spinfilter. About 18" of sludge - no crust - in the septic tank. The timer is set to 7 minutes every 1 hour. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 06/18/2020 | 12:00 PM
11/24/2020 |  | RoutineScheduled |  | Rockingham | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NO | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/26/2021 | 09:04 AM
03/30/2020 |  | Routine, Scheduled | 06-192-029 | Tazewell County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Cumberland Plateau | DEEL, DENNY M | 1942001097 | DENNY | DEEL |  |  |  | None | Gravity | None | Alternative Discharge | Chlorine | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens"] |  | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/30/2020 | Jan 1 1900 5:07PM
04/23/2020 |  | Routine/Scheduled | 01-120-0522A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesterfield | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1500 | Orenco Advantex | None | Pump | Distribution Box | Aggregate Trench | None |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | [17 empty] | The Recirculation Pump and Floats have exceeded their life expectancy; the Advantex Unit Media Sheets have exceeded their life expectancy; the Discharge Floats have exceeded their life expectancy, and there was a crack found along the Tank's Lid; the Control Panel has exceeded its expected life; | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/27/2020 | Jan 1 1900 12:07PM
11/10/2020 |  | RoutineScheduled | 69140350 | Frederick | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | none | none | Gravity | Gravity |  | Not Applicable |  | ["SludgeScum Accumulation" ,"BlowerCompressorAerator Operation"] | ["SludgeScum Accumulation" ,"BlowerCompressorAerator Operation"] | NA | [7 empty] | 11/10/2020 |  | 512.000000 | [5 empty] | Will be sent separately | Inspected | Lab sample abnormal but educated homeowner and cleaned all tanks to reboot system Replaced cracked dbox lid Shortned Cleanouts | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance |  | 04/26/2021 | 09:04 AM
12/15/2020 |  | RoutineScheduled | 07-184-5002 | Scott |  |  | EHD - Lenowisco | [11 empty] | Chlorination |  |  |  |  | None | Clear | 6.500000 | 8.000000 |  | 0.000000 | [11 empty] | Jeanette Duncan performed this inspection Tank information not found No records of maintenance or monitoring |  |  |  | 12:00 AM
06/09/2020 |  | Routine/Scheduled | 234-13-434 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesapeake | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 2.000000 | 2000 | Clearstream | Clearstream | Pump | Drip | Drip Tubing | UV Light | 900.000000 | ["Disinfection"] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | Musty | Clear | [15 empty] | Dual AOSS present - AOSS #1 - Designed by Renew the Bay - Serviced 06/05/2020 Primary septic tank in higher than normal level due to grade of outlet from tank. Aeration unit in higher than normal level due to grade of outlet - weir serviced. Compressor operating properly - serviced. U.V. disinfection unit shows electrical wiring damage - parts to be ordered. Discharge pump functioning and operating with proper voltage and amperage - pump screen serviced. AOSS #2 - Designed by MSA Engineering - Primary septic tank at normal operating level. Aeration unit functioning as designed. Compressor operating properly - serviced. U.V. disinfection operating properly - serviced. Pump and controls operating properly, pulling proper voltage and amperage. Drip mounds show no indication of surfacing. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 06/10/2020 | Jan 1 1900 3:00PM
01/13/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Biomicrobics MicroFAST |  | Pump | Drip | Drip Tubing | UV Light |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] |  | Good | Good | [15 empty] | [Comments]: Spin filter cleaned.Pump Amps 9.49 ETM 563h 3m Cycles 4388Water Meter Reading 245700Septic Sludge 9" Scum 0ATU Sludge 10" Scum 0Pump Sludge 1" Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/13/2020 | Jan 1 1900 12:56PM
07/23/2020 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump | Drip | Elevated Sand Mound | UV Light |  | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  |  | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 07/23/2020 | Jan 1 1900 9:30AM
04/03/2020 |  | Reportable Incident |  | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU | [6 empty] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation"] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation"] | N/A | [17 empty] | Changed pump and put alarm bulb in | This AOSS should now return to normal function after having provided the above state routine maintenance |  | 04/03/2020 | Jan 1 1900 8:00AM
02/28/2020 |  | RoutineScheduled | 061-STS-21336 | Fauquier | This AOSS is not functioning as designed or in acc | Approved | EHD - Rappahannock-Rapidan | Cloverleaf Environmental | 1942001135 | [11 empty] | ["Attached Growth Medium","Recirculation Pump"] | [] | [18 empty] | Softener discharge had been diverted from system. Flow Eq readings withhin permitted system capacity. Repairs to treatment components have been discussed with HH Staff. Currently obtaining bids to anchor FAST media and replace EZ Treat media (fouled from previous excessive flows) | This AOSS is not functioning as designed or in acc |  | 05/19/2020 | 12:00 AM
10/27/2020 |  | RoutineScheduled | VAG408008 | Rockingham | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance. | Approved | EHD - Central Shenandoah | Valley Soil & Environmental Consulting, LLC | 1942001218 | John | Lam | 1.000000 |  | BioMicrobics FAST model 0.50 | Wetlands | Gravity | Gravity | Discharge | Chlorination | 150.000000 | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | NA | Musty |  | 7.400000 |  |  | 0.000000 | [10 empty] | Inspected | FAST treatment unit: measured 7" of solids in septic tank side of tank and 12" solids in treatment side of tank. Tank may require a pump-out in 2021. Cleaned FAST blower housing and filter; FAST blower: 3.17 amps; added chlorine and de-chlorine tablets in respective tablet feeders; lowered wetlands effluent weir for fall/winter season; no active discharge at time of inspection | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance. |  | 08/16/2021 | 12:00 AM
11/19/2020 |  | RoutineScheduled | 08-197-A9 | Wise | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | Wise Health Dept |  | Rodney | Neece | 1.000000 |  | ATU Jet |  | Gravity | Gravity | Discharge | Chlorination |  |  |  |  | Musty | Discolored |  |  |  |  | unable to check system do to back up of effluent | [11 empty] | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 11/19/2020 | 12:00 AM
04/02/2020 |  | Routine, Scheduled | 13-120-0089A | Chesterfield | This AOSS should now return to normal function after having provided the above stated routine maintenance. | Approved | EHD - Chesterfield | Chapin, Ben |  | Ben | Chapin |  |  | Septic Tank Only | Septic Tank Only | None | None | None | None | [21 empty] | Lab results not reported by Operator, EHS chose "No" in order to allow saving updated entry. VENIS File Names: 19801 Woodpecker Rd-1.jpg | This AOSS should now return to normal function after having provided the above stated routine maintenance. |  | 04/05/2020 | Jan 1 1900 8:25PM
09/09/2020 |  | RoutineScheduled | 113-18-074 | Madison | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Environmental Systems Service | 19420001050 | Troy | Jenkins | 2.000000 | 1500 | Septic Tank | Septic Tank |  | Pressure | Drip |  | 2975.000000 | [] | [] |  |  |  | 7.140000 |  |  |  |  | 09/09/2020 | Sample Tap | 0.000000 |  |  | 1.700000 | 49.290000 |  | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 10/15/2020 | 03:00 PM
04/09/2020 |  | Routine/Scheduled | 17-120-0159AR | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesterfield | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1500 | Orenco Advantex | None | Pump | Distribution Box | Aggregate Trench | None |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | [17 empty] | Advantex Media Sheets had heavy fog; Distribution Box Lid was found broken (repairs approved by owner) | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/09/2020 | Jan 1 1900 5:13PM
09/14/2020 |  | RoutineScheduled | 175-04-0279 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Prince William | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Distribution Pump Operation"] | ["Control Operation" ,"Distribution Pump Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Concrete lid for pump tank has been replaced since last year. Peat is over 15 years old but still appears to be in decent shape. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
09/23/2020 |  | Routine/Scheduled | 12-172-0107A | Powhatan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesterfield | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 10000 | Advanced Septic |  | Gravity | Distribution Box | Aggregate Trench | None | 5000.000000 |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Recirculation Pump","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | Yeasty | Discolored | [15 empty] | Routine service Primary septic tank - requires pumpout within next few months. Supplemental Air - functioning - timer and float sensor operating. Flow Equalization - pumps, float sensors and controls operating. MMBR - Aeration unit serviced - mixing properly. Aeration upflow - mixing properly. Sludge return - operating properly. Cottage lift stations - pumps, float sensors and controls operating properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 10/05/2020 | Jan 1 1900 1:00PM
07/01/2020 |  | RoutineScheduled |  | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 2705051738 | Joshua | Hott |  |  | Septic | Puraflo | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
11/16/2020 |  | RoutineScheduled | 187120063 | Warren | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lord Fairfax | McKim Construction | 1942001330 | Michelle | McKim | 2.000000 | [8 empty] | [] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NA | [18 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12/18/2020 | 12:00 AM
06/03/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Payment | EHD - Loudoun | Great Falls Septic Service, Inc | 1942001301 | Josh | Hott | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/27/2021 | 11:51 AM
10/17/2020 |  | RoutineScheduled | 137-STS-25540 | Orange | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Wastemaster Inc |  | Timothy | Jenkins | 2.000000 |  | ATU |  |  |  | Discharge | Chlorination |  | [] | [] |  | Musty | Clear | 6.900000 | 5.300000 |  | 2.200000 |  | 10/17/2020 |  | 5.000000 |  |  | 2.200000 | [5 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 11/16/2020 | 02:05 PM
03/03/2020 |  | Routine, Scheduled | 109-18-0251 | Bedford County | This AOSS should now return to normal function after having provided the above stated routine maintenance. | Approved | EHD - Central | WAUGH, IAIN C | 1942001512 | IAIN | WAUGH | 2.000000 | 2500 | Septic Tank Only | Orenco Advantex | Pump | Drip | Drip Tubing | None |  | ["Level Sensor Operation"] | ["Level Sensor Operation"] | [18 empty] | [Comments]: System shut down pumps, error read a blockage in Baffle wall. Removed media plates to check. NOPE! Discovered fLoats switches not at proper height adjustment. Reset the Recirc side to 11", 14" and 26" and Discharge side to 17",20" & 23". also reset Trend Data to begin after 2 days use. System should move into normal mode after more usage. | This AOSS should now return to normal function after having provided the above stated routine maintenance. |  | 03/06/2020 | 08:42 PM
11/24/2020 |  | RoutineScheduled | 187080207 | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 2705110225 | Larry | Royston | [9 empty] | ["None"] | ["None"] | YES | [16 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12/05/2020 | 12:00 AM
03/02/2020 |  | Routine, Scheduled |  | Fluvanna County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Blue Ridge | CLARK, MICHAEL J | 1934000023 | MICHAEL | CLARK |  |  | Septic Tank Only | Septic Tank Only | None | None | None | None |  |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/17/2020 | 05:02 AM
09/10/2020 |  | Reportable Incident | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance | Approved | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green | [9 empty] | ["Disinfection"] | ["Disinfection"] | [18 empty] | Installed UV Bulb & head works. | This AOSS should now return to normal function after having provided the above state routine maintenance |  | 09/10/2020 | Jan 1 1900 4:00PM
05/27/2020 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Eco Virginia | 1942001235 | William | Poindexter | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 |  | 06/03/2021 | 05:53 AM
12/08/2020 |  | RoutineScheduled | 2115-06-153 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Wastemaster Inc |  | Timothy | Jenkins | 2.000000 |  | PuraFlo |  | Pump | Gravity | Discharge | Chlorination |  | [] | [] |  | Musty | Clear | 7.000000 |  |  | 2.200000 | [12 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12/16/2020 | 01:55 PM
09/11/2020 |  | Routine/Scheduled | 2017-143-0081 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Henrico | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. |  |  | Clearstream ATU |  | Pump |  |  |  |  | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 09/11/2020 | 03:00 AM
04/08/2020 |  | Follow-Up |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Loudoun | SES MidAtlantic LLC | 1942001203 | James | Green |  |  | EcoPod | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [9 empty] | 93.000000 | [5 empty] | Will be sent separately | Inspected | BOD Sample 04/08/2020 Sample point pump tank Result : 93 | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/15/2021 | 09:00 AM
12/15/2020 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | A inspection was done on a conventional gravity septic system. The state requires that all conventional septic tanks be pumped out every 5 years and filed with the state and the county. There is a clean out near the house. The sewer line was camera snaked and was clear. The septic tank has a plastic riser on it. The tank was pumped out and inspected. The conveyance line was camera snaked and was clear. The 15 port concrete d-box was dug up it was 3 feet under the ground. The 10 header lines were camera snaked and were clear. The drain field was was probed and dry. At time of inspection all components were in working condition. | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 |  | 04/14/2021 | 04:27 PM
01/29/2020 |  | Routine, Scheduled | 09-173-131 | Prince Edward County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Piedmont | Taylor, Penny | 1942001028 | Penny | Taylor | 1.000000 |  | Norweco Singulair ATU | Septic Tank Only | Pump | Distribution Box | Aggregate Trench | None | 450.000000 | ["Effluent Screens"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","SludgeScum Accumulation"] | [18 empty] | [Comments]: recommend that the septic tank will need to be cleaned next year. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/30/2020 | Jan 1 1900 7:04AM
05/15/2020 | Alternative | RoutineScheduled | 128.02.042 | Essex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services |  | joel | pinnix | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
03/25/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Septic and atu need pumped out | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/14/2021 | 04:27 PM
05/29/2020 |  |  | 175-16-0486 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | [9 empty] | ["SludgeScum Accumulation","Level Sensor Operation"] | ["SludgeScum Accumulation"] | [18 empty] | Septic/ATU had 12" sludge and 3" scum ATU had 12" sludge and was pumped out by others 6/11/2020. Pump tank had 2" sludge. Cleaned air filter for blower. Replaced the redundant off float that was stuck on. Pump cnts-3598 ETM-596h 58m Peak-N/A H/L 29 Zone#1-1810 ff-1 Zone#2-1787 ff-1 W/M- 0,204,301 | This AOSS should now return to normal function after having provided the above state routine maintenance. |  |  | 12:00 AM
06/26/2020 |  | RoutineScheduled |  | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Ashleys Septic Service | 1930332 | Shane | Majewski | 1.000000 | 1200 |  |  | Pump | Gravity | Trenches | Not Applicable | 600.000000 | ["None"] | ["None"] | YES | [16 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 07/06/2020 | 12:00 AM
09/16/2020 |  | Follow-Up | 179-14-0091-SWP | Stafford | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation"] | ["Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Panel would not alarm. Replaced motherboard. Tested by lifting alarm float, working correctly. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
12/02/2020 |  | RoutineScheduled | SD-14-431 | Fauquier | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"BlowerCompressorAerator Operation" ,"Control Operation" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | ["BlowerCompressorAerator Operation" ,"Attached Growth Medium" ,"Control Operation" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Septic tank outlet riser @ airline and 2? air grommet leaks, proposal to be sent to homeowner. Pump out of 2 compartment septic tank needed. After pump out run tub for 4 hours. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
10/06/2020 |  | Routine/Scheduled |  | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream |  | Pump | Distribution Box | Aggregate Bed | None |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 10/06/2020 | Jan 1 1900 3:00PM
07/20/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NO | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/28/2021 | 06:02 AM
05/20/2020 |  | RoutineScheduled |  | Augusta | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Effluent Screens" ,"SludgeScum Accumulation" ,"Control Operation" ,"Auxiliary Filter"] | ["Control Operation" ,"Auxiliary Filter" ,"Effluent Screens" ,"SludgeScum Accumulation"] | YES | [7 empty] | 04/01/2020 |  | 5.000000 | [5 empty] | Will be sent separately | Inspected | Pumped Septic tank after properly uncovering and servicing filter. Installed 2 risers Replaced Media in Ecoflo System | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance |  | 04/26/2021 | 09:04 AM
08/13/2020 |  | RoutineScheduled | 18-183-088 | Russell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | ATL SAND |  | Gravity | Gravity | Pad | Not Applicable | 200.000000 | ["Dispersal System Operation","SludgeScum Accumulation"] | ["Dispersal System Operation","SludgeScum Accumulation"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
10/16/2020 |  | Follow-Up | 175-12-0217 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green | [9 empty] | ["Level Sensor (Float) Operation"] | ["Level Sensor (Float) Operation"] | [18 empty] | Replaced (3) control floats. | This AOSS should now return to normal function after having provided the above state routine maintenance |  | 10/16/2020 | 04:00 PM
08/26/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 2.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/27/2021 | 01:26 PM
12/29/2020 |  | RoutineScheduled | 177-STS-87183 | Spotsylvania | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | 90-Day Inspection | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/09/2021 | 03:25 PM
05/09/2020 |  | RoutineScheduled | 153-STS-19068 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Wastemaster | 1965-001817 | Tim | Jenkins | 2.000000 | [5 empty] | Discharge | Chlorination |  | [] | [] |  | Musty | Clear | 6.600000 |  | 55.000000 | 2.200000 | [11 empty] | Cl2 Contact 1in sludge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 05/09/2020 | 11:20 AM
06/16/2020 |  | RoutineScheduled | 154-06-0600 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark | [9 empty] | [] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 04:45 AM
08/03/2020 |  | RoutineScheduled | 182-08-0107 | Rockingham | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Central Shenandoah | Onsite Wastewater Services - May Supply | 1942001022 | Sara | Tusing | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | inspection by ds | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/28/2021 | 05:41 AM
01/16/2020 |  | Routine, Scheduled |  | Lancaster County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Three Rivers | BEASLEY, THOMAS W | 1934000450 | THOMAS | BEASLEY | 2.000000 | 2500 | Microfast | Septic Tank Only | Pump | Distribution Box | Aggregate Trench | None |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [5 empty] | 40.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/16/2020 | 03:30 PM
03/02/2020 |  | Routine, Scheduled | 177-06-0389-SWT | Spotsylvania County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001350 | Mike | Cook | 1.000000 |  | Puraflo | None | Pump | Distribution Box | Aggregate Trench |  |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/06/2020 | 08:26 AM
09/15/2020 |  | RoutineScheduled | 175-05-0325 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | Aquarobic Services | 1934000142 | Michael | Blake |  |  | none | none | Pump | Gravity | Mound | Not Applicable |  | ["Auxiliary Filter" ,"Control Operation"] | ["Auxiliary Filter" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Cleaned the air pre-filter and replaced the pump standby light assembly. Roots observed at tank top seal at inlet end of tank. Groundwater penetration observed at hole in tank wall at inlet end of tank. Three single points of aeration have developed and repair is required. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 07/01/2022 | 10:30 AM
07/07/2020 |  | RoutineScheduled | 179-07-0057-SWP | Stafford | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Attached Growth Medium" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | ["Effluent Screens" ,"Level Sensor Operation" ,"Control Operation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Attached Growth Medium" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | YES | [15 empty] | Will be sent separately | Inspected | Replaced alarm power light on inside panel and filter alarm float. Removed large roots from end of pod that grew through rope holes. Septic tank has roots @ inlet wedge lid. Pump tank has roots @ wedge lid and inlet pipe is full of roots. Conduit has settled on Puraflo panel and pulled out. Proposal to be sent to homeowner for repairs. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
12/17/2020 | Alternative | Routine/Scheduled | 151-04-043 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 1.000000 | 1500 | Microfast |  | Pump | Distribution Box | Aggregate Trench |  |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | [17 empty] | Replaced sewer pump | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12/17/2020 | 05:00 PM
07/09/2020 |  | Routine, Scheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Biomicrobics MicroFAST |  |  |  |  | None |  | ["Blower/Compressor/Aerator Operation"] | ["Blower/Compressor/Aerator Operation"] |  | Good | Clear | [15 empty] | Pump 1 Amps 10.91 ETM 62 hrs 20 mins Cycles 1169 Pump 2 Amps 10.63 ETM 60 hrs 56 mins Cycles 1136 Septic Sludge 12" Scum 4" ATU Sludge 14" Scum 0 Pump Sludge 4" Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 07/09/2020 | Jan 1 1900 1:45PM
03/25/2020 |  | Routine, Scheduled |  | Loudoun County | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Paid | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | None | None | Gravity | [24 empty] | [Comments]: Sale inspection on a conventional septic system. The sewer line is cast iron but appears to be clear. The concrete septic tank has a riser on it and was pumped out. The tank did not have any visible leaks or cracks. The inlet is missing its T and the outlet has a pvc T. There is a small concrete pump tank that was full and will need pumped out to inspect tank. We could not feel a pump in the tank and it looks as though the force main is broken. There was a broken wire near the tank but no electric box. We found no septic control panel and there were no breakers in the house control panel saying the pump was wired up there. The 4 port concrete splitter box was 30 inches in the ground and is in bad condition. There is cast, orangeburg and pvc piping. The 6 port concrete d-box was also 30" under the ground and in bad condition bottom badly deteriorated and the piping coming out is orangeburg. There are 3 concrete drain lines 2 are full of water. At this time this septic system is not in working condition. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 04/12/2020 | 02:21 PM
07/01/2020 |  | RoutineScheduled | 145-05-0031 | Highland | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Central Shenandoah | Onsite Wastewater Services - May Supply | 1942001022 | Sara | Tusing | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | INSPECTION BY DS | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/28/2021 | 05:41 AM
12/28/2020 |  | Reportable Incident | 175-05-0108 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Prince William | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | High level alarm started Christmas day (after big rain previous day). Still in alarm on arrival. Pump, floats, panel working correctly. After running a garden hose on the ground for about 5 minutes, a pretty substantial leak was observed in the top seam of the atu tank near the float switch. Will need resealed during dry weather. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
02/10/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Paid | EHD - Fairfax | MCKIM, STEPHEN E | 1934000043 | STEPHEN | MCKIM |  |  | Septic Tank Only | Septic Tank Only | None | None | None | None |  | ["SludgeScum Accumulation"] | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [18 empty] | [Comments]: Septic atu tank and the pump tank need pumped out | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 02/15/2020 | Jan 1 1900 4:26PM
09/17/2020 |  | Initial Visit | 182-19-0092 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Central Shenandoah | Onsite Wastewater Services - May Supply | 1942001627 | Drew | Shull | 1.000000 |  | Orenco Advantex | none | Pump | Gravity |  | Not Applicable |  |  |  | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | STARTUP COMPLETED ON 09-17-20 BY DKS | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 06/09/2022 | 04:10 PM
07/16/2020 |  | Routine/Scheduled | 86-213 | Clarke | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | POWELLS PLUMBING, INC. | 1942001036 | Kurt | Holthaus | 1.000000 | 1000 |  |  | Pump | Manifold | Aggregate Trench |  | 450.000000 | ["Effluent Screens"] | ["Effluent Screens"] | N/A | [17 empty] | Annual Inspection - Serviced effluent screen(s). | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 07/17/2020 | 12:32 PM
09/18/2020 |  | RoutineScheduled | 109-07-0047 | Bedford | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1000 | Multiflo ATU |  | Gravity | Gravity | Trenches | Not Applicable |  | [] | [] | NA | [16 empty] | Inspected | Sludge levels- 0" Scum layer 1" sludge, Treatment unit under 1", Pump last year, NO aeration, Found warm steaming tank of water,Motor drawing 3.5 amps(spec is 1.8amp max) Found pump had locked up, Disconnected and ordered replacement. New aspirator installed Oct 2 2020 by us. Good Aeration. New Aerator pump has factory warranty 3 yrs from factory date on pump. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 10/03/2020 | 09:30 AM
11/23/2020 |  | RoutineScheduled | SD-95-527 | Fauquier | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Auxiliary Filter" ,"Control Operation"] | ["Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Auxiliary Filter" ,"Control Operation" ,"Dispersal System Operation"] | YES | [15 empty] | Will be sent separately | Inspected | Could only find one ARV. Septic tank & pump tank needs to be pumped out. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
12/01/2020 |  | Routine/Scheduled |  | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | None |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  |  | 7.950000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 12/01/2020 | Jan 1 1900 12:45PM
11/25/2020 |  | RoutineScheduled | 2018-143-0045 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Norweco | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 01/04/2021 | 12:00 AM
11/05/2020 |  | RoutineScheduled | C-122-14-0045 | Craig | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Alleghany-Roanoke | King's Alternative Septic | 1942001112 | William | King, II | 1.000000 | 1000 | Biomicrobics Microfast 0.5 |  | Gravity | Gravity | Trenches | Not Applicable | 250.000000 | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [17 empty] | Cleaned blower filter, system is working correctly. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 11/17/2020 | 12:00 AM
08/18/2020 |  | RoutineScheduled | 187120120 | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 2705110225 | Larry | Royston | [9 empty] | ["None"] | ["None"] | YES | [16 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 08/24/2020 | 12:00 AM
02/27/2020 |  | Routine, Scheduled | 234-18-105 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesapeake | VANHOLTEN, CRAIG S | 1934000053 | CRAIG | VANHOLTEN |  |  | Septic Tank Only | Septic Tank Only | None | None | None | None | [11 empty] | 02/27/2020 |  | 5.000000 |  | 5.000000 |  |  |  | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/27/2020 | Jan 1 1900 8:30AM
06/11/2020 |  | RoutineScheduled | 18-100-0327 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Bundick Well & Pump | 1942001051 | Peter | Duer | 1.000000 | 1500 | Septic Tank | EZ Flow | Pump | Pressure | Trenches | Not Applicable | 600.000000 | ["None"] | ["None"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 07/15/2020 | 12:00 AM
11/17/2020 |  | Reportable Incident | 182-05-0561 | Rockingham | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Pump | Pressure | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation","Effluent Screens"] | ["BlowerCompressorAerator Operation","Effluent Screens"] | YES | Pungent | Cloudy | [15 empty] | replaced and raised blower | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 06/02/2021 | 12:00 AM
06/03/2020 | Alternative | Routine/Scheduled | 196-17-0029 | Westmoreland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | Ecoflo | None | Pump | Distribution Box | Aggregate Trench | None |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | The Filter in the Septic Tank is outdated (we recommend its replacement during your next scheduled pumping service); the Floats in the Pump Chamber have exceeded their life expectancy; | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 06/11/2020 | 04:37 PM
10/23/2020 |  | Routine/Scheduled | 01-120-0771A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesterfield | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1500 | Orenco Advantex |  | Pump | Distribution Box | Aggregate Trench | None | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | None | Clear | [15 empty] | Routine Service Processing Tank - normal operating level - RSV, recir. pump & effluent screen serviced. Treatment Module - media drapes & spray grid serviced. Pump Tank - normal operating level - discharge pump serviced, float sensors & controls operating properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 10/26/2020 | Jan 1 1900 7:15AM
02/14/2020 |  | Reportable Incident |  | Fairfax County | This AOSS should now return to normal function after having provided the above stated routine maintenance. | Paid | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Puraflo | [6 empty] | ["Distribution Pump Operation","Level Sensor Operation"] | ["Distribution Pump Operation","Level Sensor Operation"] | [18 empty] | [Comments]: Installed (2) Z189 effluent pumps & (3) control floats. | This AOSS should now return to normal function after having provided the above stated routine maintenance. |  | 02/14/2020 | Jan 1 1900 9:30AM
02/26/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Fairfax | SEAMON, CHARLIE L | 1942001108 | CHARLIE | SEAMON |  |  | Septic Tank Only | Microfast | Pump | Distribution Box | Aggregate Trench | None |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | [18 empty] | [Comments]: Performance Inspection: Microfast Pump to Drainfield. Septic-7"sludge 2"scum/ATU-8"sludge/ Pump tank-0"sludge. No pump out needed at this time. P1 cnts-773 ETM-27h 1m/ P2 cnts-768 ETM-26h 59m/ Peak-15/High-11/ Blower air filter cleaned. Pumps Zoeller N-98 @ 63.7gpm. No breakout or spongy areas on the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/17/2020 | Jan 1 1900 6:36AM
07/02/2020 |  | Routine, Scheduled | 179-17-0261-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | EZ Treat Sandfilter |  |  |  |  | None |  | ["Effluent Screens"] | ["Effluent Screens"] |  | Good | Clear | [15 empty] | Pump Amps 8.69 Septic Sludge 12" Scum 2" Pump Sludge 6" Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 07/02/2020 | 02:30 PM
07/02/2020 | Alternative | RoutineScheduled | 150-17-0090 | King William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Atlee Sewage Disposal, LLC | 1942001144 | Francis | Frere | 1.000000 | 1250 | Clearstream ATU |  | Pump | Gravity | Trenches | Not Applicable | 600.000000 | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | NA | None | Clear |  |  | 10.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 07/02/2020 | 03:00 PM
09/04/2020 |  | RoutineScheduled | 18-177-1014 | Pulaski | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Southwest Soils, Inc. | 1942001494 | Stephen D. | Dalton | 1.000000 | 1060 Infiltrator | Aqua Safe 500 |  | Gravity | Gravity | Trenches | Not Applicable | 450.000000 | ["None"] | ["SludgeScum Accumulation","BlowerCompressorAerator Operation"] | NA | Musty | Discolored | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 09/04/2020 | 01:20 PM
07/14/2020 |  | RoutineScheduled |  | Augusta | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation" ,"SludgeScum Accumulation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation" ,"SludgeScum Accumulation"] | NA | [7 empty] | 07/14/2020 |  | 18.000000 | [5 empty] | Will be sent separately | Inspected | Treatment tank pumped Lab Sample Normal | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance |  | 04/26/2021 | 09:04 AM
03/09/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Fairfax | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | None | None | Pump | Drip | Drip Tubing |  |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation","Distribution Pump Operation"] | [18 empty] | [Comments]: The pump contactor in the control panel has broken free from its base and should be replaced before it fails. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/06/2020 | Jan 1 1900 2:45PM
01/24/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Orenco Advantex | None | Pump | Distribution Box | Aggregate Trench | [23 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/06/2020 | Jan 1 1900 7:11AM
04/14/2020 |  | Routine, Scheduled | 181-09-0028 | Rockbridge County | This AOSS should now return to normal function after having provided the above stated routine maintenance. | Approved | EHD - Central Shenandoah |  |  |  |  | 1.000000 | 1000 |  | Biomicrobics MicroFAST | Gravity | Distribution Box | Aggregate Trench | None |  | ["None"] | ["None"] | [18 empty] | [Pumpout Comments]: Septic tank pumped and cleaned. [Comments]: Filters checked and cleaned. Control panel functioning properly. No apparent leaks in system or drain field area. System pumped and cleaned. Lids properly secured. | This AOSS should now return to normal function after having provided the above stated routine maintenance. |  | 04/25/2020 | 30-12-1899 07:46 PM
07/17/2020 |  | Follow-Up | 175-05-0628 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green | [9 empty] | ["Blower/Compressor/Aerator Operation"] | ["Blower/Compressor/Aerator Operation"] | [18 empty] | Installed R2103 compressor. | This AOSS should now return to normal function after having provided the above state routine maintenance |  | 07/17/2020 | 04:00 PM
04/07/2020 |  | Routine/Scheduled | {FIPSCode}-STS-2922 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesapeake | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1500 | Orenco Advantex | None | Pump | Distribution Box | Aggregate Trench | None |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/20/2020 | Jan 1 1900 12:16PM
03/13/2020 |  | RoutineScheduled | 107-04-0197 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Onsite Wastewater Services - May Supply | 1942001022 | Sara | Tusing | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Pressure | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 05/28/2021 | 05:41 AM
07/06/2020 |  | RoutineScheduled | 182-05-0238 | Rockingham | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Central Shenandoah | Onsite Wastewater Services - May Supply | 1942001022 | Sara | Tusing | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | INSPECTION BY DS | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/28/2021 | 05:41 AM
09/29/2020 |  | Routine/Scheduled | 159-02-432 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | PremierTech, EFX |  | Pump | None | Aggregate Bed | None | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | Musty | Clear | [15 empty] | Routine Service Primary Septic tank - normal operating level - effluent screen serviced. Pump Basin - normal operating level - pump, float sensors and controls operating properly. Biofilter - peatmoss root filled - raked / turned. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 10/07/2020 | 08:00 AM
12/15/2020 |  | Initial Visit | 17118-0049 | Charles City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | Owner called due to a smell. Serviced system. Checked the pump, panel, & floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream (was broken) and changed the filter in the aerator. The whole yard is wet - have had alot of rain - when it dries out need to keep an eye on the drainfield. Needs a check valve on force main once the ground has dried out. The timer is set to .5 minutes every 2 hours. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12/15/2020 | Jan 1 1900 12:00PM
07/21/2020 |  | Routine/Scheduled | 234-14-120 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | Serviced system. Checked the pump, panel, & floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. The septic tank needs additional risers on it so it can be properly inspected in the future. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 07/21/2020 | Jan 1 1900 12:00PM
10/12/2020 | Alternative | Routine/Scheduled | 151-12-0082 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 2.000000 | 1500 | Clearstream |  | Gravity | Distribution Box | Aggregate Bed |  |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 10/12/2020 | 02:30 PM
03/19/2020 |  | Routine, Scheduled | 12-113-145 | Buchanan County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Cumberland Plateau | DEEL, DENNY M | 1942001097 | DENNY | DEEL |  |  |  | None | Gravity | None | Alternative Discharge | Chlorine | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens","SludgeScum Accumulation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Effluent Screens"] |  | Musty | Clear | [15 empty] | [Comments]: 5 blue crystals, 10 bio max | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/20/2020 | Jan 1 1900 3:04PM
09/28/2020 |  | Follow-Up |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Gravity | Gravity |  | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | iNSTALLED A NEW D-BOX AND INSPECTED AND BACKFILLED. | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 |  | 04/14/2021 | 04:27 PM
12/02/2020 |  | RoutineScheduled | 179-18-0232-SWP | Stafford | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Septic Works LLC | 1942001080 | michael | smith | 1.000000 |  | Orenco Advantex | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/25/2021 | 08:10 AM
09/16/2020 |  | RoutineScheduled | 38352 | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 2705110225 | Larry | Royston | [9 empty] | ["None"] | ["None"] | YES | [16 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 09/23/2020 | 12:00 AM
11/24/2020 |  | Follow-Up |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Gravity | Gravity |  | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | The conveyance line was rerouted for a pool. Install was inspected by AOSE and LCH. | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 |  | 04/14/2021 | 04:27 PM
09/30/2020 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump | Distribution Box | Aggregate Bed | None |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  | 4.11 | 8.400000 | 6.500000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 09/30/2020 | Jan 1 1900 2:30PM
11/24/2020 |  | RoutineScheduled | 14-174-0030 | Prince George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Crater | Lyttle Service Co., LLC dba Stamie E. Lyttle Co | 1942001332 | Benjamin | Chapin | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 11/24/2020 | 12:00 AM
12/22/2020 |  | Routine, Scheduled | 153-STS-20192 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Puraflo |  |  |  |  | None |  | ["Effluent Screens"] | ["Effluent Screens"] | [18 empty] | Pump Amps 12.94 Cycles 35636 Septic Sludge 8" Scum 0 Pump Sludge 0 Scum 0 On 39 secs Off 2hrs | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 12/22/2020 | 11:25 AM
01/24/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Puraflo |  |  |  |  | None |  | ["Effluent Screens"] | ["Effluent Screens"] | [18 empty] | [Comments]: Pump 1 Amps 16.18 ETM 16840 Cycles 18806Pump 2 Amps 15.90 ETM 51483 Cycles 13801Septic Sludge 7" Scum 1"Pump Sludge 1" Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/24/2020 | Jan 1 1900 9:28AM
11/11/2020 |  | Routine/Scheduled | 196-07-098 | Westmoreland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1500 | Microfast |  | Pump | Drip | Drip Tubing | None | 600.000000 |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | Musty | Clear | [15 empty] | Routine Service Trash Tank - normal operating level Aeration - normal operating level - serviced compressor Pump Tank - normal operating level - serviced pump, float sensors and controls operating properly. Drip Headworks - field flushed - drip screen serviced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 11/12/2020 | 08:00 AM
02/28/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS should now return to normal function after having provided the above stated routine maintenance. | Paid | EHD - Fairfax | SEAMON, CHARLIE L | 1942001108 | CHARLIE | SEAMON |  |  | Septic Tank Only | Microfast | Gravity | Distribution Box | Aggregate Trench | None |  | ["Attached Growth Medium","BlowerCompressorAerator Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation"] | [18 empty] | [Comments]: Performance Inspection: Microfast Gravity to Drainfield. Septic-8"sludge 6"scum/ Microfast-12"sludge. Tank requires pump out and media sprayed. Blower air filter cleaned. No breakout or spongy areas on the drainfield. | This AOSS should now return to normal function after having provided the above stated routine maintenance. |  | 03/16/2020 | Jan 1 1900 6:19AM
03/10/2020 |  | Routine, Scheduled | 10-192-121 | Tazewell County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Cumberland Plateau | DEEL, DENNY M | 1942001097 | DENNY | DEEL |  |  |  | None | Gravity | None | Alternative Discharge | UV Light | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Level Sensor Operation"] |  | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/16/2020 | Jan 1 1900 12:37PM
05/19/2020 |  | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | SEAL’S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal | 1.000000 |  | tank only |  | Pump | Pressure | Trenches | Not Applicable |  | [] | ["None"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
01/17/2020 |  | Routine, Scheduled |  | Loudoun County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | Delta Environmental Products, DF Series | None | Gravity | Drip | Drip Tubing | [22 empty] | [Comments]: The pump tank will need pumped out and a new hydrolic lid | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/02/2020 | 04:43 AM
09/09/2020 |  | Follow-Up | ST-04-491 | King George | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Homeowner had Berry Septic pump both tanks 7/9/2020. Resealed pump tank wedge lid. Installed riser on septic tank inlet. Replaced pump. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
08/18/2020 |  | Follow-Up | 154-07-0526 | Louisa | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Blue Ridge | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | EcoPod | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation" ,"Distribution Pump Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation" ,"Distribution Pump Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Verified both tanks had been pumped out. Repaired leak in zone 1 supply line (owner had dug up and removed headworks valve box). Replaced 20" plastic lid on septic inlet. Replaced missing lid on zone 1 arv box. Replaced blower motor and air filter. Installed new brass nipple for tubing going to pressure switch. Reconnected alarm horn and replaced bulb in atu panel so that alarm works correctly. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
04/13/2020 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Eco Virginia | 1942001235 | William | Poindexter | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation" ,"Effluent Screens"] | ["Distribution Pump Operation" ,"Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 |  | 06/03/2021 | 05:53 AM
07/15/2020 |  | RoutineScheduled | SWP-05-414 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump"] | YES | [15 empty] | Will be sent separately | Inspected | Water in the Advantex tank was milky white. If paint has been washed into the tank recently, we recommend pumping the tank. | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 |  | 04/09/2021 | 03:25 PM
11/20/2020 |  | RoutineScheduled | 061-19-092 | Fauquier | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Auxiliary Filter" ,"Attached Growth Medium" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Control Operation" ,"Dispersal System Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Attached Growth Medium" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced O-ring on drip filter #1. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
10/27/2020 |  | Routine, Scheduled | 175-09-0420 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Orenco Advantex |  |  |  |  | None |  | ["Attached Growth Medium","Effluent Screens","Recirculation Pump"] | ["Attached Growth Medium","Effluent Screens","Recirculation Pump"] |  | Acceptable | Good | [15 empty] | Pump Amps 12.04/9.76 Septic Sludge 4" Scum 4" ATU Sludge 2" Scum 0 Pump Sludge 2" Scum 0 On 3 mins 36 secs Off 12 hrs | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 10/27/2020 | 11:16 AM
11/10/2020 |  | RoutineScheduled | 177-17-0074-SWP | Spotsylvania | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Attached Growth Medium" ,"Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | ["Control Operation" ,"Dispersal System Operation" ,"Attached Growth Medium" ,"Auxiliary Filter" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | NA | [7 empty] | 11/10/2020 | [7 empty] | Will be sent separately | Inspected | Z1 drip rate high, same as start-up; no leaks, check valves functioning, zone return valve closed. Owner stated that they got an alarm after last big rain, no stains or active leaks found, we would need to make a site visit after alarm. Tri-check valve is bad, need to cut out and install quality brass check valve, gate valve and union. Repaired broken drip line in zone 2. BOD collected waiting on results. Proposal to be sent to homeowner for repairs. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
12/29/2020 |  | RoutineScheduled | 061-16-250 | Fauquier | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 5.000000 |  | Bio Barrier | Bio Barrier | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Distribution Pump Operation"] | ["Auxiliary Filter"] | NA | Musty | Clear | [13 empty] | Will be sent separately | Inspected | Biweekly inspection. Drip pump #1 still turned off. Waiting on parts (sch 80 3" union). Surge panel peak count at 1161. In the past 15 days, an average of 4,408.3 gals/day at 391.2 gals/dose (avg.) was pumped for a total of 66,125 gallons. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
06/12/2020 |  | Routine/Scheduled |  | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Pump | Distribution Box |  | None |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Recirculation Pump","Sludge/Scum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Recirculation Pump","Sludge/Scum Accumulation"] | N/A |  | 7.9 | 6.840000 | 4.500000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 06/12/2020 | Jan 1 1900 10:00AM
05/21/2020 |  | RoutineScheduled | SD-11260 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Soils, Inc. | 1940001392 | Markham | Smith | 2.000000 | 1500 |  |  | Pump | Gravity | Pad | Not Applicable |  | [] | ["Dispersal System Operation","SludgeScum Accumulation","Level Sensor Operation","Septic Tank Baffles"] | NA | [17 empty] | Septic Tank 3 Scum 8 sludge Pump Tank 0 scum 3 sludge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 07/13/2020 | 03:35 PM
05/28/2020 |  | Routine/Scheduled | 07-120-0631A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesterfield | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1500 | Orenco Advantex | None | Pump | Distribution Box | Aggregate Trench | None | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | None | Clear | [15 empty] | Upon arrival, the Processing Tank was below normal level due to a clogged RSV (which is outdated), and the Recirculation Pump & Floats have exceeded life expectancy; the Discharge Pump & Floats have exceeded life expectancy, and there was ground water leaking around the base of the Discharge Riser 07/28/2020 - Riser leak repaired - new riser installed on discharge tank - replaced aged pump and float sensors - upgraded Recirculating Splitter Valve. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 07/29/2020 | Jan 1 1900 8:15AM
10/28/2020 |  | RoutineScheduled | 154-11-0032 | Louisa | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Blue Ridge | Dominion Septic, Inc | 1942001068 | David | Stewart |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Attached Growth Medium" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Level Sensor Operation"] | ["Control Operation" ,"Attached Growth Medium" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Recirculation Pump"] | YES | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
11/25/2020 |  | Follow-Up |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Gravity | Gravity |  | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Pump tank concrete lid was replaced and the broken force main near the d-box was fixed. At this time septic system is in working condition | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 |  | 04/14/2021 | 04:27 PM
05/13/2020 |  | RoutineScheduled | 187070031 | Warren | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Lord Fairfax | Onsite Wastewater Services - May Supply | 1942001022 | Sara | Tusing | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/28/2021 | 05:41 AM
03/05/2020 |  | Follow-Up | SD-10-208 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | SES Mid Atlantic | 1942001236 | S. Michael | Lynn | 1.000000 | 20000 | EcoPod | EcoPod | Pump | Pressure | Drip | Not Applicable | 7500.000000 | ["Distribution Pump Operation"] | ["Distribution Pump Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/05/2020 | 05:03 PM
04/02/2020 | Alternative |  | 171-07-0177 | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | ["None"] | ["None"] |  | None | Clear | 7.770000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 06/30/2020 | 12:00 AM
04/14/2020 |  | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Greenway Engineering | 1942001008 | Jeremy | Ferguson | 1.000000 | 1500 | Microfast | none | Pump | Pressure | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Level Sensor Operation","SludgeScum Accumulation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 07/21/2020 | 11:50 AM
11/16/2020 |  | RoutineScheduled | 139-05-0021 | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | [6 empty] | Advantex | [6 empty] | ["Attached Growth Medium","Auxiliary Filter","Septic Tank Baffles"] | ["Attached Growth Medium","Auxiliary Filter","Septic Tank Baffles"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 11/16/2020 | 12:00 AM
12/03/2020 |  | Reportable Incident | 14-190-005 | Surry | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Crater | Environmental Services of Virginia | 1942001182 | Steve | Haley | 1.000000 | 450 | CS NC3T |  | Pump | Pressure | Mound | Not Applicable | 100.000000 | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NO | Musty | Clear | [14 empty] | Pumped Out |  | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12/05/2020 | Jan 1 1900 6:30PM
02/13/2020 |  | Routine, Scheduled |  | Prince William County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Aquarobic Mini Plant |  | Pump |  |  | None |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] |  | Good | Good | [15 empty] | [Comments]: Pump Amps 7.16Septic Sludge 1" Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/13/2020 | 04:35 PM
05/13/2020 |  | RoutineScheduled | 159-09-0024 | Middlesex | This AOSS is functioning as designed and in accord | Rejected | EHD - Three Rivers | [13 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accord |  |  | 12:00 AM
05/18/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | EcoPod | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/14/2021 | 04:27 PM
04/22/2020 |  | Routine, Scheduled | 175-18-0447 | Prince William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green | [7 empty] | None |  | ["Blower/Compressor/Aerator Operation","Dispersal System Operation"] | ["Blower/Compressor/Aerator Operation"] |  | Good | Brown | [15 empty] | Sewage surfacing in pad area. Purasyst ATU | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 04/22/2020 | 01:55 PM
02/12/2020 |  | Routine, Scheduled | 093-09-0220 | Isle of Wight County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Western Tidewater | R & K Septic, Inc. |  | John | Butt, Jr |  |  |  |  | Pump | Distribution Box |  | UV Light |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] |  |  | 7.79 | 7.990000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/12/2020 | Jan 1 1900 12:15PM
12/17/2020 |  | Follow-Up | 175-15-0180 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green | [9 empty] | ["Blower/Compressor/Aerator Operation"] | ["Blower/Compressor/Aerator Operation"] | [18 empty] | Installed new Mac80R compressor. | This AOSS should now return to normal function after having provided the above state routine maintenance |  | 12/17/2020 | 04:00 PM
09/24/2020 |  | Reportable Incident | 175-06-0203 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon |  |  | Advantex | [6 empty] | ["Level Sensor Operation","Other"] | ["Level Sensor Operation","Other"] | NA | [17 empty] | Service call: Replaced turbine pump, wide angle float and 2- solenoid valves. Pump start-24586/ Pump run-1955/ Hand-30/ High-20/ Override-20/ Water meter-0670210 | This AOSS should now return to normal function after having provided the above state routine maintenance. |  |  | 12:00 AM
02/19/2020 |  | Routine, Scheduled | 99030405 | Shenandoah | This AOSS should now return to normal function after having provided the above stated routine maintenance. | Approved | EHD - Lord Fairfax | Cubbage, Harrison Lee, II | 1942001021 | Harrison | Cubbage | 1.000000 | 1000 |  | Sandfilter, High rate | Pump | Distribution Box | Aggregate Trench | None |  | ["Auxiliary Filter","Control Operation","Distribution Pump Operation"] | ["Auxiliary Filter","Control Operation","Distribution Pump Operation"] |  | Musty | Clear | [15 empty] | [Comments]: Repaired pump electrical connection Pump Settings: Off 2hrs on 6min Sludge/Scum Accumulations: Septic Tank-6"/2" Pump Tank- 3"/0" | This AOSS should now return to normal function after having provided the above stated routine maintenance. |  | 02/22/2020 | 11:09 AM
06/01/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | SES MidAtlantic LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/15/2021 | 09:00 AM
10/22/2020 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/Maintenance requirements | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Gravity | Gravity |  | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | An inspection on a conventional gravity septic system. The state requires all conventional septic tanks must be pumped out EVERY 5 years and filed with the state and county. There is 1 pvc clean out near the house. The sewer line was camera snaked and was clear. The septic tank was at the proper level with effluent. It has a cover that is over the tank opening but will not stop ground water from getting in. The conveyance line was camera snaked it is part pvc and part corrugated but was clear. There are 2 concrete d-boxes. One was 10" under the ground the other was 2 1/2 feet under the ground. The first d-box is holding effluent but is badly deuterated . All the header lines were camera snaked and were clear. Drain field was probed and dry. At time of inspection the septic system was not in working condition. The septic tank has issue with the lid . | This AOSS is not functioning as designed or in accordance with the performance/Maintenance requirements |  | 04/14/2021 | 04:27 PM
06/18/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | Puraflo | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | The septic tank and first pump tank were high. It appearts that the floats might have been stuck as the alarm did not alert the homeowners. After running the pump and checking the floats the system appears to be functioning as designed. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/27/2021 | 01:26 PM
12/23/2020 |  | Routine/Scheduled | 07-160-0027 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Orenco Advantex |  | Gravity | Distribution Box |  | None |  | ["None"] | ["Control Operation","Level Sensor (Float) Operation","Recirculation Pump","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 12/23/2020 | 12:30 PM
05/21/2020 |  | Initial Visit | 136-14-0373 | Gloucester | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Virginia Septic Solutions LLC | 1942001500 | Justin | Barker | 1.000000 | 600gpd | Clearstream ATU |  | Pump | Pressure | Drip | UV |  | ["BlowerCompressorAerator Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","SludgeScum Accumulation"] | NA | [16 empty] | Pumped Out |  | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 05/29/2020 | 07:45 AM
09/28/2020 |  | RoutineScheduled | 061-16-039 | Fauquier | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Clearstream | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Distribution Pump Operation"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Distribution Pump Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Compressor was not running on arrival. Completed annual inspection. Returned on 10-1 and replaced compressor and the air diffuser. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
04/15/2020 | Alternative | Routine/Scheduled | 157-09-0150 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | Serviced system. Checked the pump, panel, & floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream, changed the filter in the aerator, and changed the mesh screen in the spinfilter. The timer is set to 10.5 minutes every 2 hours. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 04/15/2020 | 12:00 PM
09/22/2020 |  | Routine/Scheduled | 14-174-0090 | Prince George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Crater | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. |  |  | Aqua Klear |  | Pump |  |  |  |  | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 09/22/2020 | Jan 1 1900 12:00PM
04/08/2020 |  | Routine, Scheduled |  | York County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Peninsula | PARSLEY, JAMES MICHAEL | 194001106 | JAMES | PARSLEY | 1.000000 | 1000 | Clearstream | Septic Tank Only | None | Distribution Box | Aggregate Trench | None |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | [18 empty] | [Comments]: Replaced diaphragm in blower | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/27/2020 | Jan 1 1900 3:33PM
09/21/2020 |  | Routine/Scheduled |  | Greene | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Blue Ridge | SES Mid Atlantic | 1942001236 | S. Michael | Lynn | 1.000000 | 10000 | EcoPod |  | Pump | Pressure | Trenches |  | 19100.000000 | ["BlowerCompressorAerator Operation","Recirculation Pump"] | ["BlowerCompressorAerator Operation","Recirculation Pump"] | N/A | Musty | Clear |  | 2.000000 |  |  |  | 09/28/2020 | Sample Tap | [8 empty] | Only influent samples were collected, tech misunderstood. Back down to 363 BOD 22 TSS significant improvement form last quarter | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 10/07/2020 | 05:30 PM
11/28/2020 |  | RoutineScheduled | 109-07-0907 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1500 | Advantex |  | Pump | Gravity | Trenches |  |  | ["None"] | ["None"] | [18 empty] | Annual inspection. Recirculation splitter valve clogged with solids forcing water to discharge tank too soon. This resulted in a lower level in septic tank than normal. Cleaned splitter valve and placed back in service. 10" of solids in septic tank. Flushed treatment unit spray manifold. tested floats, pumps and alarm. cleaned recirculation pump basket filter. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12/10/2020 | 07:03 PM
05/13/2020 |  | Pump-Out Only |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | POWELLS PLUMBING, INC. | 1942001036 | Kurt | Holthaus |  |  | Puraflo | [6 empty] | ["Sludge/Scum Accumulation"] | ["Sludge/Scum Accumulation"] | N/A | [17 empty] | Pumped septic tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 06/19/2020 | 01:52 PM
10/21/2020 |  | RoutineScheduled | 88-184-139 | Scott |  |  | EHD - Lenowisco | [11 empty] | Chlorination |  |  |  |  | None | Clear | 8.500000 | 5.000000 |  | 0.000000 | [11 empty] | Inspection performed by Jeanette Duncan No records of maintenance or monitoring |  |  |  | 12:00 AM
06/23/2020 |  | Routine/Scheduled |  | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  |  |  | Elevated Sand Mound | UV Light |  | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  |  | 6.140000 | 4.500000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 06/23/2020 | Jan 1 1900 9:00AM
06/19/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/27/2021 | 01:26 PM
12/30/2020 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Fairfax | Joe Blevins Equipment Rental, Inc | 2705013926 | Joel | Blevins | 1.000000 | 1500 | .75 Microfast |  | Pump | Gravity | Trenches | Not Applicable |  | ["None"] | ["Other"] | NA | Musty | Cloudy | [5 empty] | 12/30/2020 | Sample Chamber | 8.000000 | [7 empty] | Cleaned the air filter and the ditches are dry. 24' of sludge on treatment side. Took water sample | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
04/14/2020 |  | Routine, Scheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green | [7 empty] | None |  | ["Effluent Screens"] | ["Effluent Screens"] | [18 empty] | Spin filter cleaned. Pump 1 Amps 11.90 Pump 2 Amps 8.10 Water Meter Reading 10375570 Septic Sludge 8" Scum 1" Pump Sludge 3" Scum 1" Concrete casing lid needs replacement. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/14/2020 | Jan 1 1900 8:27AM
09/28/2020 |  | Routine/Scheduled | 03-120-0556A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesterfield | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1500 | Orenco Advantex |  | Pump | Distribution Box | Aggregate Bed | None | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | None | Clear | [15 empty] | Routine service Processing Tank - normal operating level - RSV, recirc pump & effluent screen serviced. Treatment Module - media drapes & spray grid serviced. Pump Tank - discharge pump serviced, float sensors and controls operating properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 10/06/2020 | Jan 1 1900 9:00AM
08/28/2020 |  | Routine/Scheduled | 234-17-243 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | Serviced system. Checked the pump, panel, & floats (ok). Cleaned the filter in the Clearstream and cleaned the UV light bulb. Changed the diffuser in the Clearstream, changed the filter in the aerator, and changed the disc filter. The septic tank needs additional risers on it so it can be properly inspected in the future. The timer is set to 8 minutes every 1.5 hours. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 08/28/2020 | Jan 1 1900 12:00PM
11/05/2020 |  | Routine/Scheduled | 05-174-0018 | Prince George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Crater | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. |  |  | Ecoflo |  | Pump |  |  |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 11/06/2020 | Jan 1 1900 2:00AM
12/11/2020 |  | Routine/Scheduled | 03-172-0334A | Powhatan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesterfield | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1250 | Orenco Advantex | None | Gravity | Distribution Box | Aggregate Trench | None | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | None | Clear | [15 empty] | Routine Service Processing Tank - normal level - RSV, recirc pump, Effluent screen serviced. Treatment Module - media drapes & spray grid serviced. Distribution box - intact - all laterals accepting effluent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 12/14/2020 | Jan 1 1900 7:15AM
11/11/2020 |  | Initial Visit | 550-STS-6321 | Chesapeake | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Chesapeake | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | None | None | Pump | Distribution Box | Aggregate Trench | None | 450.000000 |  | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | [17 empty] | Initial visit - evaluate for surfacing of effluent FOIA filed with Chesapeake County HD Absorption laterals flooded - Free Water encountered at 42" - stabilized after 10 minutes at 18" in boring. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 11/12/2020 | Jan 1 1900 8:15AM
12/18/2020 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001301 | Joshua | Hott | [9 empty] | [] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
09/30/2020 |  | Initial Visit | 179-STS-87705 | Stafford | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Septic Works LLC | 1942001080 | michael | smith | 1.000000 |  | EZ Treat Sandfilter | none | Gravity | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/25/2021 | 08:10 AM
01/17/2020 |  | Routine, Scheduled |  | Loudoun County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim |  |  | Delta Environmental Products, DF Series | None | Pump | Distribution Box | Gravel-Less Trench | [5 empty] | YES | YES | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/02/2020 | 04:43 AM
07/10/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Gravity | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Pump tank needs pumped out | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 |  | 04/14/2021 | 04:27 PM
08/14/2020 |  | RoutineScheduled |  | Rockingham | This AOSS should now return to normal function after having provided the above state routine maintenance | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | none | none | Pump | Gravity |  | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter"] | ["Control Operation" ,"Auxiliary Filter"] | NA | [7 empty] | 08/14/2020 |  | 25.000000 | [5 empty] | Will be sent separately | Inspected | Lab sample normal Repaired alarm Added solution to media to help with drainage | This AOSS should now return to normal function after having provided the above state routine maintenance |  | 04/26/2021 | 09:04 AM
12/23/2020 |  |  | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001301 | Joshua | Hott | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
12/09/2020 |  | Follow-Up | 98-197-A1 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | Wise County Health Dept |  | Rodney | Neece | 1.000000 |  | ATU |  | Gravity | Gravity | Discharge | Chlorination |  |  |  |  | None | [5 empty] | Tablets are now stocked in the chambers. | [11 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12/10/2020 | 12:00 AM
09/01/2020 |  | RoutineScheduled | 181-10-0006 | Rockbridge | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Central Shenandoah | Onsite Wastewater Services - May Supply | 1942001022 | Sara | Tusing | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Inspection DKS | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/28/2021 | 05:41 AM
11/17/2020 |  | Routine/Scheduled |  | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Ecoflo |  | Pump |  |  |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | Installed concrete Eco Flo tank | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 11/17/2020 | Jan 1 1900 11:30AM
05/05/2020 | Alternative | Routine/Scheduled | 136-06-0447 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1250 | Clearstream ATU | None | Pump | Distribution Box | Aggregate Trench | None |  |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | The Septic Tank was found above normal level with heavy sludge/solids; in the Aeration Tank, the Diffuser was found damaged and there were roots infiltrating the Tank from under the Riser; the Floats in the Discharge Tank were not properly secured, and there were roots infiltrating the Discharge Tank around the Forcemain Line; there were roots infiltrating the Distribution Box 08/10/2020 - Distribution box roots removed - replaced damaged diffuser - | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 08/10/2020 | 09:30 AM
12/18/2020 |  |  | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001301 | Joshua | Hott | [9 empty] | [] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
09/29/2020 |  | Routine/Scheduled | 16-120-0491 A conditional | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. |  |  | Orenco Advantex |  | Pump |  |  |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump","Sludge/Scum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump","Sludge/Scum Accumulation"] | N/A | [17 empty] | Still issues with groundwater around unit. System is currently functioning properly. Electrical issues have been resolved. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 09/29/2020 | Jan 1 1900 10:30AM
08/12/2020 |  | Reportable Incident | S 800-14-0011 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | Owner called due to it being water by green tops. Serviced system. Checked the pump, panel, & floats (ok). Changed the diffuser in the Clearstream, changed the filter in the aerator, and changed the mesh screen in the spinfilter. Installed a re-build kit on the aerator. Need to go back and fix the pump or return line - too wet to do so right now. The timer is set to 3 minutes every 116 minutes. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 08/12/2020 | Jan 1 1900 12:00PM
04/21/2020 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump | Drip | Elevated Sand Mound | UV Light |  | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  |  | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/21/2020 | Jan 1 1900 10:30AM
05/16/2020 |  | Initial Visit | 033-06-0432-SP | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Doug's Septic | 1942001441 | Charles | Thomas | 2.000000 | 1000 |  |  | Pump | Gravity | Mound | Not Applicable | 250.000000 | ["Dispersal System Operation"] | ["Dispersal System Operation"] | true | None | Clear |  |  | 0.000000 | [11 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 05/22/2020 | 11:30 AM
03/23/2020 |  | Routine, Scheduled | 177-09-0059-SP | Spotsylvania County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | None | None | Pump | Distribution Box | Aggregate Trench |  |  | ["Attached Growth Medium","Effluent Screens","None"] | ["Attached Growth Medium","Effluent Screens","None"] | [18 empty] | [Comments]: Roots are growing into the Puraflo Modules. At some point in the future this may limit our ability to service the peat. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/06/2020 | 02:46 PM
06/15/2020 | Alternative | Reportable Incident | 103-STS-101418 | Lancaster | This AOSS should now return to normal function after having provided the above state routine maintenance | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | None | None | Pump | Distribution Box | Aggregate Trench | None | 450.000000 | ["Distribution Pump Operation"] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | [17 empty] | Septic tank and pump tank pumped for replacement of failed discharge pump. Alarm event - Discharge pump failed - replaced - Septic tank and Pump tank pumped for repairs. | This AOSS should now return to normal function after having provided the above state routine maintenance |  | 06/18/2020 | 07:30 AM
03/12/2020 |  | Routine, Scheduled |  | Louisa County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Blue Ridge | CLARK, MICHAEL J | 1934000023 | MICHAEL | CLARK |  |  | Septic Tank Only | Septic Tank Only | None | None | None | None |  |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/17/2020 | 04:32 AM
01/17/2020 |  | Routine, Scheduled | 2004-143-0170 | Henrico County | This AOSS should now return to normal function after having provided the above stated routine maintenance. | Approved | EHD - Henrico | [7 empty] | Septic Tank Only | None | None | None | None |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens"] | [18 empty] | [Comments]: Peat change done on 01/27/20 | This AOSS should now return to normal function after having provided the above stated routine maintenance. |  | 02/13/2020 | 10:23 AM
05/09/2020 |  | RoutineScheduled | 175-14-0303 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Wastemaster | 1965-001817 | Tim | Jenkins | 2.000000 |  |  | Effluent Filter | Pump |  | Discharge | UV |  | [] | [] |  | Musty | Clear | 6.700000 | [14 empty] | #1 & #2 Sandfilters are holding slight amount of water. HRS 1420.73 CC 7581 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 05/09/2020 | 08:25 AM
04/15/2020 |  | Routine, Scheduled | SWT-01-897 | Spotsylvania County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 2.000000 |  | None | None | Pump | Drip | Drip Tubing |  |  | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [18 empty] | [Comments]: K-rain valve has a small leak at the top of O-ring. Septic tank: inlet riser leaking and the outlet wedge lid has roots. Pump tank: The outlet riser and inlet wedge lid has a few roots. All tanks need to be pumped out (Septic, ATU & pump tank). Please contact a pumping company to have the pump out done. A proposal for repairs will be sent. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/27/2020 | 04:14 AM
06/03/2020 |  | RoutineScheduled | 099-18-0159 SWP | King George | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart |  |  | Orenco Advantex | none | Pump | Gravity | Drip | UV |  | ["Recirculation Pump" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Control Operation" ,"Dispersal System Operation" ,"Auxiliary Filter" ,"Attached Growth Medium" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Level Sensor Operation"] | ["SludgeScum Accumulation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Control Operation" ,"Auxiliary Filter" ,"Attached Growth Medium" ,"Effluent Screens" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles"] | YES | [15 empty] | Will be sent separately | Inspected | BOD & fecal collected, waiting on results. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
06/04/2020 |  | RoutineScheduled | 107-16-0082 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Enviro-Klean Co. | 1942001087 | michael | clark | [9 empty] | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 04:55 AM
10/22/2020 |  | Routine/Scheduled | 2008-143-0157 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Henrico | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. |  |  | Hoot |  | Pump |  |  |  |  | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 11/09/2020 | 03:00 AM
05/01/2020 |  | RoutineScheduled |  | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Joe Blevins Equipment Rental, Inc | 2705013926 | Joel | Blevins | 2.000000 | 1500 | Microfast |  | Pump | Gravity | Trenches | Not Applicable | 450.000000 | ["None"] | ["None"] | NA | Musty | Clear |  |  |  |  | none required | [10 empty] | Compressor is strong - cleaned the air filter. There is 24" of sludge on treatment side. Need to get the tank pumped. Ditches are dry | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 05/30/2020 | Jan 1 1900 11:40AM
10/27/2020 |  | RoutineScheduled | 179-12-0319-SWP | Stafford | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 2.000000 |  | Clearstream | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"Control Operation" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | NA | [15 empty] | Will be sent separately | Inspected | Pump tank requires a pump out, client to contact Marshalls. Changed pump times so owner pumps out 420 gal/day. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
07/31/2020 | Alternative | RoutineScheduled | 151-11-0091 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | KC Forge Environmental Service, LLC | 1942001034 | Kent | Cuthbertson |  |  |  |  | Pump | Gravity | Trenches | UV | 23100.000000 | [] | [] | [18 empty] | Effluent is sampled weekly | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 08/15/2020 | 03:25 PM
04/30/2020 |  | RoutineScheduled | 107-09-0145 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Onsite Wastewater Services - May Supply | 1942001022 | Sara | Tusing | 1.000000 |  | none | none | Gravity | Gravity |  | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 05/28/2021 | 05:41 AM
08/01/2020 |  | RoutineScheduled |  | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Prince William | Wastemaster Inc |  | Timothy | Jenkins | 2.000000 |  | ATU | EZ Treat | Pump | Gravity | Discharge | UV |  | ["SludgeScum Accumulation"] | [] |  | Musty | Clear | 7.300000 |  | 35.000000 | [12 empty] | Effluent Pump Tanks Require Pumping | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 08/27/2020 | 03:55 PM
03/26/2020 |  | Routine, Scheduled |  | Loudoun County | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Paid | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | Biomicrobics MicroFAST | None | Pump | Drip | Drip Tubing | [22 empty] | [Comments]: septic and atu need pumped out | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 04/12/2020 | 02:21 PM
11/03/2020 |  | RoutineScheduled |  | Rockingham | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Upgraded timer in control panel | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/26/2021 | 09:04 AM
06/24/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/27/2021 | 01:26 PM
04/16/2020 |  | RoutineScheduled | VAG408256 | Rockingham | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Central Shenandoah | Onsite Wastewater Services - May Supply | 1942001022 | Sara | Tusing |  |  | none | none | Gravity | Gravity |  | Chlorination |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/28/2021 | 05:41 AM
01/06/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | EZ Treat Sandfilter | Biomicrobics MicroFAST |  |  |  | UV Light |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection"] |  | Some Odor | Good | [15 empty] | [Comments]: Pump repaired.Pump Amps 10.4/4.3Septic Sludge " Scum 0.25ATU Sludge 2" Scum 0.75Pump Sludge 0 Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/06/2020 | Jan 1 1900 10:19AM
02/26/2020 |  | Routine, Scheduled | 05-125-081 | Dickenson | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Cumberland Plateau | DEEL, DENNY M | 1942001097 | DENNY | DEEL |  |  |  | None | Gravity | None | Alternative Discharge | Chlorine | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens"] |  | Musty | Clear | [15 empty] | [Comments]: 4 blue crystals, 10 bio max | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/16/2020 | Jan 1 1900 11:21AM
12/18/2020 |  | RoutineScheduled | 175-14-0016 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Prince William | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"BlowerCompressorAerator Operation" ,"Control Operation" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | ["Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Control Operation" ,"Attached Growth Medium" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Media is good but water level is high; can?t find reason why. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
12/30/2020 | Alternative | Routine/Scheduled | 147-13-0100 | James City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Peninsula | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Clearstream ATU |  | Pump |  |  |  |  | ["Control Operation","Disinfection","Dispersal System Operation","Effluent Screens","Septic Tank Baffles"] | ["Control Operation","Disinfection","Dispersal System Operation","Effluent Screens","Septic Tank Baffles"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 12/30/2020 | Dec 30 1899 3:30PM
04/14/2020 |  | Routine, Scheduled | -STS-43176 | Botetourt County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Alleghany-Roanoke | AYRES, HUNTER E | 1942001166 | HUNTER | AYRES | 1.000000 | 1000 | Septic Tank Only | Biomicrobics MicroFAST | Pump | Drip | Drip Tubing | None |  | ["None"] | ["None"] | [18 empty] | [Comments]: Filters checked and cleaned. System did not need to be pumped. No apparent leaks in system or drain field area. All control panels functioning properly. All alarms operating properly. Lids properly secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/14/2020 | Jan 1 1900 9:14PM
05/02/2020 |  | RoutineScheduled | SWP-05-256 | Stafford | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  | ["Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Attached Growth Medium" ,"Control Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Level Sensor Operation"] | ["SludgeScum Accumulation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Septic Tank Baffles" ,"Distribution Pump Operation" ,"Attached Growth Medium" ,"Control Operation"] | YES | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
10/15/2020 |  |  | 12-125-022 | Dickenson | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 10/15/2020 |  | 2.070000 | [5 empty] | Attached to this report |  | BOD: 2.07 TSS: BDL | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 10/15/2020 | 12:00 AM
05/22/2020 |  | RoutineScheduled | 179-18-0166-SP | Stafford | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Effluent Screens" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Effluent Screens" ,"Recirculation Pump"] | YES | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/09/2021 | 03:25 PM
06/02/2020 |  | Follow-Up | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance | Approved | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green | [9 empty] | ["Disinfection"] | ["Disinfection"] | [18 empty] | Replaced Jet UV bulb, chord & housing tube for bulb. | This AOSS should now return to normal function after having provided the above state routine maintenance |  | 06/02/2020 | Jan 1 1900 4:00PM
04/21/2020 |  | Routine/Scheduled |  | Loudoun | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Loudoun | POWELLS PLUMBING, INC. | 1942001036 | Kurt | Holthaus | 1.000000 | 540 | Multiflo FTB |  | Pump | Distribution Box | Aggregate Trench |  | 600.000000 | ["Level Sensor (Float) Operation"] | ["Level Sensor (Float) Operation"] | N/A | [17 empty] | Annual Inspection - Replaced old transducer float with new mechanical style float. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 05/13/2020 | 12:22 PM
09/04/2020 | Alternative | Initial Visit | 136-15-0305 | Gloucester | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | Advanced Septic | None | Pump | Manifold | Aggregate Trench | UV Light | 500.000000 |  | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | Musty | Clear | [15 empty] | Initial Visit Septic Tank at normal operating level Aeration Unit (AquaSafe) - at normal operating level - heavy solids present Aeration - operating properly - serviced compressor Disinfection - U.V. bulb burned out - serviced quartz crystal Discharge Tank - leaks present in riser - discharge pump serviced, float sensors and controls operating Absorption field has indicators of surfacing - requires further evaluation. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 09/08/2020 | 08:00 AM
01/21/2020 |  | Routine, Scheduled |  | Richmond City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Richmond | Ware, Michele P | 1942001165 | Michele | Ware |  |  | Septic Tank Only | Septic Tank Only | None | None | None | None |  |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/28/2020 | Jan 1 1900 5:46PM
12/15/2020 |  | Routine/Scheduled |  | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | UV Light |  | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  |  | 4.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 12/15/2020 | Jan 1 1900 7:15AM
06/23/2020 |  | RoutineScheduled | 177-10-0242-SP | Spotsylvania | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Orenco Advantex | Orenco Advantex | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Control Operation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | ["Control Operation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Attached Growth Medium" ,"Effluent Screens" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | YES | [15 empty] | Will be sent separately | Inspected | A few roots in distribution box. 10" Maple tree 3ft. from distribution box, recommend having it removed. Cleaned water out of junction box on Advantex. Advnatex RT unit needs to be pumped out, proposal to be sent to homeowner for pumping. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
10/08/2020 |  |  | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Wastemaster Inc |  | Timothy | Jenkins | 2.000000 |  | ATU |  | Pump | Pressure | Drip |  |  | [] | [] | [5 empty] | 8.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 10/08/2020 | Jan 1 1900 12:55PM
11/02/2020 |  | Reportable Incident | 86-152 | Clarke | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Lord Fairfax | POWELLS PLUMBING, INC. | 1942001036 | Kurt | Holthaus | [9 empty] | ["Distribution Pump Operation","Sludge/Scum Accumulation"] | ["Distribution Pump Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | Pumped septic tank and pump chamber. Repaired discharge line coming out of pump chamber. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 11/25/2020 | 12:55 PM
05/12/2020 | Alternative | Routine/Scheduled | 166-04-824 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1500 | Orenco Advantex | None | Pump | Distribution Box | Aggregate Trench | None |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | [17 empty] | There are roots infiltrating the Recirculation Tank Riser; the Advantex Media Pod Lid was not properly secured with hinges and was missing support Struts; Distribution Box was not located | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 05/26/2020 | 03:26 PM
11/16/2020 |  | RoutineScheduled | 069050096 | Frederick | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/26/2021 | 09:04 AM
04/11/2020 |  | RoutineScheduled | SD-97-97 | Culpeper | This AOSS is functioning as designed and in accord | Approved | EHD - Rappahannock-Rapidan | Wastemaster |  | Douglas | Crooks | 2.000000 |  |  |  | pump |  | discharge | Chlorine |  | [] | [] |  | Low | Clear | 6.500000 |  |  | 1.900000 |  | 04/11/2020 |  | 4.000000 |  |  | 1.600000 |  |  | Attached to this report |  | Functioning as Designed | This AOSS is functioning as designed and in accord |  |  | 12:00 AM
01/15/2020 |  | Routine, Scheduled | 171-12-0229 | Shenandoah | This AOSS should now return to normal function after having provided the above stated routine maintenance. | Approved | EHD - Lord Fairfax | POWELLS PLUMBING, INC. | 1942001036 | Kurt | Holthaus | 1.000000 | 1250 |  |  | Pump | Drip | Drip Tubing |  | 450.000000 | ["BlowerCompressorAerator Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Distribution Pump Operation"] | [18 empty] | [Comments]: Excavated and exposed incoming line and outgoing line on pump chamber. Sealed entry and exit lines of tank with hydraulic cement and top coat with Benseal. Replaced 1 ¼ gate valve in valve box. Installed 2€™ Polylok riser on incoming side of septic tank. Sealed riser to septic tank with Benseal. Serviced spin filter and blower. | This AOSS should now return to normal function after having provided the above stated routine maintenance. |  | 01/15/2020 | 01:54 PM
02/10/2020 |  | Routine, Scheduled | SWP-04-347 | Stafford County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Puraflo | None | Pump | Distribution Box | Aggregate Trench |  |  | ["Control Operation","Level Sensor Operation"] | ["Control Operation","Level Sensor Operation"] | [18 empty] | [Comments]: Concrete lid for pump tank is crumbling and lid for septic tank has deep iris cracks - both need to be replaced. Effluent level in pump tank was all the way down to the pump intake due to a "failed on" timer float. Replaced the timer and high level floats. Could not test pump flow rate due to lack of effluent (water) in tank. Bumped switch briefly to verify it still ran. Rust stains in pump tank suggest infiltration, but owner said he rarely gets alarms. Septic tank was recently pumped but still had fairly big chunks of floating scum. Recommend adding a riser and lid to the inlet end of tank to allow for better pump-outs and to check for inflow from the house. Mounting post for control panel is rotten and needs replaced. Piping in tank would make pump replacement very difficult without entering the tank and should be modified. Peat is showing its age (15 years) with fairly big pockets of standing water and is very compacted. Raked peat. It should be replaced before next year’s inspection. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/11/2020 | 06:36 AM
07/23/2020 |  | Initial Visit | VAG408149 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | [6 empty] | Multiflo | [6 empty] | ["Attached Growth Medium"] | ["Attached Growth Medium"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 07/23/2020 | 12:00 AM
12/21/2020 |  | RoutineScheduled | 179-18-0231-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Distribution Pump Operation" ,"Recirculation Pump" ,"Auxiliary Filter" ,"Disinfection" ,"Attached Growth Medium"] | ["Auxiliary Filter" ,"Attached Growth Medium" ,"Disinfection" ,"Distribution Pump Operation" ,"Recirculation Pump"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced UV Bulb and cord. | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 |  | 04/09/2021 | 03:25 PM
03/06/2020 |  | Routine, Scheduled |  | Fluvanna County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Blue Ridge | CLARK, MICHAEL J | 1934000023 | MICHAEL | CLARK |  |  | Septic Tank Only | Septic Tank Only | None | None | None | None |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/17/2020 | 04:43 AM
06/03/2020 |  | RoutineScheduled | SP-05-15 | King George | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Ecoflo | none | Pump | Gravity | Pad | Not Applicable |  | ["Distribution Pump Operation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Attached Growth Medium" ,"Control Operation" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | ["Effluent Screens" ,"Level Sensor Operation" ,"Septic Tank Baffles" ,"Attached Growth Medium" ,"Control Operation" ,"Distribution Pump Operation" ,"SludgeScum Accumulation"] | YES | [15 empty] | Will be sent separately | Inspected | Pump tank inlet & outlet pipe leaks. Septic tank inlet wedge lid has roots, homeowner stated no alarms after rain events. Pump out of septic & pump tank needed. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
10/19/2020 |  | RoutineScheduled | {FIPSCode}-STS-5685 | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | ["None"] | ["None"] | YES | [16 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
11/11/2020 |  | RoutineScheduled | 18-100-0018 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Environmental Systems Service | 1942001050 | Troy | Jenkins | [9 empty] | [] | [] |  | None | Discolored | 7.320000 | [14 empty] | UV not working. Parts on order. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
04/21/2020 |  | RoutineScheduled | 175-04-0388 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | EcoVirginia LLC | 1942001235 | William | Poindexter | 1.000000 |  | Delta DF |  | Pump | Pressure | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation","Auxiliary Filter"] | ["BlowerCompressorAerator Operation","Auxiliary Filter"] | NA | Musty | Clear | [15 empty] | 4672 hrs/26621 cy/12.1A WM:1692307 gal | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 07/21/2020 | 12:00 AM
01/08/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS should now return to normal function after having provided the above stated routine maintenance. | Paid | EHD - Fairfax | SEAMON, CHARLIE L | 1942001108 | CHARLIE | SEAMON |  |  | Septic Tank Only | Microfast | Pump | Manifold | Drip Tubing | UV Light |  | ["BlowerCompressorAerator Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation"] | [8 empty] | 01/16/2020 |  |  |  | 1.800000 |  |  |  | Attached to this report |  | [Comments]: Performance Inspection: Microfast w/UV Light to American Drip. Septic-8"sludge 3"scum/ATU-12"sludge/Pump tank-0"sludge. Septic/Microfast ATU needs pump out.Zone1 cnts-607 ff-49/Zone2 cnts-601 ff-50/Pump cnts-1307 ETM-353h 25m/Peak-1 ETM-0h/ High-1 ETM-0. Blower air filter cleaned. Water meter-887,225.5/No breakout on the drainfield. | This AOSS should now return to normal function after having provided the above stated routine maintenance. |  | 03/19/2020 | Jan 1 1900 7:40AM
06/12/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/14/2021 | 04:27 PM
11/21/2020 |  | RoutineScheduled | 2126-09-153 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Wastemaster Inc |  | Timothy | Jenkins | 2.000000 |  | PuraFlo | Effluent Filter | Pump | Gravity | Discharge | UV |  | [] | [] |  | Musty | Clear | 6.700000 | [14 empty] | Peat is in great shape. Tested HLA. Cleaned Effluent Filter. Post aeration checked. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12/09/2020 | 01:30 PM
09/21/2020 |  | Follow-Up |  | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Rejected | EHD - Chesterfield | Wastemaster Inc |  | Timothy | Jenkins | 2.000000 |  | ATU |  | Pump | Pressure | Drip |  |  | [] | ["BlowerCompressorAerator Operation"] | [18 empty] | Installed new aerator | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 10/08/2020 | Jan 1 1900 1:00PM
12/08/2020 |  | RoutineScheduled | 179-06-0164-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Wastemaster Inc |  | Timothy | Jenkins | 2.000000 |  | PuraFlo |  | Pump | Pressure | Drip |  |  | [] | [] | [18 empty] | In for annual inspection. Found pump tank level low because of a stuck float switch. Cleaned and operating properly but floats may soon need replacement. Peat in very good condition. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12/14/2020 | 02:05 PM
07/29/2020 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU | [6 empty] | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  |  | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 07/29/2020 | Jan 1 1900 10:00AM
06/11/2020 |  | RoutineScheduled | 154-03-0415 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Aiternative Systems Inspection Services, LLC | 1942001047 | Wesley | Basore | 1.000000 | 500 | EcoFlow ST650 |  | Pump | Gravity | Trenches |  | 100.000000 | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation","Auxiliary Filter"] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation","Attached Growth Medium","Auxiliary Filter"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 07/19/2020 | 01:50 PM
12/28/2020 |  | RoutineScheduled | 04-165-0061 | Northampton | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Bundick Well & Pump | 1942001051 | Peter | Duer | 40.000000 | 40000 | Septic Tank | Microfast | Pump | Pressure | Trenches | Not Applicable | 26690.000000 | ["Distribution Pump Operation"] | ["Distribution Pump Operation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 01/19/2021 | 08:00 AM
08/10/2020 |  |  | 13-113-102 | Buchanan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 08/10/2020 |  | 9.120000 | [5 empty] | Attached to this report |  | TSS: BDL | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 08/10/2020 | 12:00 AM
11/06/2020 |  | Follow-Up | 02-197-188 | Wise |  |  | EHD - Lenowisco | Wise Health Dept |  | Rodney | Neece | 1.000000 |  | ATU |  | Gravity | Gravity | Discharge | Chlorination | [10 empty] | Chlorine tables are now located in the chamber | [14 empty] | 12:00 AM
05/09/2020 |  | RoutineScheduled | 109-04-0947 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1500 | MultiFlo |  | Gravity | Gravity | Trenches |  |  | ["None"] | ["None"] | [18 empty] | 12" of solids in septic tank. Tested alarm. Adequate aeration. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 09/18/2020 | 07:03 PM
10/12/2020 |  | RoutineScheduled | 11-183-019 | Russell |  |  | EHD - Cumberland Plateau |  |  |  |  | 3.000000 | 4000 |  |  | Gravity | Gravity | Trenches | Not Applicable | 1350.000000 | [19 empty] | Pumped Out | Outlet tees intact per pumper and installed speed levelers in distribution boxes where needed and repaired Distribution box 1. |  |  |  | 12:00 AM
01/31/2020 |  | Routine, Scheduled | SD-14-207 | Fauquier County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | KLEINDL, JAMES LEE | 1942001380 | JAMES LEE | KLEINDL | 1.000000 | 1500 | Aqua Safe ATU | Septic Tank Only | Gravity | Distribution Box | Aggregate Trench | None |  |  | ["SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/03/2020 | 06:25 PM
04/10/2020 |  | Routine, Scheduled |  | Loudoun County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | None | None | Pump | Manifold | [24 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/12/2020 | 02:21 PM
01/17/2020 |  | Routine, Scheduled |  | Middlesex County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Three Rivers | PINNIX, JOEL S | 1934000193 | JOEL | PINNIX |  |  | Septic Tank Only | Septic Tank Only | None | None | None | None | [22 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/23/2020 | 10:12 AM
12/28/2020 |  | Routine, Scheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Biomicrobics MicroFAST |  |  |  |  | None |  | ["Blower/Compressor/Aerator Operation"] | ["Blower/Compressor/Aerator Operation"] |  | Acceptable | Clear | [15 empty] | Spin filter cleaned. Pump Amps 7.13 ETM 1094 hrs Cycles 10796 Water Meter Reading 652000 Septic Sludge 6" Scum 3" ATU Sludge 8" Scum 0 Pump Sludge 3" Scum 0 On 6 mins Off 1 hr 51 mins | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 12/28/2020 | Jan 1 1900 8:48AM
01/24/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Fairfax | GOINS, AARON M | 1942001248 | AARON | GOINS |  |  | Septic Tank Only | Septic Tank Only | None | None | None | None | [22 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/27/2020 | Jan 1 1900 1:38PM
09/16/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Ecoflo | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Upon arrival we noticed a wet spot with black staining below the recirculation/splitter valve housing. When testing the pump the valve housing was filling with effluent and spilling out of the housing. | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 |  | 05/27/2021 | 01:26 PM
09/16/2020 |  | RoutineScheduled |  | Shenandoah | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/26/2021 | 09:04 AM
01/31/2020 |  | Routine, Scheduled | 033-12-0101-SWP | Caroline County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Ware, Michele P | 1942001165 | Michele | Ware |  |  | Septic Tank Only | Septic Tank Only | None | None | None | None |  |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/31/2020 | 04:35 PM
08/27/2020 |  | RoutineScheduled | 11-125-010 | Dickenson | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Drip | Not Applicable | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","Effluent Screens"] | ["BlowerCompressorAerator Operation","Control Operation","Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
12/01/2020 | Alternative | Routine/Scheduled | 166-08-313 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 2.000000 | 2500 | Ecoflo |  | Pump | Distribution Box | Aggregate Trench |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12/01/2020 | 04:30 PM
02/04/2020 |  | Routine, Scheduled |  | Loudoun County | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Paid | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | None | None | Pump | Distribution Box | Gravel-Less Trench | [22 empty] | [Comments]: Sale inspection on a conventional pump system. The demand dose septic control panel is exterior. There are 3 pvc clean outs The sewer line was camera snaked. The septic tank has plastic risers on the inlet and outlet side of the tank. There is a filter that was cleaned when the tank was pumped. The pump tank, pump, floats and force main were inspected. The 15 port concrete d-x was dug up it was 12" under the ground. The box is badly broken and not holding water. The Loudoun county health dept will need to come out and issue a repair permit to replace the d-box. All 5 header lines were full of water. Drain field was probed At this time the septic system is not in working condition | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 03/02/2020 | 04:43 AM
03/11/2020 |  | Routine, Scheduled | 177-06-0555-SWP | Spotsylvania County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001350 | Mike | Cook | 1.000000 |  | EcoPod | None | Pump | Drip | Drip Tubing |  |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/18/2020 | 06:42 AM
10/22/2020 |  | RoutineScheduled | 154-01-0052 | Louisa | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Blue Ridge | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  | ["Dispersal System Operation"] | ["Dispersal System Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Quarterly Inspection Pump Station #1 - We recommend replacing the Zone 3 psi gauge Pump Station #2 - We recommend replacing the American Manufacturing Contactor Pump Station #5 - We recommend replacing the psi gauge for Zone 4. There are damaged globe valves in the dispersal area and a repair proposal has been approved. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/09/2021 | 03:25 PM
12/30/2020 |  | Routine/Scheduled | 175-04-0023 | Prince William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Biomicrobics MicroFAST |  |  |  |  | Not Applicable |  | ["Dispersal System Operation"] |  | N/A | [18 empty] | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 12/30/2020 | 04:00 PM
05/19/2020 |  | Routine, Scheduled | 175-08-0092 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Puraflo |  |  |  |  | None |  | ["Effluent Screens"] | ["Effluent Screens"] | [18 empty] | Pump Amps 10.37 ETM 10769 Cycles 8422 Pump Amps 10.13 ETM 52325 Cycles 8155 Septic Sludge 11" Scum 0 Pump Sludge 1"/3" Scum 0/0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 05/19/2020 | 05:20 PM
06/01/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/27/2021 | 01:26 PM
07/08/2020 |  | Routine/Scheduled | 10-120-0200A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. |  |  | Norweco Singulair ATU |  | Pump |  |  |  |  | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 07/09/2020 | Jan 1 1900 12:30PM
12/17/2020 | Alternative | Routine/Scheduled | 151-04-043 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 1.000000 | 1500 | Microfast |  | Pump | Distribution Box | Aggregate Trench |  |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12/17/2020 | 05:00 PM
04/22/2020 |  | Routine, Scheduled | 175-18-0382 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green | 1.000000 |  | EcoPod |  |  |  |  | None |  | ["Blower/Compressor/Aerator Operation","Effluent Screens"] | ["Blower/Compressor/Aerator Operation","Effluent Screens"] |  | Good | Clear | [5 empty] | 04/22/2020 | Pump tank | 6.000000 | [7 empty] | Spin filter cleaned. Pump Amps 9.40 ETM 373 Cycles 2243 Water Meter Reading 70210 Septic Sludge 1" Scum 1" ATU Sludge 2" Scum 0 Pump Sludge 0 Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/22/2020 | 08:27 AM
08/08/2020 |  | RoutineScheduled | 109-17-0203 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1000 | Advantex |  | Pump | Gravity | Trenches |  |  | ["None"] | ["None"] | [18 empty] | 6" of solids in septic tank. Cleaned septic tank filter. Flushed treatment unit spray manifold. Tested floats, pumps and alarm. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 09/30/2020 | 07:03 PM
07/06/2020 | Alternative | Routine/Scheduled | 157-10-0139 | Mathews | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | Serviced system. Checked the pump, panel, & floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream, changed the filter in the aerator, changed the mesh screen in the spinfilter, and replaced the UV light bulb. The timer is set to 15 minutes every 1 hour. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 07/06/2020 | 12:00 PM
07/01/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | The float bracket had broken off the riser and was hanging in the tank. The inlet riser of the Microfast was broken and needs a new lid. Homeowner is contacting the installer for warranty. | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 |  | 05/27/2021 | 01:26 PM
10/27/2020 |  | Reportable Incident |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | SES MidAtlantic LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Level Sensor Operation"] | ["Level Sensor Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced (3) control floats. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/15/2021 | 09:00 AM
05/13/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | EcoPod | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/27/2021 | 01:26 PM
06/29/2020 |  | Routine, Scheduled | 175-19-0229 | Prince William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Orenco Advantex |  | Pump | None | Alternative Discharge | UV Light |  | ["Blower/Compressor/Aerator Operation","Effluent Screens"] | ["Blower/Compressor/Aerator Operation","Effluent Screens"] |  | Good | Clear | [5 empty] | 06/29/2020 | Pump tank | 11.000000 |  | 540.000000 | [5 empty] | Pump Amps 10.79 ETM 88 hrs 20 mins Cycles 17037 Pump Amps 8.87 ETM 172 hrs 25 mins Cycles 350 | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 06/29/2020 | 12:36 PM
10/13/2020 | Alternative | Routine/Scheduled | 166-17-073 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 6.000000 | 19000 | Microfast |  | Pump | Distribution Box | Aggregate Trench |  |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 10/13/2020 | 02:30 PM
03/09/2020 |  | Routine, Scheduled |  | Warren County | This AOSS should now return to normal function after having provided the above stated routine maintenance. | Paid | EHD - Lord Fairfax | POWELLS PLUMBING, INC. | 1942001036 | Kurt | Holthaus | 1.000000 | 1000 | Puraflo |  | Pump | Distribution Box | Aggregate Trench |  | 450.000000 | ["Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | ["Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | [18 empty] | [Comments]: Annual Inspection - Serviced effluent screens, pumped septic tank and pump chamber. Replaced distribution box and repaired 4 header lines. | This AOSS should now return to normal function after having provided the above stated routine maintenance. |  | 03/09/2020 | 04:33 PM
01/17/2020 |  | Routine, Scheduled | 234-13-35 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesapeake | R & K Septic, Inc. |  | John | Butt, Jr |  |  | Clearstream ATU |  | Pump | Drip | Elevated Sand Mound | UV Light |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] |  |  | 7.58 | 8.110000 | 3.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/17/2020 | Jan 1 1900 8:45AM
09/17/2020 |  | RoutineScheduled |  | Rockingham | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity |  | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation"] | ["BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/26/2021 | 09:04 AM
05/22/2020 |  | RoutineScheduled | 107-04-0517 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Onsite Wastewater Services - May Supply | 1942001022 | Sara | Tusing | 1.000000 |  | Orenco Advantex | none | Pump | Gravity |  | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 05/28/2021 | 05:41 AM
08/21/2020 | Alternative | Routine/Scheduled | 136-09-0266 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 2000 | Clearstream | None | Pump | Drip | Drip Tubing | None | 450.000000 |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | Musty | Clear | [15 empty] | Routine service conducted. Trash Tank - normaloperating level Aeration Tank - normal operating level - compressor serviced. Pump Tank - normal operating level - pump serviced, float sensors and controls operating properly. Drip Field - drip screen serviced, field flushed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 08/27/2020 | 08:45 AM
03/23/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Paid | EHD - Fairfax | MCKIM, STEPHEN E | 1934000043 | STEPHEN | MCKIM |  |  | Septic Tank Only | Septic Tank Only | None | None | None | None |  | ["SludgeScum Accumulation"] | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | [18 empty] | [Comments]: Septic/Atu and pump tank need pumped out | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 04/20/2020 | Jan 1 1900 10:29AM
03/26/2020 |  | Routine, Scheduled | 136-15-0003 | Gloucester County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers | LANGFORD, CHARLES T | 1934000143 | CHARLES | LANGFORD | 1.000000 | 1500 | Microfast | Septic Tank Only | Pump | Distribution Box | Aggregate Trench | None |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/14/2020 | 02:56 PM
09/09/2020 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Gravity | Gravity |  | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | A septic inspection was done on a conventional pump system. The state requires that all conventional septic tanks must be pumped out EVERY 5 years and filed with the state and county. The septic control panel is a demand dose. There are 2 clean outs and the pvc sewer line was camera snaked and was clear. The septic tank has a concrete riser on the outlet side and a filter that was cleaned. The filter manufacture recommends that the filter be cleaned every 6 months. The septic tank was pumped out and inspected for any cracks or leaks none were found. The pump tank, pump, floats and force main were inspected. The ground level 9 port plastic d-box was opened and all 6 header lines were camera snaked and were clear. The drain field was probed and dry. At time of inspection all components were in working condition. | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 |  | 04/14/2021 | 04:27 PM
04/23/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | Orenco Advantex | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/14/2021 | 04:27 PM
07/31/2020 |  | Pump-Out Only | 175-13-0417 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | POWELLS PLUMBING, INC. | 1942001036 | Kurt | Holthaus |  |  | Aquarobic Mini Plant | [6 empty] | ["Sludge/Scum Accumulation"] | ["Sludge/Scum Accumulation"] | N/A | [17 empty] | Pumped Aquarobic | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 10/08/2020 | 02:21 PM
03/10/2020 |  | Routine, Scheduled | 08-192-039 | Tazewell County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Cumberland Plateau | DEEL, DENNY M | 1942001097 | DENNY | DEEL |  |  |  | None | Gravity | None | Alternative Discharge | Chlorine | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Level Sensor Operation"] |  | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/16/2020 | Jan 1 1900 12:32PM
04/06/2020 | Alternative | Routine/Scheduled | 136-97-0401 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | Puraflo | None | Pump | None | Aggregate Trench | None |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | Septic Tank does not have a Riser for required access to clean/inspect Filter, Tank has heavy sludge/solids, Lid did not have proper handle and broke upon re installation; the Override/High Level Alarm Float was not functioning in the Pump Tank, Conduit from Crock Riser to Control Panel was not properly set/sealed; Puraflo Biofilter Peat Moss has severely deteriorated and is no longer properly filtering water | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/07/2020 | 02:28 PM
03/05/2020 |  | Routine, Scheduled | 179-13-0239-SWP | Stafford County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001350 | Mike | Cook | 1.000000 |  | None | None | Pump | Distribution Box | Gravel-Less Trench |  |  | ["Control Operation","Distribution Pump Operation","SludgeScum Accumulation"] | ["Control Operation","Distribution Pump Operation","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/18/2020 | 06:42 AM
12/18/2020 |  | Routine/Scheduled | 154-14-0002 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Old Dominion Onsite, Inc. | 1942001134 | John | Ewing | 1.000000 | 1000 | Orenco Advantex |  | Pump | Distribution Box | Gravel-Less Trench | None | 450.000000 | ["Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump"] | ["Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump"] | N/A | [17 empty] | Effluent filter was significantly clogged. Effluent filter was cleaned and the manifold was flushed. The system reported 22 overrides in the last 30 days. Recirculation pump off time was changed from 19.7 to 18 minutes, and the override was changed to 8 minutes. Septic tank should be pumped out within the next year. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12/18/2020 | 11:24 AM
04/09/2020 |  | RoutineScheduled | 13-184-5001 | Scott | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. |  | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Effluent Screens"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
02/24/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Puraflo |  |  |  |  | None |  | ["Effluent Screens"] | ["Effluent Screens"] | [8 empty] | 02/24/2020 |  | 7.000000 | [7 empty] | [Comments]: Pump 1 Amps 9.80 ETM 13h 21m Cycles 2016Pump 2 Amps 9.75Septic Sludge 4" Scum 0Pump Sludge 0.50 Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/24/2020 | Jan 1 1900 2:31PM
01/13/2020 |  | Routine, Scheduled |  | Warren County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Lord Fairfax | MCKIM, STEPHEN E | 1934000043 | STEPHEN | MCKIM |  |  | Septic Tank Only | Septic Tank Only | None | None | None | None |  |  | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/15/2020 | 01:24 PM
06/02/2020 |  | Routine, Scheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Biomicrobics MicroFAST |  |  | Drip |  | None |  | ["Blower/Compressor/Aerator Operation","Dispersal System Operation"] | ["Blower/Compressor/Aerator Operation","Dispersal System Operation"] |  | Good | Clear | [15 empty] | Spin filter cleaned. Pump 1 Amps 15.92 Pump 2 Amps 15.51 Water Meter Reading 682230 Septic Sludge 10" Scum 3" ATU Sludge 9" Scum 0 Pump Sludge 0 Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 06/02/2020 | Jan 1 1900 4:04PM
07/29/2020 |  | RoutineScheduled | {FIPSCode}-STS-40633 | Botetourt | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Alleghany-Roanoke | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1000 | Whitewater ATU |  | Pump | Pressure | Drip | Not Applicable |  | [] | [] | NA | [16 empty] | Inspected | Sludge levels-- 2" sludge in Septic tank, 1" in treatment unit & 3" sludge in Pump tank, Depth gauge has lost suction and reset to zero, while sitting idle, Removed depth guage rest and read 14", Pump operational. Both alarms operational, cleaned drip filter, Pump runs when required in auto. Good aeration in treatment. Cleaned Blower airfilter, very dirty . System will return to normal operational. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 07/30/2020 | Jan 1 1900 9:30AM
07/13/2020 |  | Reportable Incident | 2016-143-0066 | Henrico | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Henrico | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | Owner called due to the alarm going off. Serviced system. Checked the pump, panel, & floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. Installed a re-build kit on the aerator. The septic tank needs to be pumped out and when pumping out pump the trash off the Clearstream. The timer is set to 4 minutes every 2 hours. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 07/13/2020 | 12:00 PM
02/26/2020 |  | Routine, Scheduled | 04-160-0071 | Montgomery County | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - New River | Conner, Timothy Wayne | 1942001003 | Timothy | Conner | 1.000000 | 1000 | Ecoflo | None | Pump | Distribution Box | Aggregate Trench | None | [21 empty] | [Lab Comments]: NO SAMPLE PORT ONSITE. [Comments]: THE PEAT MOSS AND OUTLET FILTER NEED TO BE REPLACED. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 03/13/2020 | 04:21 PM
08/27/2020 |  | RoutineScheduled | SD-09-312 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Soils, Inc. | 1940001392 | Markham | Smith | 2.000000 | 1500 | Puroflo |  | Pump | Gravity | Pad | Not Applicable |  | [] | ["Septic Tank Baffles","SludgeScum Accumulation","Control Operation","Attached Growth Medium","Level Sensor Operation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 09/01/2020 | 09:30 AM
11/04/2020 |  | Follow-Up |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Gravity | Gravity |  | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Both d-boxes were replaced and Loudoun County Health dept inspected and passed the install. D-boxes were back filled and seeded | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 |  | 04/14/2021 | 04:27 PM
10/06/2020 |  | Follow-Up |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [11 empty] | N/A | [7 empty] | 10/06/2020 |  | 3.000000 | [8 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 10/13/2020 | Jan 1 1900 8:30AM
05/19/2020 |  | Routine/Scheduled |  | Southampton | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump | Distribution Box | Aggregate Bed | None |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  |  | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 05/19/2020 | Jan 1 1900 11:00AM
04/24/2020 |  | RoutineScheduled | SWP-05-19 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Ace Contracting Services Inc | 1942001120 | Lawrence | Fellenz Jr. | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected | Sampling Box Lid Broken Needs Replaced. Distribution Box Cracked Needs Replaced. Home Owner Made Aware. | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 |  | 06/29/2021 | 10:39 PM
04/27/2020 |  | RoutineScheduled |  | Fairfax | This AOSS is functioning as designed and in accord | Approved | EHD - Fairfax | Great Falls Septic Service | 1942001301 | Joshua | Hott | 1.000000 | 1250 |  | Puraflo | Pump | Distribution Box | Aggregate Trench | None | 500.000000 | ["None"] | ["None"] |  | Low | [17 empty] | This AOSS is functioning as designed and in accord |  |  | 12:00 AM
09/23/2020 |  | Reportable Incident | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance | Approved | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green | [9 empty] | ["Disinfection"] | ["Disinfection"] | [18 empty] | Replaced UV transformer. | This AOSS should now return to normal function after having provided the above state routine maintenance |  | 09/23/2020 | Jan 1 1900 1:30PM
08/01/2020 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 | Pending Payment | EHD - Loudoun | WasteMaster, Inc. | 1942001062 | Tim | Jenkins |  |  | none | none | Gravity | Gravity |  | Chlorination |  |  |  | NA | [5 empty] | 2.200000 | [6 empty] | 25.000000 |  |  | Will be sent separately | Inspected | Delivered 1 bucket of Dechlor | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 |  | 06/21/2021 | 10:37 AM
10/23/2020 |  | Reportable Incident | 05-137-0294 | Goochland | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Chickahominy | Old Dominion Onsite, Inc. | 1942001549 | Russell | Revis | [9 empty] | ["Dispersal System Operation","Distribution Pump Operation","Recirculation Pump"] | ["Dispersal System Operation","Distribution Pump Operation","Recirculation Pump"] | N/A | [17 empty] | Recirc alarm. System has significant leaks and is taking in thousands of gallons of ground water when available. Pumped down recirc for approximately two hours. New leak found around RSV grommet during this visit. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. |  | 10/27/2020 | Jan 1 1900 11:22AM
02/20/2020 |  | Routine, Scheduled | 177-17-0056-SP | Spotsylvania County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Ware, Michele P | 1942001165 | Michele | Ware |  |  | Septic Tank Only | Septic Tank Only | None | None | None | None |  |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/21/2020 | 07:29 AM
09/17/2020 | Alternative | Routine/Scheduled | 166-02-690 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 2000 | Orenco Advantex | Orenco Advantex | Pump | Drip | Drip Tubing | None | 1000.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | None | Clear | [15 empty] | Routine Service Primary Septic Tank - normal operating level Processing Tank - normal operating level - RSV, Recirc. Pump & Effluent screen serviced. Treatment Modules (2) - media drapes & spray grids serviced Discharge Tank - normal operating level - discharge pump serviced, float sensors & controls operating properly. Drip Headworks - Vortex filter serviced. Drip field - REMOTE - walked field - no indications of surfacing | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 09/18/2020 | 08:00 AM
12/29/2020 |  | RoutineScheduled |  | Shenandoah | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NO | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/26/2021 | 09:04 AM
06/17/2020 |  | Routine/Scheduled |  | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump | Drip | Elevated Sand Mound | UV Light |  | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  | 16 | 7.650000 | 3.800000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 06/17/2020 | Jan 1 1900 1:45PM
11/30/2020 |  | Routine/Scheduled | 08-137-0078 | Goochland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Old Dominion Onsite, Inc. | 1942001549 | Russell | Revis | [9 empty] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump"] | N/A | [17 empty] | Cleaned manifold, RSV and effluent filter. Checked float and pump function. System appears to be working normally. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 11/30/2020 | Jan 1 1900 9:45AM
05/13/2020 |  | RoutineScheduled | 182-11-0030 | Rockingham | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Central Shenandoah | Onsite Wastewater Services - May Supply | 1942001022 | Sara | Tusing | 1.000000 |  | Orenco Advantex | none | Pump | Gravity |  | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | INSPECTION DS | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/28/2021 | 05:41 AM
01/13/2020 |  | Routine, Scheduled |  | Louisa County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Blue Ridge | CLARK, MICHAEL J | 1934000023 | MICHAEL | CLARK |  |  | Septic Tank Only | Septic Tank Only | None | None | None | None |  |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/14/2020 | 03:14 AM
04/24/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Air vent is broken | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 |  | 04/14/2021 | 04:27 PM
09/17/2020 |  | RoutineScheduled |  | Rockingham | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/26/2021 | 09:04 AM
10/03/2020 |  | Initial Visit | 019-STS-23891 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1000 | MicroFast 0.50 |  | Pump | Pressure | Drip |  |  | ["None"] | ["None"] | [18 empty] | Initial start-up visit. Set pressure on drip field. Set discharge pump timer at 5 minutes ON, 5 minutes OFF. Blower operational. Tested floats, pump and alarms. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 10/29/2020 | 12:00 AM
08/03/2020 |  | RoutineScheduled | 175-13-0417 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | Aquarobic Services | 1934000142 | Michael | Blake |  |  | none | none | Pump | Gravity | Mound | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Single point aeration had developed. Tank pumped and cleaned 3 days prior. New manifold installed, leveled, and secured with marine nylon rope. Ballast added to prevent manifold from floating and flush valve added for future maintenance. Added enough fresh water to verify excellent aeration and measure pump rate. Filter bed vent was broken on one side and cracked on the other. Replaced both vent pipes. Air pre-filter cleaned as preventative maintenance. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 07/01/2022 | 10:30 AM
03/17/2020 |  | Pump-Out Only |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [11 empty] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/17/2020 | Jan 1 1900 10:00AM
05/20/2020 |  | Routine/Scheduled | 02-163-0379 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chickahominy | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1500 | Orenco Advantex | None | Pump | Distribution Box | Aggregate Trench | None |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | [17 empty] | Advantex Treatment Unit Lid has a seal that has cracked again, and the middle ring was not present. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 06/05/2020 | Jan 1 1900 4:10PM
04/08/2020 |  | Routine, Scheduled | 179-08-0248-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | EcoPod |  |  |  |  | None |  | ["Blower/Compressor/Aerator Operation"] | ["Blower/Compressor/Aerator Operation"] |  | Good | Clear | [15 empty] | Pump Amps 12.92 ETM 24927 m Cycles 6683 Septic Sludge 5" Scum 0.50 ATU Sludge 5" Scum 7"+ Pump Sludge 1" Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/08/2020 | 01:39 PM
06/03/2020 | Alternative | Reportable Incident | 073-STS-93034 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001063 | K.R. Trapper | Davis | 2.000000 | 2000 | None | None | Pump | Distribution Box | Aggregate Trench | None | 750.000000 |  | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | [17 empty] | System inspection / commissioning for main house system installation - HDID #136-19-0405. System operational, though residence is not completed and occupied as of this date. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 06/03/2020 | 11:45 AM
03/05/2020 |  | Routine, Scheduled | 107-07-0283 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | PLAUGER, DARRIN F | 1942001173 | DARRIN | PLAUGER |  |  | Microfast | Septic Tank Only | None | None | None | None |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] |  | Slightly Musky | Clear | 8.030000 | [14 empty] | [Comments]: System functioning in accordance with regulations. Spin filter was cleaned during inspection. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 03/05/2020 | 09:11 AM
03/25/2020 |  | Routine, Scheduled | 04-160-0229 | Montgomery County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - New River | Conner, Timothy Wayne | 1942001003 | Timothy | Conner | 1.000000 | 1000 | PremierTech, EFX | None | Gravity | Distribution Box | Aggregate Trench | None | [21 empty] | [Pumpout Comments]: PUMPED AND CLEANED TANK ON 10/19/16 RECOMMEND TANK BE PUMPED EVERY 3 TO 5 YEARS. [Comments]: Everything appears to be functioning properly at this time. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/26/2020 | 01:51 PM
11/18/2020 |  | RoutineScheduled | 175-15-0386 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 | Approved | EHD - Prince William | Ace Contracting Services Inc | 1942001120 | Lawrence | Fellenz Jr. | 1.000000 |  | Puraflo | none | Pump | Gravity |  | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 |  | 06/29/2021 | 10:39 PM
09/29/2020 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump | Distribution Box |  | None |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  | 3.98 | 7.090000 | 6.700000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 09/29/2020 | Jan 1 1900 2:00PM
11/11/2020 |  | Routine, Scheduled | 175-05-0668 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Puraflo |  |  |  |  | None |  | ["Effluent Screens"] | ["Effluent Screens"] | [18 empty] | Pump Amps 5.39 ETM 121.00 Cycles 99 Septic Sludge 12" Scum 1" Pump Sludge 1" Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 11/11/2020 | 03:25 PM
05/13/2020 |  | RoutineScheduled | 069040263 | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Greenway Engineering | 1942001008 | Jeremy | Ferguson | 1.000000 | 1250 | Microfast | none | Pump | Pressure | Mound | Not Applicable |  | ["BlowerCompressorAerator Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Level Sensor Operation","SludgeScum Accumulation"] | NA | [17 empty] | System is operational | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 09/28/2020 | 10:20 AM
12/17/2020 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Pump |  |  |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Recirculation Pump","Sludge/Scum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Recirculation Pump","Sludge/Scum Accumulation"] | N/A |  |  | 7.540000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 12/17/2020 | Jan 1 1900 9:00AM
02/14/2020 |  | Routine, Scheduled | 069050085 | Frederick County | This AOSS should now return to normal function after having provided the above stated routine maintenance. | Approved | EHD - Lord Fairfax | Ferguson, Jeremy | 1942001008 | Jeremy | Ferguson | 1.000000 | 1250 | Biomicrobics MicroFAST | None | Pump | Drip | Drip Tubing | None |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | [Comments]: Replaced blower due to being locked up. System is now in compliance with approved plans and health department regulations. | This AOSS should now return to normal function after having provided the above stated routine maintenance. |  | 02/14/2020 | 02:08 PM
07/20/2020 |  | RoutineScheduled | 124-STS-2379 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Blue Ridge | Drainfield Solutions | 2705163102 | Michele | Ware | [9 empty] | [] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Auxiliary Filter","Disinfection","Distribution Pump Operation","Effluent Screens","Recirculation Pump","Septic Tank Baffles","Level Sensor Operation","Dispersal System Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
12/15/2020 |  | Follow-Up | 175-11-0248 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green | [9 empty] | ["None"] | ["None"] | [18 empty] | Repaired broken 4" clean out. | This AOSS should now return to normal function after having provided the above state routine maintenance |  | 12/15/2020 | 04:00 PM
11/25/2020 |  | RoutineScheduled |  | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Central Shenandoah | Onsite Wastewater Services - May Supply | 1942001627 | Drew | Shull | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Attached Growth Medium" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Septic Tank Baffles"] | ["Attached Growth Medium" ,"Septic Tank Baffles" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NO | None | Clear | [13 empty] | Will be sent separately | Inspected | Repair completed on Disc. Float #2 stuck "ON". | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/01/2022 | 12:13 PM
11/17/2020 |  | RoutineScheduled | 18-197-A1 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | Wise Co Health Dept |  | Rodney | Neece |  |  | Jet |  | Gravity | Gravity | Discharge | Chlorination |  |  |  |  | None | Clear | 6.000000 | 7.000000 |  | 0.000000 | System is good | [11 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 11/17/2020 | 12:00 AM
02/24/2020 |  | Routine, Scheduled |  | Culpeper County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | None | None | Pump | Distribution Box | Aggregate Trench |  |  | ["BlowerCompressorAerator Operation","Effluent Screens","None"] | ["BlowerCompressorAerator Operation","Effluent Screens","None"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/06/2020 | 02:45 PM
09/22/2020 |  | Routine, Scheduled | 175-16-0378 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green | [9 empty] | ["None"] | ["None"] |  | Acceptable | Clear | [15 empty] | Spin filter cleaned. Water Meter Reading 26360 Septic Sludge 12" Scum 0 Pump Sludge 4" Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 09/22/2020 | 04:58 PM
03/20/2020 |  | Routine, Scheduled |  | Warren County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Lord Fairfax | Cubbage, Harrison Lee, II | 1942001021 | Harrison | Cubbage | 1.000000 | 1500 | Septic Tank Only | Biomicrobics MicroFAST | Pump | Distribution Box | Aggregate Trench | None |  | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] |  | Musty | Clear | [15 empty] | [Comments]: Pump Settings: Off 2Hrs On 3min ETM-17.37HR Cycle Count-493 Sludge/Scum Accumulations: Comp.1-14"/6" Comp.2-13"/0" Pump Tank-2"/0" | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/29/2020 | 11:41 AM
10/13/2020 |  | Routine, Scheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Biomicrobics MicroFAST |  | Gravity |  |  | None |  | ["Blower/Compressor/Aerator Operation"] | ["Blower/Compressor/Aerator Operation"] |  | Acceptable | Clear | [15 empty] | Septic Sludge 4" Scum 2" ATU sludge 5" Scum 0 No pumping necessary. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 10/13/2020 | Jan 1 1900 1:25PM
04/03/2020 |  | Routine, Scheduled |  | Mathews County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Three Rivers | Farmer’s Septic Service, Inc. |  | Ross | Cole | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | [Comments]: Serviced system. Checked the pump, panel, & floats (ok). Cleaned the filter and the diffuser in the Clearstream. Changed the filter in the aerator and replaced the UV light bulb. The timer is set to 4 minutes every 1 hour. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/03/2020 | 12:00 PM
12/08/2020 |  | RoutineScheduled | 37821 | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | Musty |  | 7.210000 | 6.710000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12/21/2020 | 02:50 PM
01/27/2020 |  | Routine, Scheduled |  | Warren County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Lord Fairfax | ROYSTON, LARRY J, II | 1942001325 | LARRY | ROYSTON |  |  | Septic Tank Only | Septic Tank Only | None | None | None | None |  | ["None"] | ["None"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/17/2020 | 12:42 PM
01/10/2020 |  | Routine, Scheduled |  | Prince William County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Delta Environmental Products, DF Series |  | Pump | Drip | Drip Tubing | None |  | ["BlowerCompressorAerator Operation","Level Sensor Operation"] | ["BlowerCompressorAerator Operation","Level Sensor Operation"] |  | Good | Clear | [15 empty] | [Comments]: Spin filter cleaned.Pump Amps 10.4 ETM 1693h Cycles 127258Water Meter Reading 694140Septic Sludge 6" Scum 0.25ATU Sludge 2" Scum 0Pump Sludge 0 Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/10/2020 | 10:52 AM
06/26/2020 |  | RoutineScheduled | 175-08-0274 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | [9 empty] | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | [18 empty] | Septic tank had 4" sludge and 0' scum ATU had 0" sludge 0" scum Pump tank had 0" sludge. Cleaned air filter for blower. Registers in control panel were Pump starts-37887 Pump run-6144 Hand-38 H/L-232 WW/M-1,389,491 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
09/15/2020 |  | RoutineScheduled |  | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Catoctin Environmental |  | Cameron | Creighton | 1.000000 |  | Microfast |  | Gravity | Gravity | Trenches | Not Applicable |  | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 09/15/2020 | 12:00 AM
01/02/2020 |  | Routine, Scheduled | 179-07-0027-SR | Stafford County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Orenco Advantex | None | Pump | Distribution Box | Aggregate Trench |  |  | ["Attached Growth Medium","Dispersal System Operation","Effluent Screens","Recirculation Pump"] | ["Attached Growth Medium","Effluent Screens","Recirculation Pump"] | [18 empty] | [Comments]: The lower end of the drainfield area is starting to grow up with vines and small trees. We recommend the entire drainfield be maintained in a mowed condition. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/04/2020 | 07:46 AM
02/19/2020 |  | Routine, Scheduled | SD-07-167 | Fauquier County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson |  |  | Orenco Advantex | None | Pump | Distribution Box | Aggregate Trench |  |  | ["Control Operation","Distribution Pump Operation","Level Sensor Operation"] | ["Control Operation","Distribution Pump Operation","Level Sensor Operation"] | [18 empty] | [Comments]: In the past 30 days, the system averaged 3 discharge cycles @ 1.1 min per day. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/25/2020 | 07:16 AM
10/30/2020 |  | RoutineScheduled | 182-06-0491 | Rockingham | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Central Shenandoah | Onsite Wastewater Services - May Supply | 1942001627 | Drew | Shull | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Pressure | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/28/2021 | 05:41 AM
06/02/2020 | Alternative | Routine/Scheduled | 171-06-0791 | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | POWELLS PLUMBING, INC. | 1942001036 | Kurt | Holthaus | 1.000000 | 1000 | Puraflo |  | Pump | Distribution Box | Aggregate Trench |  | 300.000000 | ["Effluent Screens"] | ["Effluent Screens"] | N/A | [17 empty] | Annual Inspection - Serviced effluent screen(s). | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 06/15/2020 | 02:59 PM
11/09/2020 | Alternative | Routine/Scheduled | 157-11-0040 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | Serviced system. Checked the pump, panel, & floats (ok). Cleaned the filter in the Clearstream, cleaned the mesh screen in the spinfilter, and cleaned the filter in the septic tank. Changed the diffuser in the Clearstream and changed the filter in the aerator. The pipe in the Clearstream is cocked. The pump is running loud but pumping fine. The timer is set to 4 minutes every 1 hour. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 11/06/2020 | 12:00 PM
05/19/2020 |  | RoutineScheduled | 12-142-0139 | Hanover | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Cleastream |  | Gravity | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | YES | [17 empty] | We replaced the Clearstream blower. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 09/11/2020 | 12:00 AM
10/03/2020 |  | RoutineScheduled | 2042-97-153 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Wastemaster Inc |  | Timothy | Jenkins |  |  | Sequencing Bat Reactor |  |  |  | Discharge | UV |  | [] | [] |  | Musty | Clear | 6.900000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 10/20/2020 | 09:40 AM
03/26/2020 |  | Routine, Scheduled |  | Prince William County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Prince William | SEAMON, CHARLIE L | 1942001108 | CHARLIE | SEAMON |  |  | Septic Tank Only | Microfast | Pump | Distribution Box | Aggregate Trench | None |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | [8 empty] | 03/26/2020 |  | 9.000000 | [5 empty] | Attached to this report |  | [Comments]: Performance Inspection and sample:Microfast to Drainfield. Septic-4"sludge 2"scum/Microfast-0"sludge/Pump tank-0"sludge. Pump out not required.Counts:Peak-0 (n/a)/ High-5/ Pump-107 ETM-11h 37m Blower air filter cleaned. No breakout or spongy areas on the drainfield. VENIS File Names: Holly Ridge Lane 13600.pdf | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/09/2020 | 12:22 PM
12/08/2020 |  | RoutineScheduled | 179-07-0335-DS | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Wastemaster Inc |  | Timothy | Jenkins | 2.000000 |  | Advantex | Polishing SandFilter | Pump | Gravity | Discharge | UV |  | [] | [] |  |  |  | 7.600000 | [14 empty] | In for service and inspection. Sand filter effluent. pump running but not pumping, pump will need to be replaced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12/14/2020 | 07:03 PM
10/28/2020 |  | RoutineScheduled | SP-05-546 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Wastemaster Inc |  | Timothy | Jenkins | 2.000000 |  | PuraFlo | Effluent Filter | Pump | Gravity | Discharge | Chlorination |  | [] | [] |  | Musty | Clear | 7.200000 |  |  | 2.200000 | [12 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 11/20/2020 | 11:45 AM
04/17/2020 |  | Routine, Scheduled | 06-120-0728A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesterfield | Madison Environmental LLC |  | Larry | Madison, Jr. |  |  | Orenco Advantex |  | Pump | Distribution Box |  |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | [18 empty] | [Comments]: Removed roots from distribution box Lab results not reported by Operator, EHS chose "No" in order to allow saving updated entry. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/17/2020 | Jan 1 1900 9:00AM
12/02/2020 |  | RoutineScheduled | SD-07-33 | Fauquier | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Control Operation" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Level Sensor Operation"] | ["Attached Growth Medium" ,"Control Operation" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Level Sensor Operation"] | YES | [15 empty] | Will be sent separately | Inspected | Owner stated that pumper said the septic tank leaks after pump out. Infiltration at pump tank mid-seam. Effluent pump is slow. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
10/01/2020 |  | RoutineScheduled | {FIPSCode}-STS-6934 | Warren | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Lord Fairfax | Onsite Wastewater Services - May Supply | 1942001022 | Sara | Tusing | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Inspection DKS | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/28/2021 | 05:41 AM
07/27/2020 |  | Follow-Up | 179-14-0007-SWP | Stafford | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [9 empty] | 30.000000 | [5 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
04/17/2020 |  | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Greenway Engineering | 1942001008 | Jeremy | Ferguson | 1.000000 | 1500 | Advantex | none | Pump | Pressure | Drip | Not Applicable |  | ["Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 07/21/2020 | 10:30 AM
01/17/2020 |  | Reportable Incident | 09-142-0021 | Hanover County | This AOSS should now return to normal function after having provided the above stated routine maintenance. | Approved | EHD - Chickahominy | Old Dominion Onsite, Inc. |  | Jason | Hackler | 1.000000 | 1000 | Biomicrobics MicroFAST | None | Pump | Drip | Drip Tubing | None | [21 empty] | [Comments]: Alarm reported. Found bad contactor. Replaced. System appears to be operating normally. | This AOSS should now return to normal function after having provided the above stated routine maintenance. |  | 01/17/2020 | Jan 1 1900 8:15AM
09/03/2020 |  | Routine/Scheduled | SP-04-386 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1500 | Orenco Advantex | None | Pump | Distribution Box | Aggregate Trench | None | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | None | Clear | [15 empty] | Routine service conducted. Processing Tank - normal operating level - RSV, recirc pump & effluent screen serviced. Treatment Module - media drapes and spray grid serviced. Discharge Tank - Pump, float sensors and controls operating properly. Surge/Distribution box intact - removed minor root intrusion - all laterals accepting effluent. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 09/04/2020 | 07:30 AM
10/12/2020 |  | RoutineScheduled |  | Rockingham | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity |  | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Client stated that system was pumped on 10/13/2020. Riser installed at time if service | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/26/2021 | 09:04 AM
07/02/2020 |  | Follow-Up | SP-05-16 | Caroline | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Control Operation" ,"Auxiliary Filter" ,"Attached Growth Medium" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Control Operation" ,"Auxiliary Filter" ,"Attached Growth Medium" ,"Effluent Screens" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | YES | [15 empty] | Will be sent separately | Inspected | Replaced broken spin filter. Bleached and flushed drip tubing-rate was slow. Added flow meter. Cleaned ARV in headworks. Replaced pressure gauge. Replaced leaking tri-check assembly w/ quality union and gate valve. Replaced field flush auto valve. Added Orenco pod vent that was missing. Set panel correctly. Replaced low level float in recirc. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
09/16/2020 | Alternative | RoutineScheduled | 124-STS-2379 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Three Rivers | GeoEnvironmental Services, Inc. | 1942001010 | Peter | Mamunes | 0.000000 |  | Clearstream ATU |  | Pump | Pressure | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["SludgeScum Accumulation","Effluent Screens","Level Sensor Operation","Dispersal System Operation","Control Operation","BlowerCompressorAerator Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 09/24/2020 | 04:05 PM
08/12/2020 |  | RoutineScheduled | 153-STS-19104 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ EZ-Treat | Pump Tank | Pump | Pressure | Drip | UV |  | ["SludgeScum Accumulation"] | [] | NA | [9 empty] | 32.000000 | [7 empty] | Septic 4"sludge 0"scum/ EZ-Treat-0"sludge/Pump Tank-0"sludge (Spoke to owner about excessive fats,oils and grease in the tank and recommend a pump out to protect the EZ-Treat. Found broken 24"lid on the septic tank and the owner stated he will replace. Owner also requested moving the supply/return drip pipes to accommodate a pool, informed him to speak to his builder. No breakout or spongy areas on the drip field. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  |  | 12:00 AM
03/10/2020 |  | Routine, Scheduled | SWP-03-379/SWT-04-225 | King George County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001350 | Mike | Cook | 1.000000 |  | None | None | Pump | Distribution Box | Aggregate Trench |  |  | ["Attached Growth Medium","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/18/2020 | 06:42 AM
12/22/2020 |  | RoutineScheduled | SWP-04-154 | King George | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | ["Distribution Pump Operation" ,"Level Sensor Operation" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Dispersal System Operation" ,"Attached Growth Medium"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced broken effluent filter during yearly inspection. Alarm panel not working will be replaced when I'm in the area. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
11/18/2020 |  | RoutineScheduled |  | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - New River | MSS INC |  | Tim | Conner | 1.000000 | 1500 | MIRCOFAST |  | Gravity | Gravity | Trenches | Not Applicable |  | ["on"] | ["on"] | YES | Septic | Clear | [5 empty] | 11/18/2020 | Sample Chamber | [6 empty] | Attached to this report | Inspected | TANK NEEDS TO BE PUMPED AND CLEANED. INLET KICKED UP IN TANK; MAY NEED REPLACED IN THE FUTURE IF PROBLEMS OCCUR. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 11/18/2020 | 12:00 PM
03/18/2020 |  | Routine, Scheduled | 69140009 | Frederick County | This AOSS should now return to normal function after having provided the above stated routine maintenance. | Approved | EHD - Lord Fairfax | Cubbage, Harrison Lee, II | 1942001021 | Harrison | Cubbage | 1.000000 | 1500 | Septic Tank Only | Biomicrobics MicroFAST | Pump | Drip | Drip Tubing | None |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation"] |  | Musty | Clear | [15 empty] | [Comments]: Replaced bad override float at time of service Pump Settings: Off 2.5Hr On 12.5min ETM-880.98Hr Cycle Count-4688 Sludge/Scum Accumulations: Comp.1-13"/2" Comp.2-13"/1" Pump Tank-6"/0" | This AOSS should now return to normal function after having provided the above stated routine maintenance. |  | 03/29/2020 | 12:03 PM
03/02/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Paid | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green |  |  |  |  | Pump | Manifold | Aggregate Trench | None |  | ["Distribution Pump Operation","Effluent Screens"] | ["Effluent Screens"] | [18 empty] | [Comments]: LPD.Check valves need replacing.Pump 1 Amps 17.20Pump 2 Amps 15.05Septic Sludge 6" Scum 1"Pump Sludge 1" Scum 0 | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 03/02/2020 | Jan 1 1900 1:55PM
05/28/2020 |  | RoutineScheduled | 061-16-250 | Fauquier | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 5.000000 |  | Bio Barrier | Bio Barrier | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter"] | ["Control Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | Biweekly inspection. Cleaned air filter. Spin filter split on one side. Installed used one until new one is obtained. Grass has been cut around tanks, but grass in drip field is almost waist high. In the past 14 days, the drip flow meter advanced by 20,643 gals (1,474.5 gals/day, 208.5 gals per cycle). The recirc pump total was approximately 55,267 gals (38.38 hrs x 24 GPM). The surge pumps total was approximately 52,416 gals (33 hrs 36 min x 26 GPM). Need to add a peak float to the surge tank so that the dosing to the Fast tank can be slowed down in low flow conditions and hopefully improve treatment. | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
01/24/2020 |  | Routine, Scheduled | 04-137-0475 | Goochland County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chickahominy | Mamunes, Peter S. | 1942001010 | Peter | Mamunes | 1.000000 | 1000 | Best 1 | None | Gravity | Distribution Box | Aggregate Trench | None | 450.000000 | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | [18 empty] | [Comments]: ST sludge = 8" ST scum = 1" | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/18/2020 | Jan 1 1900 1:07PM
08/03/2020 |  | Initial Visit | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Fairfax | Ashleys Septic Service | 1930332 | Shane | Majewski | 1.000000 | 1200 | [7 empty] | ["Level Sensor Operation"] | ["Level Sensor Operation"] | NO | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 08/11/2020 | Jan 1 1900 11:07AM
04/07/2020 |  | Routine, Scheduled | SD-06-072 | Orange County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | JENKINS, TIMOTHY R | 1942001062 | TIMOTHY | JENKINS | 1.000000 |  | Aero-flo ATU | Septic Tank Only | None | Drip | Alternative Discharge | Chlorine |  | ["None"] | ["None"] |  | Musty | Clear | 7.300000 |  | 35.000000 | 2.200000 | [11 empty] | [Comments]: Functioning as Designed | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/20/2020 | 04:00 AM
08/05/2020 |  | Routine/Scheduled |  | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Pump | Distribution Box | Aggregate Bed | None |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Recirculation Pump","Sludge/Scum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Recirculation Pump","Sludge/Scum Accumulation"] | N/A |  |  | 8.000000 | 3.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 08/05/2020 | Jan 1 1900 9:30AM
09/21/2020 | Alternative | RoutineScheduled | {FIPSCode}-STS-51112 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
03/31/2020 |  | Routine, Scheduled | 02-163-0408 | New Kent County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chickahominy | TIMBERLAKE, LOUIS RHEA | 1942001339 | LOUIS RHEA | TIMBERLAKE | 1.000000 | 1000 | Orenco Advantex | Septic Tank Only | Pump | Drip | Drip Tubing | None | 600.000000 | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Recirculation Pump","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/13/2020 | Jan 1 1900 2:50PM
07/16/2020 |  | Initial Visit | TELS-BC6JQN | Southampton | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | Serviced system. Checked the pump, panel, & floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. The aerator should be raised. Replaced the alarm light bulb. The timer is set to 2 minutes every 2 hours. Took initial BOD sample. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 07/16/2020 | Jan 1 1900 12:00PM
10/08/2020 |  | Routine, Scheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Puraflo | [6 empty] | ["Effluent Screens"] | ["Effluent Screens"] | [18 empty] | Septic Sludge 3" Scum 1" Pump Sludge 1" Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 10/08/2020 | Jan 1 1900 11:39AM
09/03/2020 |  | Routine, Scheduled | 175-02-0054 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Aquarobic Mini Plant |  |  |  |  | None |  | ["Blower/Compressor/Aerator Operation"] | ["Blower/Compressor/Aerator Operation"] |  | Good | Tan | [15 empty] | Pump Amps 5.90 No pumping necessary. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 09/03/2020 | 09:10 AM
12/22/2020 | Alternative | RoutineScheduled | 171-13-0276 | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | Musty | Cloudy | 7.060000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 01/13/2021 | 10:50 AM
09/28/2020 |  | Routine/Scheduled |  | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump | Distribution Box | Aggregate Bed | None |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  | 7.83 | 7.190000 | 6.600000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 09/28/2020 | Jan 1 1900 2:30PM
03/12/2020 |  | Initial Visit | 067-STS-37840 | Franklin | This AOSS is functioning as designed and in accord | Approved | EHD - West Piedmont |  |  |  |  | 1.000000 | 1000 |  | Orenco Advantex | Gravity | Distribution Box | Aggregate Trench | None |  | ["Control Operation"] | ["Control Operation"] | [18 empty] | [Comments]: Ran system in test mode, checked filter (New) Set Pump run time to 45 seconds on 19.7 off and 9.7 min in overide. Alarm and pump operational, floats wired correctly System On & ready for operation | This AOSS is functioning as designed and in accord |  | 03/12/2020 | 11:51 PM
05/29/2020 |  | RoutineScheduled | SD-07-172 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Soils, Inc. | 1940001392 | Markham | Smith | 2.000000 | 1500 | Peat filter PuroFlo (6 Pods ) |  | Pump | Gravity | Trenches |  | 65.500000 | [] | ["Septic Tank Baffles","SludgeScum Accumulation","Distribution Pump Operation","Attached Growth Medium","Control Operation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 05/14/2020 | 04:05 PM
07/07/2020 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump | Distribution Box |  | None |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  |  | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 07/07/2020 | Jan 1 1900 2:15PM
01/29/2020 |  | Routine, Scheduled | 05-113-116 | Buchanan County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Cumberland Plateau | DEEL, DENNY M | 1942001097 | DENNY | DEEL |  |  |  | None | Gravity | Distribution Box | Aggregate Bed | None | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Effluent Screens"] |  | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/05/2020 | Jan 1 1900 2:27PM
06/11/2020 | Alternative | Routine/Scheduled | 136-18-0297 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1500 | Biomicrobics Retrofast |  | Pump | Drip | Drip Tubing | None | 450.000000 |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | Musty | Clear | [15 empty] | Routine service conducted. Trash tank - 14" sludge, 1" scum Aeration operating properly - blower serviced. Discharge operating properly - drip screens serviced - all zones accepting effluent. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 06/15/2020 | 07:30 AM
03/11/2020 |  | Routine, Scheduled |  | Loudoun County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | None | None | Pump | Manifold | [24 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/12/2020 | 02:21 PM
07/16/2020 |  | RoutineScheduled | 181-05-0097 | Rockbridge | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Central Shenandoah | Onsite Wastewater Services - May Supply | 1942001022 | Sara | Tusing | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Pressure | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | INSPECTION BY DS | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/28/2021 | 05:41 AM
04/16/2020 |  | Routine/Scheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | POWELLS PLUMBING, INC. | 1942001036 | Kurt | Holthaus | 1.000000 | 1500 | Microfast |  | Pump | Drip | Drip Tubing |  | 450.000000 | ["Effluent Screens","Sludge/Scum Accumulation"] | ["Effluent Screens","Sludge/Scum Accumulation"] | N/A | [17 empty] | Annual Inspection - Serviced spin filter and effluent screen(s). Pumped Microfast tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 05/13/2020 | 01:58 PM
05/21/2020 | Alternative | Initial Visit | 073-STS-105191 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1250 | Clearstream ATU | None | Pump | Distribution Box | Aggregate Trench | None |  |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | Alarm was found active for several days; the Aeration Tank has a non-serviceable Air Line, and the Riser had root infiltration; the Air Pump was found deteriorated, corroded, and not functioning properly; the Air Pressure Sensor was found without the proper signal wire; the Plumbing in the Discharge Tank is outdated; in the Control Panel, the Push-to-Silence Button was not operating properly; the Distribution Box was found with broken Seals, and one Drain Line was root bound | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 05/27/2020 | 10:56 AM
05/08/2020 |  | Follow-Up |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | SES MidAtlantic LLC | 1942001203 | James | Green |  |  | Clearstream | none | Pump | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation"] | ["Dispersal System Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced K4000 zoner. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/15/2021 | 09:00 AM
09/10/2020 |  | RoutineScheduled |  | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Prince William | Onsite Wastewater Service | 1942001223 | MATTHEW | FERRELL | 1.000000 | 1500 | Aquarobics |  | Gravity | Pressure | Mound | Not Applicable | 450.000000 | ["None"] | ["None"] | NA | None | Cloudy | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 09/10/2020 | 12:00 AM
09/10/2020 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump | Drip | Elevated Sand Mound | UV Light |  | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  |  | 7.330000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 09/10/2020 | Jan 1 1900 9:45AM
11/05/2020 |  | Follow-Up | 179-14-0301-SP | Stafford | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [7 empty] | 10/05/2020 |  | 10.000000 | [5 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
05/06/2020 |  | Routine/Scheduled | 147-15-0095 | James City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Peninsula | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | Serviced system. Checked the pump, panel, & floats (ok). Cleaned the filter and the diffuser in the Clearstream. Changed the filter in the aerator. The timer is set to 3 minutes every 2 hours. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 05/06/2020 | Jan 1 1900 12:00PM
06/09/2020 |  | RoutineScheduled |  | Rockingham | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 4.000000 |  | Biomicrobics MicroFAST | Biomicrobics MicroFAST | Pump | Pressure | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter" ,"Control Operation" ,"Dispersal System Operation"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | No flow from Zerx Tank to ET BEd Replaced PT3 Pump Will be returning to site and cleaning necessary tanks | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 |  | 04/26/2021 | 09:04 AM
03/06/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Biomicrobics MicroFAST |  |  |  |  | UV Light |  | ["BlowerCompressorAerator Operation","Disinfection"] | ["BlowerCompressorAerator Operation","Disinfection"] |  | Good | Good | [15 empty] | [Comments]: Spin filter cleaned.Pump Amps 8.40 ETM 510h Cycles 5518Water Meter Reading 199900Septic Sludge 6" Scum 4"ATU Sludge 16" Scum 0Pump Sludge 0 Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/06/2020 | Jan 1 1900 12:41PM
12/11/2020 |  | RoutineScheduled | S-12-111-0081 | Botetourt | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | Hunter E. Ayres, General Contractor | 1942001166 | Hunter | Ayres | 3.000000 | 6000 | Ecopod |  | Pump | Pressure | Trenches | Not Applicable |  | ["Auxiliary Filter","Effluent Screens"] | ["Auxiliary Filter","Effluent Screens"] | YES | [17 empty] | Filters checked and cleaned. No apparent leaks in system or drain field area. Pumps and control panels functioning properly. System did not need to be pumped. All child safety nets in place and in good condition. All lids properly secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 01/05/2021 | Jan 1 1900 11:00AM
03/10/2020 |  | Routine, Scheduled |  | Warren County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Lord Fairfax | Ferguson, Jeremy | 1942001008 | Jeremy | Ferguson | 1.000000 | 1000 | Ecoflo | None | Gravity | Distribution Box | Aggregate Trench | None | 100.000000 | ["Attached Growth Medium","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","Effluent Screens","SludgeScum Accumulation"] | [18 empty] | [Comments]: The septic tank levels were inspected and do not meet the minimum recommended levels to pump out. The peat moss was raked and releveled as part of the inspection. The entire system is operational and in working order. no issues found | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/12/2020 | 12:05 AM
05/04/2020 | Alternative | RoutineScheduled | 151-12-0139 | Lancaster | This AOSS is functioning as designed and in accord | Approved | EHD - Three Rivers | [13 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accord |  |  | 12:00 AM
09/29/2020 |  | Initial Visit | 12-142-0160 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chickahominy | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1500 | Hoot |  | Pump | Drip | Drip Tubing | None | 600.000000 |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | Musty | Clear | [15 empty] | Initial visit - Service Trash Tank - normal operating level Aeration Tank - Normal operating level - Compressor serviced. Pump Tank - normal operating level - discharge pump serviced - sensor probe & controls operating properly. Drip field - serviced disk filter - wet spots over drip field - abnormally heavy rains and entire property has standing water - unknown if this is surfacing. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 10/07/2020 | Jan 1 1900 7:15AM
01/18/2020 |  | Routine, Scheduled | 179-11-0239-SP | Stafford County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Puraflo | None | Pump | Distribution Box | Aggregate Trench |  |  | ["Control Operation","Level Sensor Operation"] | ["Control Operation","Level Sensor Operation"] | [18 empty] | [Comments]: Effluent level high due to pressure transducer reading incorrectly. Replaced transducer and programmed panel with new zero bias code. Also, set date and time. Will return in next 2 weeks to collect 5-year BOD sample. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/28/2020 | 01:39 PM
05/19/2020 |  | RoutineScheduled | 069050247 | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 2705110225 | Larry | Royston | 2.000000 | 2 | 1000 | 1000 | Pump | Pressure | Drip | Not Applicable |  | ["None","Auxiliary Filter"] | ["Auxiliary Filter"] | YES | None | Cloudy | [14 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 06/10/2020 | 03:40 PM
06/03/2020 |  | Routine, Scheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Biomicrobics Retrofast |  |  |  |  | None |  | ["Blower/Compressor/Aerator Operation"] | ["Blower/Compressor/Aerator Operation"] |  | Good | Brown | [15 empty] | Pump 1 Amps 9.61 ETM 189 hrs 53 mins Cycles 38805 Pump 2 Amps 10.34 ETM 181 hrs 50 mins Cycles 39819 Water Meter Reading 1979340 Septic Sludge 12" Scum 3" Pump Sludge 3" Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 06/03/2020 | Jan 1 1900 9:28AM
09/23/2020 |  | Follow-Up | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance | Approved | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green | [9 empty] | ["Disinfection"] | ["Disinfection"] | [18 empty] | Replaced UV Bulb & chord. Replaced spin filter. | This AOSS should now return to normal function after having provided the above state routine maintenance |  | 09/14/2020 | Jan 1 1900 4:00PM
07/27/2020 |  | RoutineScheduled | 069050897 | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | ["None"] | ["None"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
10/14/2020 |  | Routine/Scheduled | 2006-143-0270 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Henrico | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1500 | Microfast |  | Pump | Drip | Drip Tubing | None | 600.000000 |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | Musty | Clear | [15 empty] | Routine Service Trash Tank - normal operating level BioMicrobics - Normal operating level - mixing properly - compressor serviced. Pump tank - normal operating level - pump serviced - float sensors and controls operating properly. Drip Field - headworks serviced - drip screen serviced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 10/16/2020 | 11:45 AM
11/17/2020 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Gravity | Gravity |  | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | An inspection of a conventional gravity septic system. The state requires that all conventional septic tanks must be pumped out EVERY 5 years and filed with the state and the county. There is a pvc cleanout near the house. The sewer line was camera snaked and was clear. The septic tank was pumped out and inspected. The tank is at ground level. The conveyance line was camera snaked and was clear. The The 9 port plastic d-box was dug up it was 12" under the ground. All 6 header lines were camera snaked and were clear. The drain field was probed and was dry. At time of inspection all components were in working condition | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 |  | 04/14/2021 | 04:27 PM
05/12/2020 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Aquarobic Services | 1934000142 | Michael | Blake |  |  | none | none | Pump | Gravity | Mound | Not Applicable |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | Annual inspection. Air pre-filter cleaned as routine maintenance. Moisture penetration/ streaking observed at bulkhead adapter for discharge pipe. No mechanical fitting (conduit or pipe) was used between blower housing and mechanical manway. Minor moisture penetration visible there as well. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 07/01/2022 | 10:30 AM
09/18/2020 |  | Routine, Scheduled | 175-05-0974 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Puraflo |  |  |  |  | None |  | ["Effluent Screens","Sludge/Scum Accumulation"] | ["Effluent Screens","Sludge/Scum Accumulation"] | [18 empty] | Septic tank pumped 09/18/2020 Pump Amps 12.89 ETM 360.77 Cycles 22602 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 09/18/2020 | 11:30 AM
09/21/2020 |  |  | 08-142-0016 | Hanover | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Best One | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | YES | [17 empty] | Replaced the transducer 10/8/20 | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 10/23/2020 | 12:00 AM
06/16/2020 |  | RoutineScheduled | 177-11-0223-SP | Spotsylvania | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Septic Works LLC | 1942001080 | michael | smith |  |  | Orenco Advantex | Orenco Advantex | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/25/2021 | 08:10 AM
06/02/2020 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES MidAtlantic LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 |  | 04/15/2021 | 09:00 AM
06/10/2020 | Alternative | Reportable Incident | 119-STS-106021 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 750 | None | None | Gravity | Distribution Box | Aggregate Trench | None | 450.000000 | ["Septic Tank Baffles"] | ["Dispersal System Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | [17 empty] | Septic tank pumped empty due to report of slow drains. Building sewer line pressure jetted and removed clog in sewer. Septic tank baffles (T's) are cast iron, heavily corroded and should be replaced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 06/15/2020 | 08:00 AM
04/14/2020 |  | Routine, Scheduled |  | Albemarle County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Blue Ridge | CLARK, MICHAEL J | 1934000023 | MICHAEL | CLARK |  |  | Septic Tank Only | Septic Tank Only | None | None | None | None |  |  | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/19/2020 | 04:18 AM
07/06/2020 |  | Follow-Up |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Aquarobic Services | 1934000142 | Michael | Blake |  |  | none | none | Pump | Gravity | Mound | Not Applicable |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | Access manway had thin spots in fiberglass that eventually wore through and created holes. Access manway (inlet end) removed, tank top heated dry, power brushed clean and new manway installed. Cleaned the air pre-filter as preventative maintenance. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 07/01/2022 | 10:30 AM
08/13/2020 |  | RoutineScheduled | 16-183-005 | Russell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Effluent Screens"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
04/16/2020 |  | RoutineScheduled |  | Frederick | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Lord Fairfax | Aquarobic Services | 1934000142 | Michael | Blake |  |  | none | none | Pump | Gravity | Mound | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | Single point aeration has developed, chunk of diffuser observed floating in tank. Tank will need pumped out to complete repairs. Filterbed manifold is clogged which is causing effluent to be ejected from vent pipe during pump cycles. One tree is dead, and another one has fallen on a nearby fence. Force main is exposed where it connects to the filterbed. Should be rerouted to the inside of manifold to protect it. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 07/01/2022 | 10:30 AM
01/06/2020 |  | Routine, Scheduled | 234-01-7862 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesapeake | R & K Septic, Inc. |  | John | Butt, Jr |  |  | Clearstream ATU |  | Pump | Distribution Box | Aggregate Bed | UV Light |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] |  |  | 2.77 | 7.850000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/06/2020 | Jan 1 1900 12:15PM
12/22/2020 |  | RoutineScheduled | 196-07-035 | Westmoreland | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | EcoPod | none | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 |  | 04/09/2021 | 03:25 PM
04/01/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 | Approved | EHD - Loudoun | SES MidAtlantic LLC | 1942001203 | James | Green |  |  | Clearstream | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Dispersal System Operation" ,"Level Sensor Operation"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | [9 empty] | 215.000000 | [5 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. Clearstream unit has bad float Needs timer float New zoner (hit by lawnmower) | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 |  | 04/15/2021 | 09:00 AM
05/13/2020 |  | Follow-Up |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | FIXED RISER | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/14/2021 | 04:27 PM
01/22/2020 |  | Routine, Scheduled |  | Louisa County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Blue Ridge | Mamunes, Peter S. | 1942001010 | Peter | Mamunes | 1.000000 | 1000 | Whitewater ATU | None | Gravity | Distribution Box | Aggregate Trench | None | 450.000000 | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | [Comments]: replaced blower, rewire alarm float | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/28/2020 | 12:47 PM
03/27/2020 |  | Routine, Scheduled | 234-14-447 | Chesapeake | This AOSS should now return to normal function after having provided the above stated routine maintenance. | Approved | EHD - Chesapeake | Farmer's Septic Service, Inc. |  | Ross | Cole | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | [Comments]: Serviced system. Checked the pump, panel, & floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream, changed the filter in the aerator, and changed the mesh screen in the spinfilter. Replaced the UV light bulb and UV cord (Salcor). Aerator needs to be raised. The pump tank needs a new 24" Tuf-Tite dome lid. The timer is set to 6 minutes every 2 hours. | This AOSS should now return to normal function after having provided the above stated routine maintenance. |  | 03/27/2020 | Jan 1 1900 12:00PM
06/08/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | SES MidAtlantic LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/15/2021 | 09:00 AM
05/14/2020 |  | Reportable Incident |  | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | [9 empty] | ["Control Operation"] | ["Control Operation"] | [18 empty] | Replaced control panel and three floats that had been struck by lighting. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  |  | 12:00 AM
09/28/2020 |  | Reportable Incident |  | Loudoun | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Loudoun | POWELLS PLUMBING, INC. | 1942001036 | Kurt | Holthaus | [9 empty] | ["Distribution Pump Operation"] | ["Distribution Pump Operation"] | N/A | [17 empty] | Pumped pump chamber and replaced sewer pump. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 11/19/2020 | 03:12 PM
01/23/2020 |  | Routine, Scheduled | 109-14-0120 | Bedford County | This AOSS should now return to normal function after having provided the above stated routine maintenance. | Approved | EHD - Central | WAUGH, IAIN C | 1942001512 | IAIN | WAUGH | 1.000000 | 1500 | Septic Tank Only | Aqua Klear | Pump | Drip | Drip Tubing | None |  | ["Dispersal System Operation"] | ["Dispersal System Operation"] | [18 empty] | [Comments]: Owners had puddling water in drain field near old repair site after Freezing cold weather. Found 3 holes in Drip tubing & repaired. Possibly more to be located in vicinity. Nothing actively puddling. Clay soil has heavy slate and during install a truck had accidentally backed up onto the area causing previous damage. | This AOSS should now return to normal function after having provided the above stated routine maintenance. |  | 01/26/2020 | 12:09 PM
09/17/2020 |  |  |  | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | McKim Construction | 1942001330 | Michelle | McKim | 2.000000 |  |  |  | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 11/13/2020 | Jan 1 1900 9:45AM
09/01/2020 |  | RoutineScheduled | {FIPSCode}-STS-58318 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Wastemaster Inc |  | Timothy | Jenkins | 2.000000 |  |  |  | Pump | Gravity | Mound | Chlorination |  | [] | [] |  | Musty | Clear | 6.300000 |  |  | 2.200000 | [12 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 09/10/2020 | 03:45 PM
03/18/2020 |  | Routine, Scheduled | 179-06-0241-SWP | Stafford County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001350 | Mike | Cook | 1.000000 |  | Puraflo | None | Pump | Distribution Box | Aggregate Bed |  |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/01/2020 | 06:33 AM
04/18/2020 |  | Routine, Scheduled | SD-04-347 | Culpeper County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | JENKINS, TIMOTHY R | 1942001062 | TIMOTHY | JENKINS | 1.000000 |  | Sandfilter, Non-recirculating | None | None | Drip | Alternative Discharge | Chlorine |  | ["None"] | ["None"] |  | Musty | Clear | 7.200000 |  |  | 1.900000 | [11 empty] | [Comments]: Functioning as Designed | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/24/2020 | 02:51 PM
04/02/2020 |  | Routine, Scheduled | 17-172-0336A | Powhatan County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesterfield | Farmer’s Septic Service, Inc. |  | Ross | Cole | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | [Comments]: Serviced system. Checked the pump, panel, & floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream, changed the filter in the aerator, and changed the mesh screen in the spinfilter. Drainfield has visible wetness - need to keep an eye on it. Need to watch the water usage - the drainfield needs to have good vegetation over top of the entire drainfield. The timer is set to 10 minutes every 2 hours. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/02/2020 | Jan 1 1900 12:00PM
10/08/2020 |  | Routine, Scheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Puraflo |  |  |  |  | None |  | ["Effluent Screens"] | ["Effluent Screens"] | [18 empty] | Recommend BOD sampling for Puraflo modules. Pump 1 Amps 6.02 ETM 189 hrs Cycles 13582 Pump 2 Amps 6.01 ETM 187 hrs Cycles 13506 Septic Sludge 5" Scum 2" Pump Sludge 3" Scum 0 On 54 secs Off 2 hrs | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 10/08/2020 | Jan 1 1900 9:50AM
10/14/2020 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Pump | Distribution Box |  | None |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Recirculation Pump","Sludge/Scum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Recirculation Pump","Sludge/Scum Accumulation"] | N/A |  | 6.81 | 7.270000 | 3.300000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 10/14/2020 | Jan 1 1900 11:00AM
05/21/2020 |  | RoutineScheduled | SD-11-391 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Soils, Inc. | 1940001392 | Markham | Smith | 2.000000 | 1500 | PuroFlo |  | Pump | Gravity | Pad | Not Applicable | 61.500000 | [] | ["Attached Growth Medium","Control Operation","SludgeScum Accumulation","Level Sensor Operation"] | NA | [17 empty] | Septic 3scum 22sludge Pump Tank 0 scum 2 sludge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 07/13/2020 | 12:00 AM
06/25/2020 |  | RoutineScheduled | 177-10-0096-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | EcoPod | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter" ,"Distribution Pump Operation" ,"Dispersal System Operation"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | NA | [15 empty] | Will be sent separately | Inspected | We recommend removing the small pine trees & vines growing close to the drip mound. The mound surrounding area should be maintained in a mowed condition. | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 |  | 04/09/2021 | 03:25 PM
10/12/2020 | Alternative | Routine/Scheduled | 151-10-0077 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 2.000000 | 3500 | Ecoflo |  | Pump | Distribution Box | Aggregate Trench |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | Had to replace reflow dipper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 10/12/2020 | 02:30 PM
03/23/2020 |  | Routine, Scheduled | SWP-02-110 | Stafford County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Biomicrobics MicroFAST | None | Pump | Drip | Drip Tubing |  |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Distribution Pump Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Distribution Pump Operation"] | [18 empty] | [Comments]: Replaced defective alarm horn. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/06/2020 | 02:45 PM
07/07/2020 |  | RoutineScheduled |  | Warren | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Puraflo | none | Pump | Gravity |  | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter"] | ["Control Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/26/2021 | 09:04 AM
12/03/2020 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Ashleys Septic Service | 1930332 | Shane | Majewski | 1.000000 | 1500 |  |  | Pump | Gravity | Drip | Not Applicable | 700.000000 | ["None"] | ["None"] | YES | [7 empty] | 12/03/2020 | Sample Chamber | 6.000000 |  |  | 4.100000 |  |  | Attached to this report | Pumped Out | Microfast system | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12/18/2020 | Jan 1 1900 10:10AM
05/12/2020 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Aquarobic Services | 1934000142 | Michael | Blake |  |  | none | none | Pump | Gravity | Mound | Not Applicable |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | Annual inspection. Replaced air pre-filter and filter cloth for the blower housing vent. Access manway has thin spots that have worn down so now there are holes in the fiberglass. Recommended riser replacement. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 07/01/2022 | 10:30 AM
06/08/2020 |  | Reportable Incident | 175-13-0518 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green | [9 empty] | ["Blower/Compressor/Aerator Operation"] | ["Blower/Compressor/Aerator Operation"] | [18 empty] | Rebuild Clearstream compressor. | This AOSS should now return to normal function after having provided the above state routine maintenance |  | 06/08/2020 | 08:30 AM
01/29/2020 |  | RoutineScheduled | 08-113-227 | Buchanan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | DEEL, DENNY M | 1942001097 | DENNY | DEEL |  |  | Norweco Singulair ATU | None | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens"] |  | Musty | Clear | [15 empty] | [Comments]: 5 Blue Crystal 15 Bio Max Added | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 02/05/2020 | Jan 1 1900 2:24PM
05/05/2020 |  | Reportable Incident | SD-97-164 | Fauquier | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Distribution Pump Operation" ,"Auxiliary Filter"] | ["Auxiliary Filter" ,"Distribution Pump Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Pump tank in high level alarm. Flow rate down to 1/2 gpm. Cleaned debris from under diaphragms in both filter backwash valves, cleaned disc filters, cleaned pump intake (clogged) and cleaned effluent filter (very dirty). Flow rate increased to 4.2 gpm. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
03/06/2020 |  | Routine, Scheduled |  | Fluvanna County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Blue Ridge | CLARK, MICHAEL J | 1934000023 | MICHAEL | CLARK |  |  | Septic Tank Only | Septic Tank Only | None | None | None | None |  |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/17/2020 | 04:46 AM
04/28/2020 |  | Routine/Scheduled | 2003-143-0306 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Henrico | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1500 | Orenco Advantex | None | Pump | Distribution Box | Aggregate Trench | None |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | [17 empty] | Recirculation Pump & Floats have exceeded life expectancy, and there was heavy sludge found in the Processing Tank; in the Advantex Media Unit, the Media Sheets have exceeded their life expectancy and are no longer filtering water properly; the Discharge Pump and Floats have exceeded their expected life | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 05/20/2020 | 02:40 PM
11/09/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | SES MidAtlantic LLC | 1942001203 | James | Green | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [7 empty] | 11/09/2020 |  | 14.000000 | [5 empty] | Will be sent separately | Inspected | Pump Tank - Sludge 2" Scum 0 Recir Treatment Tank #1 - Sludge 1" Scum 1" Recir Treatment Tank #2 - Sludge 0 Scum 0 Recir Calcite Tank Sludge 0 Scum 0 Septic Tank #1 Sludge 12" Scum 10" Septic Tank #2 Sludge 6" Scum0 Water Meter Reading 255700 Panel #1 EQ Tank Pump #1 Amps 6.55 Pump #2 Amps 6.63 Cycle Count 3737/3720 ETM 4422 hrs/4420 hrs Off 15 mins On 3 mins Panel #2 Recir Tank #1 Pump #1 Amps 6.55 Pump #2 Amps 6.63 On 3 mins Off 3 mins 45 secs Panel #3 Recir Tank #2 Pump #1 Amps 10.04 Pump #2 Amps 10.15 On 3 mins Off 4 mins Panel #4 D Nit Tank Pump Amps 9.02 Cycles 531 On 2 mins Off 3 hrs Panel #5 Calcite Recir Pump Amps 5.27 On 3 mins Off 30 mins 2380 gpd EZ Treat | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/15/2021 | 09:00 AM
03/10/2020 |  | Routine, Scheduled |  | Loudoun County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | None | None | Pump | Manifold | [24 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/12/2020 | 02:21 PM
01/15/2020 |  | Routine, Scheduled |  | Page County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Lord Fairfax | Cubbage, Harrison Lee, II | 1942001021 | Harrison | Cubbage | 1.000000 | 1500 | Septic Tank Only | Biomicrobics MicroFAST | Pump | Drip | Drip Tubing | None |  | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation"] | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation"] |  | Musty | Clear | [15 empty] | [Comments]: Added solution to media to help with sludge Pump Settings: Off 2.5Hr On 7.5min ETM-368.86Hr Cycle COunt-1225 Sludge/Scum Accumulations: Comp.1-14"/4" Comp.2-14"/1" Pump Tank-3"/0" | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/18/2020 | 12:44 PM
08/24/2020 |  | Follow-Up | SD-12-261 | Fauquier | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | UV |  | ["Control Operation" ,"Auxiliary Filter" ,"Level Sensor Operation"] | ["Auxiliary Filter" ,"Level Sensor Operation" ,"Control Operation"] | NA | [9 empty] | 7.000000 |  | 1.800000 |  |  |  | Will be sent separately | Inspected | Treatment has improved tremendously in the past 2 weeks. Drip RO float is as low as it can go. Lowered timer float 1" . Difficult to get proper dose and more difficult when field flushing. Recommend replacing small pump basin with proper 1,000 gal pump tank. Drip rate is still well below design. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
12/24/2020 |  | RoutineScheduled | 159-13-0065 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Church View Septic Service Inc. | 1942001302 | Charles | Langford | 1.000000 | 1000 | Clearstream |  | Pump |  | Pad | Not Applicable |  | ["None"] | ["None"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 01/07/2021 | 12:00 AM
07/21/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | SES MidAtlantic LLC | 1942001203 | James | Green | 1.000000 |  | Delta Environmental Products, DF Series | none | Gravity | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Dispersal System Operation"] | ["Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | Repairs scheduled: Install new compressor Install K4000 3 Zone | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 |  | 04/15/2021 | 09:00 AM
04/24/2020 |  | Routine, Scheduled | 109-15-0366 | Bedford County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Central | WAUGH, IAIN C | 1942001512 | IAIN | WAUGH | 1.000000 | 1000 | Septic Tank Only | Orenco Advantex | Pump | Distribution Box | Aggregate Trench | None |  | ["Control Operation","Effluent Screens"] | ["Control Operation","Effluent Screens"] | [18 empty] | [Pumpout Comments]: No Pumping needed [Comments]: Septic Tank 1" scum 6" sludge (4" new 2" old) Recirc tank trace Discharge 16-18" light sludge- A bit high Cleaned Bio-filter - ran pump and flushed spray nozzle- Computer control still in startup mode company recommended to change trending data to last year set at two days but still in startup | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/24/2020 | 10:54 PM
07/21/2020 |  |  | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 2705051738 | Joshua | Hott | [9 empty] | ["None"] | ["None"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
06/13/2020 |  | RoutineScheduled | 133 12 0033 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1000 | Advantex |  | Pump | Gravity | Trenches |  |  | ["None"] | ["None"] | [18 empty] | 10" in septic tank. Flushed treatment unit spray manifold. Cleaned septic tank filter. Cleaned recirculation pump screen. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 09/22/2020 | 07:03 PM
07/21/2020 |  | Initial Visit |  | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Western Tidewater | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | PremierTech, EFX | None | Pump | Distribution Box | Aggregate Trench | None | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | [17 empty] | Initial service visit. Primary septic tank in normal level - effluent screen serviced. Premier Tech Concrete unit - peatmoss biofilter in good condition raked / turned Pump station at normal lever - integral to concrete unit - pump and float sensors operating properly. Distibution box in normal level - all laterals accepting effluent. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 07/22/2020 | Jan 1 1900 8:00AM
08/13/2020 |  | RoutineScheduled | 175-04-0477 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William |  |  | James | Kleindl | 2.000000 | 1875 | puraflo |  | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
04/16/2020 |  | RoutineScheduled | SD-92-200 | Culpeper | This AOSS is functioning as designed and in accord | Approved | EHD - Rappahannock-Rapidan | Wastemaster |  | Douglas | Crooks | 2.000000 |  |  | Polishing Sandfilter | pump |  | discharge | Chlorine |  | [] | [] |  | Low | Clear | 6.800000 |  |  | 2.200000 |  | 04/16/2020 |  | 3.000000 |  |  | 2.700000 |  |  | Attached to this report |  | Functioning as Designed | This AOSS is functioning as designed and in accord |  |  | 12:00 AM
02/24/2020 |  | Routine, Scheduled | 228-03-0237 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Virginia Beach | [8 empty] | Pump |  |  | None |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] |  |  |  | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/24/2020 | Jan 1 1900 10:00AM
02/18/2020 |  | Routine, Scheduled | 179-10-0016-SWP | Stafford County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Orenco Advantex | None | Pump | Drip | Drip Tubing |  |  | ["Attached Growth Medium","Auxiliary Filter","Disinfection","Effluent Screens","Recirculation Pump"] | ["Attached Growth Medium","Auxiliary Filter","Disinfection","Effluent Screens","Recirculation Pump"] | [18 empty] | [Comments]: New Orenco UV lamp to be installed in the near future. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/02/2020 | 11:52 AM
10/23/2020 |  | RoutineScheduled | 182-00-0237 (LEGACY ALT. SYSTEM) | Rockingham | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Central Shenandoah | Onsite Wastewater Services - May Supply | 1942001627 | Drew | Shull | 1.000000 |  | none | none | Pump | Pressure | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/28/2021 | 05:41 AM
06/01/2020 |  | Reportable Incident | 175-14-0030 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green | [9 empty] | ["Blower/Compressor/Aerator Operation"] | ["Blower/Compressor/Aerator Operation"] | [18 empty] | Rebuild Clearstream compressor. | This AOSS should now return to normal function after having provided the above state routine maintenance |  | 06/01/2020 | 10:30 AM
08/07/2020 |  | RoutineScheduled | {FIPSCode}-STS-13475 | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Greenway Engineering | 1942001008 | Jeremy | Ferguson | 1.000000 | 1250 | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","Level Sensor Operation","Effluent Screens","SludgeScum Accumulation"] | ["Attached Growth Medium","Level Sensor Operation","Effluent Screens","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 08/13/2020 | 02:45 PM
08/27/2020 |  | RoutineScheduled | 109-04-1101 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | waugh | 3.000000 | 6000 |  |  | Pump | Gravity | Trenches | Not Applicable |  | ["Other"] | ["None"] | NA | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 08/30/2020 | 02:25 PM
09/03/2020 |  | RoutineScheduled | 139-06-0561 | Page | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Lord Fairfax | Onsite Wastewater Services - May Supply | 1942001022 | Sara | Tusing | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Inspection DKS | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/28/2021 | 05:41 AM
01/07/2020 |  | Reportable Incident | 234-16-135 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesapeake | R & K Septic, Inc. |  | John | Butt, Jr |  |  | Clearstream ATU | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] |  |  | 13.64 | 7.820000 | 4.000000 | [13 empty] | [Comments]: Replaced pump float and diffuser. UV isn't working. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/07/2020 | Jan 1 1900 4:00PM
03/13/2020 |  | Routine, Scheduled |  | Buchanan County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Cumberland Plateau | DEEL, DENNY M | 1942001097 | DENNY | DEEL |  |  | Norweco Singulair ATU | None | Gravity | None | Alternative Discharge | Chlorine | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens"] |  | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/20/2020 | Jan 1 1900 3:52PM
11/25/2020 |  | RoutineScheduled | 019-STS-24187 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Advantex AX20RT |  | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | NA | [16 empty] | Inspected | Newly Installed advantex AX20RT- Set pump run time to factory reccomended. Check float switches for correct operation. Checked recirclatuin and discharge pump for operation and alarm. All Functuional at this time. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 11/28/2020 | 09:30 AM
04/01/2020 |  | Routine, Scheduled | S-15-111-0010 | Botetourt County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Alleghany-Roanoke | Advanced Environmental & Septic, LLC | 1934000259 | Rodney | Rice | 1.000000 |  | Biomicrobics MicroFAST |  | Gravity | Distribution Box |  | None |  |  | ["Attached Growth Medium","BlowerCompressorAerator Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/01/2020 | Jan 1 1900 11:00AM
10/14/2020 |  | Routine/Scheduled | 08-160-0096 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Delta Environmental Products, DF Series |  | Pump | Drip | Drip Tubing | None | 103.000000 | ["None"] | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 10/14/2020 | 05:15 PM
03/02/2020 |  | Routine, Scheduled |  | Prince William County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Puraflo |  |  |  |  | None |  | ["Dispersal System Operation","Effluent Screens"] | ["Effluent Screens"] | [18 empty] | [Comments]: Recommend BOD sampling of Puraflo modules.Pump Amps 9.57 ETM 658h 55m Cycles 33890Septic Sludge 2" Scum 0Pump Sludge 0 Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/02/2020 | 09:52 AM
02/25/2020 |  | Routine, Scheduled | 179-10-0242-SWP | Stafford County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Ecoflo | None | Pump | Distribution Box | Aggregate Trench |  |  | ["Effluent Screens"] | ["Effluent Screens"] | [18 empty] | [Comments]: Upon arrival the Ecoflo tipping tray was dislocated and only dosing half of the peat. Tray was re-installed and a follow-up visit will be made to check tray and peat. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/06/2020 | 02:45 PM
08/05/2020 |  | RoutineScheduled | 39738 | Frederick | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage |  |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Control Operation"] | ["Auxiliary Filter" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | reattached float tree | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/26/2021 | 09:04 AM
11/20/2020 | Alternative | RoutineScheduled | 128-13-0037 | Essex | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | System breaker tripped. Restarted system in high water alarm condition. Pumped down to normal conditions.. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  |  | 12:00 AM
10/09/2020 |  | RoutineScheduled | 03-137-0002 | Goochland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | GeoEnvironmental Services, Inc. | 1942001010 | Peter | Mamunes | 1.000000 | 1500 | Orenco Advantex |  | Pump | Pressure | Trenches | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Recirculation Pump","Level Sensor Operation","SludgeScum Accumulation"] | ["SludgeScum Accumulation","Recirculation Pump","Effluent Screens","Level Sensor Operation","Distribution Pump Operation","Dispersal System Operation","Control Operation","Attached Growth Medium"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 10/12/2020 | Jan 1 1900 1:15PM
05/11/2020 |  | RoutineScheduled | {FIPSCode}-STS-13316 | Prince William | This AOSS is functioning as designed and in accord | Approved | EHD - Prince William | WasteMaster | 1942-001062 | Tim | Jenkins | 1.000000 |  |  |  | Gravity |  | Discharge | Chlorine |  | [] | [] |  | Musty | Clear | 6.900000 |  |  | 2.200000 |  | 05/11/2020 |  | 3.000000 |  |  | 6.700000 |  |  | Will be sent separately |  |  | This AOSS is functioning as designed and in accord |  |  | 12:00 AM
03/23/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Orenco Advantex |  |  |  |  | None |  | ["Effluent Screens"] | ["Effluent Screens"] |  | Good | Clear | [15 empty] | [Comments]: Pump Amps 9.1/9.6/11.2Septic Sludge 4" Scum 1"ATU Sludge 3" Scum 0.25Pump Sludge 1" Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/23/2020 | Jan 1 1900 9:00AM
02/26/2020 |  | Routine, Scheduled |  | Buckingham County | This AOSS should now return to normal function after having provided the above stated routine maintenance. | Paid | EHD - Piedmont | Taylor, Penny | 1942001028 | Penny | Taylor | 3.000000 | 6000 | Septic Tank Only | EZ Treat Sandfilter | Pump | Manifold | Gravel-Less Trench | None | 1400.000000 | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Recirculation Pump","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Recirculation Pump","SludgeScum Accumulation"] | [18 empty] | [Pumpout Comments]: pumped and cleaned all the tanks 230000. recommended to clean tanks annually. [Comments]: clean filters, reattach braces for filter bags, repairs to plumbing, clean filter housing install Sta-Rite effluent pump. | This AOSS should now return to normal function after having provided the above stated routine maintenance. |  | 02/27/2020 | Jan 1 1900 6:34PM
04/08/2020 |  | Routine, Scheduled |  | Mathews County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Three Rivers | Farmer’s Septic Service, Inc. |  | Ross | Cole | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | [Comments]: Serviced system. Checked the pump, panel, & floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/08/2020 | 12:00 PM
04/09/2020 |  | Routine, Scheduled | 18-120-0452A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesterfield | Madison Environmental LLC |  | Larry | Madison, Jr. |  |  | Clearstream ATU |  | Pump |  |  |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | [Comments]: Grab Bod sample Lab results not reported by Operator, EHS chose "No" in order to allow saving updated entry. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/09/2020 | Jan 1 1900 12:00PM
12/01/2020 |  | Routine/Scheduled |  | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Pump |  |  | None |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Recirculation Pump","Sludge/Scum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Recirculation Pump","Sludge/Scum Accumulation"] | N/A |  | 9.74 | 7.390000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 12/01/2020 | Jan 1 1900 9:45AM
01/30/2020 |  | Routine, Scheduled |  | Loudoun County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | None | None | Pump | Manifold | [24 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/02/2020 | 04:43 AM
09/04/2020 |  | Reportable Incident | SD-14-231 | Fauquier | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Distribution Pump Operation" ,"Control Operation" ,"BlowerCompressorAerator Operation"] | ["Control Operation" ,"Distribution Pump Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Tanks in high level due to pump not running. Measured 85 volts at pump breaker. Traced problem to corroded/broken wires in junction box on side of house. Installed temporary jumper in septic control panel so that pump would run. Owner to have electrician repair wiring and try to figure out source of water in junction box. Blower was very hot and shut off on thermal overload, may need replaced. Atu alarm bulb burnt out. Atu air filter very dirty and rusty (metal mesh), needs replaced. Infiltration observed at pump tank riser joint. | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
10/01/2020 |  | RoutineScheduled |  | Warren | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | Microfast tank pumped at time of inspection | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/26/2021 | 09:04 AM
08/18/2020 |  | Routine/Scheduled |  | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump | Distribution Box | Aggregate Bed | None |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  |  | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 08/18/2020 | Jan 1 1900 9:00AM
09/26/2020 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 | Pending Payment | EHD - Loudoun | WasteMaster, Inc. | 1942001062 | Tim | Jenkins |  |  | Multiflo FTB | none | Gravity | Gravity |  | Chlorination |  |  |  | NA | [5 empty] | 2.200000 | [9 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 |  | 06/21/2021 | 10:37 AM
01/22/2020 |  | Follow-Up | SR-02-2001 | Spotsylvania County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Biomicrobics MicroFAST | Biomicrobics MicroFAST | Pump |  |  |  |  | ["Auxiliary Filter","Control Operation","Dispersal System Operation","Distribution Pump Operation","SludgeScum Accumulation"] | ["Auxiliary Filter","Control Operation","Dispersal System Operation","Distribution Pump Operation"] | [18 empty] | [Comments]: Replaced flow meter (a critical component for operating a drip system). First 2 (short) test cycles revealed pump was dosing at 17 gpm with all 3 air release valves pressurizing and 31 psi showing on post filter gauge (other 2 gauges are broken). Inspection of zoner valve revealed stem/disc spring was jammed, which prevented disc from fully seating. Installed new stem/disc assembly and retested. This time, zoner rotated as designed but zone 1 (bottom) pressurized each cycle. Measured 7.2 gpm and 52 psi when fully dosing zone 3 and partially zone 1 (bad check valve). Verified power getting to non-functioning field flush solenoid. Replaced field flush solenoid and cleaned both solenoid valve bodies. Still getting a small trickle through return to septic line. Need to replace failed pressure gauge on return to septic line to verify adequate back-pressure. Drip timer was found set at 12:20 min on, 90 min standard rest and 20 min override rest. Increased override rest time to 60 min. More changes coming after all repairs are complete. Siemens processor appears to be failing as pump and etm counts are zero, and 6 adjustable drip settings are missing from parameters screen. Panel should probably be replaced considering its age. Septic tank pumping set up for the 25th. No lid to grade. Pumping through 6" pipes may not be adequate. Dirt showing at first pump tank riser joints. Suspect other points of infiltration such as at Microfast top that is covered by shrubs. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/28/2020 | 01:39 PM
03/19/2020 |  | Routine, Scheduled | 061-16-250 | Fauquier County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 5.000000 |  | Bio Barrier | Bio Barrier | Pump | Drip | Drip Tubing |  |  | ["Auxiliary Filter","Level Sensor Operation"] | ["Auxiliary Filter","Level Sensor Operation"] |  | YES | YES | [15 empty] | [Comments]: Biweekly inspection. Observed low pressure on return gauge when dosing zone 2. Criss-crossed over zone 2 with pump running. Some effluent surfacing near header ditch. Observed some wet stains in surge dosing tank at top seam. Need to recheck after rain to see if actively leaking. In the past 15 days, the system pumped an average of 1,948.2 gals/day at 335.9 gals/dose (avg.) for a total of 29,224 gals. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/01/2020 | 06:33 AM
04/09/2020 |  | Reportable Incident | 2015-143-0173 | Henrico County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Henrico |  |  |  |  | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | [Comments]: Owner called due to the light coming off and on when they have a lot of rain. Serviced system. Checked the pump, panel, & floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. Installed a check valve on the pump in the pump tank. The timer was set at 1.25 minutes every 2 hours - changed it to 1.25 minutes every 1 hour = 624 gallons per day. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/09/2020 | 12:00 PM
05/01/2020 | Alternative | Reportable Incident | 119-STS-105998 | Middlesex | This AOSS should now return to normal function after having provided the above state routine maintenance | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | None | None | Gravity | Distribution Box | Aggregate Trench | None | 450.000000 | ["Dispersal System Operation","Septic Tank Baffles"] | ["Dispersal System Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | [17 empty] | Septic tank pumped to facility replacement of building sewer and installation of new inlet baffle. Building sewer replaced from foundation to septic tank - new inlet "T" installed. | This AOSS should now return to normal function after having provided the above state routine maintenance |  | 05/14/2020 | 11:00 AM
03/31/2020 |  | Routine, Scheduled |  | Loudoun County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | None | None | Pump | Drip | Drip Tubing | [23 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/12/2020 | 02:21 PM
08/28/2020 |  | RoutineScheduled | 099-17-0056 SPSA | King George | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 |  | 04/09/2021 | 03:25 PM
03/25/2020 |  | Routine, Scheduled | 181-10-0056 | Rockbridge County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Central Shenandoah |  |  |  |  | 2.000000 | 4000 |  | Biomicrobics MicroFAST | None | None | Drip Tubing | None |  | ["None"] | ["None"] | [18 empty] | [Comments]: Filters checked and cleaned. No apparent leaks in system or drain field area. All control panels functioning properly. System did not need to be pumped. Lids properly secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/26/2020 | 30-12-1899 12:13 AM
11/05/2020 |  | RoutineScheduled | 07-184-5010 | Scott |  |  | EHD - Lenowisco |  |  | John | Hyder |  |  | Norweco 960 |  | Gravity |  |  | Chlorination | 450.000000 | [20 empty] | Dwelling vacant. No testing performed. |  |  |  | 12:00 AM
02/10/2020 |  | Routine, Scheduled |  | Warren County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Lord Fairfax | Cubbage, Harrison Lee, II | 1942001021 | Harrison | Cubbage | 1.000000 | 1500 | Septic Tank Only | Biomicrobics MicroFAST | Pump | Drip | Drip Tubing | None |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation"] |  | Musty | Clear | [15 empty] | [Comments]: Please keep area clean around septic system Pump Settings: Off 2hrs On 9min ETM-1734.17Hr Cycle Count-11097 Sludge/Scum Accumulations: Comp.1-14"/4" Comp.2-14"/0" Pump Tank-4"/0" | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/11/2020 | 02:04 PM
07/17/2020 |  | Routine, Scheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Clearstream ATU |  |  |  |  | None |  | ["Blower/Compressor/Aerator Operation","Effluent Screens"] | ["Blower/Compressor/Aerator Operation","Effluent Screens"] |  | Good | Clear | [15 empty] | Septic Sludge 5" Scum 1" ATU Sludge 0 Scum 0.25 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 07/17/2020 | Jan 1 1900 9:16AM
08/12/2020 |  | RoutineScheduled | 175-07-0412 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 1.000000 |  | Septic/ EZ-Treat Recirculation Tank |  | Gravity | Gravity | Trenches |  |  | ["Other"] | ["Other"] | NO | [9 empty] | 88.000000 | [7 empty] | Septic-3"sludge 0"scum/ Recirc-0"sludge (No pump out needed. Monster Box broken and was replaced. Counts: Pump-2 ETM-0h/ Peak-n/a/ High-5/ Dose-180/ on-3m 56s/ off-12h/ 45.7 gpm | This AOSS should now return to normal function after having provided the above state routine maintenance. |  |  | 12:00 AM
06/25/2020 |  | Follow-Up |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Drainfield area was mowed and cleared. Recommend keeping area mowed. System appears to be functioning as designed at this time. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/27/2021 | 01:26 PM
06/04/2020 |  | RoutineScheduled | 133 17 0208 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | S.E.P.T.I.C., Inc. |  | Denny | Deel |  |  | Clearstream |  | Gravity | Gravity | Mound | UV | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Effluent Screens"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
01/20/2020 |  | Routine, Scheduled | 191-STS-36019 | Washington County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Mount Rogers | DEEL, DENNY M | 1942001097 | DENNY | DEEL |  |  |  | None | Gravity | None | Alternative Discharge | Chlorine | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens"] |  | Musty | Clear | [15 empty] | [Comments]: 6 Blue Crystal Added | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/05/2020 | Jan 1 1900 4:58PM
05/11/2020 |  | Routine, Scheduled | 175-13-0503 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Clearstream |  |  |  |  | None |  | ["Blower/Compressor/Aerator Operation"] | ["Blower/Compressor/Aerator Operation"] |  | Good | Good | [15 empty] | Pump Amps 8.60 ETM 21866 Cycles 2765 Septic Sludge 10" Scum 10" ATU Sludge 16" Scum 0 Pump Sludge 2" Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 05/11/2020 | 04:20 PM
06/22/2020 |  | Routine/Scheduled | 03-172-0262AR | Powhatan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesterfield | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1500 | Orenco Advantex |  | Gravity | Distribution Box | Aggregate Trench | None | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | None | clear | [15 empty] | Routine Service conducted Processing tank in normal operating level - Recirculating Splitter Valve serviced - effluent screen serviced - recirculating pump serviced. Advantex module - media drapes and spray distribution grid serviced. Module lid has warped and support struts have failed (does not affect the treatment or operation). Distribution box intact and at normal operating level. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 06/23/2020 | Jan 1 1900 8:30AM
02/20/2020 |  | Routine, Scheduled |  | Loudoun County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | Orenco Advantex | None | Pump | Distribution Box | Gravel-Less Trench | [23 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/02/2020 | 04:43 AM
03/30/2020 |  | Routine, Scheduled | 185-STS-17514 | Tazewell County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Cumberland Plateau | DEEL, DENNY M | 1942001097 | DENNY | DEEL |  |  | Norweco Singulair ATU | None | Gravity | None | Alternative Discharge | Chlorine | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens"] |  | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/30/2020 | Jan 1 1900 5:14PM
12/04/2020 |  | RoutineScheduled | 101-19-0116 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Old Dominion Engineering | 1942001085 | Michael | Craun | 1.000000 | 1000 | Aqua Safe AS500 |  | Pump | Gravity | Pad | Not Applicable | 450.000000 | ["None"] | ["None"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12/15/2020 | 03:12 PM
11/20/2020 |  | RoutineScheduled | 187041015 | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax |  | 1942001008 | Jeremy | Ferguson | 1.000000 | 1060 | Puraflo | N/A | Pump | Gravity | Trenches | Not Applicable | 100.000000 | ["None"] | ["Effluent Screens","Control Operation"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 04:00 AM
03/31/2020 |  | Routine, Scheduled |  | Fluvanna County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Blue Ridge | CLARK, MICHAEL J | 1934000023 | MICHAEL | CLARK |  |  | Septic Tank Only | Septic Tank Only | None | None | None | None |  |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/01/2020 | 03:57 AM
06/20/2020 |  | RoutineScheduled | 171-18-0020 | Pittsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Pittsylvania-Danville | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1000 | Advantex |  | Pump | Gravity | Trenches |  |  | ["None"] | ["None"] | [18 empty] | 2" of solids in septic tank. Flushed treatment unit spray manifold. Cleaned septic tank filter. Tested floats, Pumps and alarm. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 09/25/2020 | 07:03 PM
05/11/2020 |  | RoutineScheduled |  | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Fairfax | FIVE STAR SEPTIC INC | 1944001248 | AARON | GOINS | [9 empty] | [] | [] | [18 empty] | NEEDS PUMP OUT AND THERE IS A SEVERE ROOT INFESTATION AND D-BOXES NEED TO BE DUG UP TO BE CHECKED | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. |  | 05/11/2020 | 12:00 AM
03/30/2020 |  | Routine, Scheduled | 185-STS-17515 | Tazewell County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Cumberland Plateau | DEEL, DENNY M | 1942001097 | DENNY | DEEL |  |  | Advanced Septic | None | Gravity | Distribution Box | Aggregate Bed | Chlorine | 200.000000 | ["Auxiliary Filter","Control Operation","Disinfection","Distribution Pump Operation","SludgeScum Accumulation"] | ["Auxiliary Filter","Control Operation","Disinfection","Distribution Pump Operation"] |  | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/30/2020 | Jan 1 1900 5:09PM
04/03/2020 |  | Routine, Scheduled | 04-160-0061 | Montgomery County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1934000259 | Rodney | Rice | 1.000000 |  | Orenco Advantex |  | Gravity | Distribution Box |  | None |  |  | ["Control Operation","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/03/2020 | 03:00 PM
06/22/2020 |  | Routine, Scheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Biomicrobics MicroFAST |  | Pump | Drip | Drip Tubing | None |  | ["Blower/Compressor/Aerator Operation"] | ["Blower/Compressor/Aerator Operation"] |  | Good | Clear | [15 empty] | Spin filter cleaned. Pump Amps 8.08 ETM 153 hrs Cycles 1305 Water Meter Reading 94800 Septic Sludge 4" Scum 2" ATU Sludge 4" Scum 0 Pump Sludge 0 Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 06/22/2020 | Jan 1 1900 3:55PM
05/22/2020 | Alternative | Routine/Scheduled | 171-06-0227 | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | POWELLS PLUMBING, INC. | 1942001036 | Kurt | Holthaus | 1.000000 | 1000 | Puraflo |  | Pump | Drip | Drip Tubing |  | 300.000000 | ["Effluent Screens"] | ["Effluent Screens"] | N/A | [17 empty] | Annual Inspection - Serviced spin filter and effluent screen(s). | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 05/22/2020 | 01:33 PM
08/21/2020 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Eco Virginia | 1942001235 | William | Poindexter | 1.000000 |  | Ecoflo | none | Gravity | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 |  | 06/03/2021 | 05:53 AM
01/02/2020 |  | Routine, Scheduled |  | Louisa County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Blue Ridge | CLARK, MICHAEL J | 1934000023 | MICHAEL | CLARK |  |  | Septic Tank Only | Septic Tank Only | None | None | None | None |  |  | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/14/2020 | 03:56 AM
07/23/2020 |  | RoutineScheduled | SD-01-590 | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Wastemaster Inc |  | Timothy | Jenkins | 2.000000 |  | ATU | Polishing SandFilter | Pump | Gravity | Discharge | Chlorination |  | [] | [] |  | Musty | Clear | 7.100000 |  |  | 2.200000 | [12 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 07/23/2020 | 03:15 PM
02/17/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Paid | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Biomicrobics MicroFAST |  | Pump | Drip | Drip Tubing | UV Light |  | ["BlowerCompressorAerator Operation"] |  |  | Good | Good | [5 empty] | 02/17/2020 |  | 122.000000 | [7 empty] | [Comments]: Spin filter cleaned.Pump Amps 10.10 ETM 21248 Cycles 1484Water Meter Reading 466300Pump Sludge 6" Scum 7"ATU Sludge 12" Scum 0Pump Sludge 2" Scum 0Compressor needs replacing. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 02/17/2020 | Jan 1 1900 11:10AM
03/24/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Fairfax | BLEVINS, JOEL R, SR | 1934000415 | JOEL | BLEVINS |  |  | Microfast | Septic Tank Only | None | None | None | None |  | ["None"] | ["None"] | [8 empty] | 03/24/2020 | pump tank | 31.000000 | [5 empty] | Attached to this report |  | [Comments]: Cleaned the air filter and took water sample. The compressor is strong, no sludge or build up. Tank was pumped in December 2019. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/07/2020 | Jan 1 1900 12:13PM
02/12/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Puraflo |  | Pump |  |  | None |  | ["Effluent Screens"] | ["Effluent Screens"] | [18 empty] | [Comments]: Concrete casing lid needs replacement.Pump 1 Amps 13.07 ETM 306767 Cycles 11409Pump 2 Amps 13.06 ETM 00 Cycles 11388Septic Sludge 8" Scum 2"Pump Sludge 2" Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/12/2020 | Jan 1 1900 11:15AM
10/08/2020 | Alternative | Routine/Scheduled | 159-02-182 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1500 | Orenco Advantex |  | Pump | Manifold | Aggregate Bed | None | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | None | Clear | [15 empty] | Routine Service Processing Tank - drawing to low level due to effluent screen clog - RSV, recirc pump & effluent screen serviced. Treatment Module - media drapes & spray grid serviced. Discharge Tank - normal operating level - pump, float sensors and controls operating proerply. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 10/13/2020 | 08:30 AM
04/02/2020 |  | Routine/Scheduled |  | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump | Drip | Elevated Sand Mound | UV Light |  | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  |  | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/02/2020 | Jan 1 1900 3:00PM
03/20/2020 |  | Routine, Scheduled | SD-04-7 | Culpeper County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | CLARK, MICHAEL J | 1934000023 | MICHAEL | CLARK |  |  | Septic Tank Only | Septic Tank Only | None | None | None | None |  |  | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/01/2020 | 04:07 AM
12/22/2020 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump | Distribution Box | Aggregate Bed | None |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  | 4.69 | 7.590000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 12/22/2020 | Jan 1 1900 12:15PM
12/07/2020 | Alternative | Reportable Incident | 073-STS-105714 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | None | None | Gravity | Distribution Box | Aggregate Trench | None | 450.000000 |  | ["Dispersal System Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | [17 empty] | Installed new outlet baffle in septic tank. Installed new 4" PVC conveyance Line Replaced existing distributin box with new concrete 6 port Installed new 4" PVC header lines to existing laterals. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 12/09/2020 | 10:00 AM
01/31/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Fairfax | Hott, Joshua D. | 1942001301 | Joshua | Hott | 1.000000 | 1875 | Septic Tank Only | Microfast | Pump | Distribution Box | Aggregate Trench | None |  | ["None"] | ["None"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/06/2020 | Jan 1 1900 12:53PM
04/29/2020 |  | Initial Visit | S175-11-0045 | Southampton | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | Serviced system. Checked the pump, panel, & floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream. Installed a new aerator motor (19070170) and a new pressure switch for the aerator. Replaced the alarm float in the Clearstream. Owner wants a new Clearstream top (old style). | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 04/29/2020 | Jan 1 1900 12:00PM
05/08/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/27/2021 | 01:26 PM
02/05/2020 |  | Routine, Scheduled | 02-100-1108 | Accomack County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Eastern Shore | DUER, PETE C | 1942001051 | PETE | DUER | 1.000000 | 1500 | Septic Tank Only | Orenco Advantex | Pump | None | None | None |  | ["None"] | ["None"] | [18 empty] | [Comments]: Aoss Inspection. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/07/2020 | 11:37 AM
03/06/2020 |  | Routine, Scheduled | 2016-143-0040 | Henrico County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Henrico |  |  |  |  | 1.000000 | 1250 |  | None | Pump | Drip | Drip Tubing | None | 450.000000 | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | [Comments]: Sludge = 6" Scum = 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/25/2020 | 09:14 AM
09/18/2020 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Fairfax | McKim Construction | 1942001330 | Michelle | McKim | 2.000000 |  |  |  | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium"] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles"] | YES | [17 empty] | Sample failed peat fiber needs to be replaced | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. |  |  | 12:00 AM
07/17/2020 |  | Routine/Scheduled | 09-120-0393A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesterfield | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1500 | Orenco Advantex |  | Pump | Distribution Box | Aggregate Trench | None | 600.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | None | Clear | [15 empty] | Processing tank pumped for real estate inspection. Inspection & service conducted for real estate transaction. Processing tank - pumped empty for inspection - RSV, effluent screen and recirc. pump serviced. - processing tank refilled with fresh water. AdvanTex Module - media drapes and spray grid serviced - media flushed. Discharge tank - discharge pump serviced - float sensors and controls functioning as normal. Distribution box excavated - intact - all 8 laterals accepting effluent. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 07/20/2020 | Jan 1 1900 11:30AM
03/18/2020 |  | Routine, Scheduled | SP-05-269 | Stafford County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001350 | Mike | Cook | 1.000000 |  | Puraflo | None | Pump | Distribution Box | Aggregate Trench |  |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/01/2020 | 06:33 AM
06/24/2020 |  | RoutineScheduled |  | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 2705051738 | Joshua | Hott |  |  |  |  | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
07/25/2020 |  | RoutineScheduled | 145-18-0008 | Highland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Hunter E. Ayres, General Contractor | 1942001166 | Hunter | Ayres | 1.000000 | 1000 | Orenco Advantex |  | Pump | Pressure | Trenches | Not Applicable |  | ["Septic Tank Baffles","Effluent Screens","Auxiliary Filter"] | ["Septic Tank Baffles","Auxiliary Filter","Effluent Screens"] | YES | [17 empty] | All filters checked and cleaned. No apparent leaks in system or drain field area. Control panel functioning properly. Textile sheets were sprayed off and found to be in good condition. System did not need to be pumped. Lids were properly secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 08/04/2020 | 08:35 PM
01/15/2020 |  | Routine, Scheduled | 15-142-0091 | Hanover County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chickahominy | Old Dominion Onsite, Inc. | 1942001508 | Danna | Revis | [9 empty] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation"] | [18 empty] | [Comments]: Cleaned vent, checked float operation. Lots of growth on top of socks. Recommend pump &refill and stock replacement. Checked float and pump function. System appears to be working properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/15/2020 | Jan 1 1900 3:30PM
09/23/2020 |  | RoutineScheduled |  | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 2705051738 | Joshua | Hott | 1.000000 | 1500 | Septic | Puraflo | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
09/30/2020 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump | Distribution Box | Aggregate Bed | None |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  |  | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 10/08/2020 | Jan 1 1900 2:30PM
06/26/2020 |  | RoutineScheduled | 179-15-0008-SR | Stafford | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Distribution Pump Operation" ,"Control Operation" ,"Recirculation Pump"] | ["Distribution Pump Operation" ,"Control Operation" ,"Recirculation Pump"] | NA | [15 empty] | Will be sent separately | Inspected | Sand filter tank in high level again, this time due to failed pump. Replaced pump and check valve. Also replaced broken j-box on side of sand filter pump tank riser. Observed 2 dead geckos flush out of sand filter turn-up during test cycle. Had to level the manifolds to get equal flow from each end. Could not locate zone 1 ARV. Valve box for zone 2 (near large holly tree) was full of dirt and hindering operation of pop-up ARV). Cleaned zone return valve after valve stuck open when checking forward flush rate. Owner said remote alarm box is not helpful and is turned off. Some roots visible at lower seam in drip pump tank. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
07/09/2020 |  | RoutineScheduled |  | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/Ecopod | Pump Tank | Pump | Pressure | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [17 empty] | Septic-6"sludge 0"scum/Ecopod-10"sludge (May require pump out next year)/Pump Tank-0"sludge/Blower air filter cleaned. Syster has a Aquaworks Panel. Drainfield is good. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
05/14/2020 |  | RoutineScheduled | SWP-05-132 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Attached Growth Medium"] | ["Effluent Screens" ,"Attached Growth Medium"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 |  | 04/09/2021 | 03:25 PM
11/18/2020 |  | RoutineScheduled | 069-16-0405 | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 2705110225 | Larry | Royston | [9 empty] | ["None"] | ["None"] | YES | [16 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12/05/2020 | 12:00 AM
10/07/2020 |  | RoutineScheduled | 17-152-009 | Lee | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | CLEARSTREAM |  | Gravity | Gravity | Mound | Not Applicable | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","Septic Tank Baffles"] | ["BlowerCompressorAerator Operation","Control Operation"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
07/16/2020 |  | Follow-Up | SWP-05-157 | Stafford | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Repaired settled pipe between septic tank and pump tank. Resealed pump tank wedge lid and installed tee on inlet of pump tank. Resealed pump tank riser joint. Resealed outlet riser joint on septic tank. Resealed risers on septic tank inlet and adaptor. Resealed out pump pipe. Repaired improper septic inlet tee. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
06/01/2020 |  | Routine, Scheduled | SD-02-323 | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Orenco Advantex | [6 empty] | ["Effluent Screens"] | ["Effluent Screens"] |  | Good | Clear | [15 empty] | Pump Amps 9.84 ETM 17272 Cycles 23032 discharge Pump Amps 12.20 ETM 442150 Cycles 895975 Septic Sludge 0 Scum 0.50 ATU Sludge 12" Scum 0 Pump Sludge 0 Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 06/01/2020 | 03:58 PM
12/18/2020 |  | RoutineScheduled | 179-09-0145-SWP | Stafford | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | ["Level Sensor Operation" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Disinfection" ,"Dispersal System Operation"] | NA | [15 empty] | Will be sent separately | Inspected | All tanks were in high level when I arrived for the yearly inspection. The circuit board in the panel had failed. I replaced the board. The blower failed as well. Came back on Monday Dec. 21 to replace. Both compartments of the septic tank need to be pumped out. Home owner called pumper and they were pumped on Tuesday Dec 22. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
05/20/2020 |  | Routine/Scheduled |  | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump | Distribution Box |  | None |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  |  | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 05/20/2020 | Jan 1 1900 10:30AM
05/18/2020 |  | RoutineScheduled | 10-113-188 | Buchanan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | Septic Inc |  | Denny | Deel |  |  |  |  | Gravity | None | Alternative Discharge | Chlorine | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens"] | true | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
04/20/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Payment | EHD - Loudoun | Great Falls Septic Service, Inc | 1942001301 | Josh | Hott |  |  | Delta Environmental Products, UC Series | none | Gravity | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/27/2021 | 11:51 AM
06/08/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | SES MidAtlantic LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/15/2021 | 09:00 AM
07/20/2020 |  | Reportable Incident | 234-18-084 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | Owner called due to the alarm going off and light being on. Serviced system. Checked the pump, panel, & floats (ok). Cleaned the filter in the Clearstream, cleaned the disc filter, and cleaned the UV light bulb. Changed the diffuser in the Clearstream and changed the filter in the aerator. The septic tank needs additional risers on it so it can be properly inspected in the future. The timer is set to 9 minutes every 2 hours. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 07/20/2020 | Jan 1 1900 12:00PM
09/24/2020 |  | Routine, Scheduled | 175-02-0463 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Puraflo |  |  |  |  | None |  | ["Effluent Screens"] | ["Effluent Screens"] | [18 empty] | Pump Amps 15.37 ETM 316.59 hrs Cycles 14851 Septic Sludge 6" Scum 0.25 Pump Sludge 2" Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 09/24/2020 | 10:30 AM
08/26/2020 |  | Follow-Up | 061-18-270 | Fauquier | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Resealed septic tank inlet riser. Removed Fast unit lid, cleaned media, reinstalled and sealed. System pumped out by others. Added flow meter to headworks. Checked drip and flush rates. Sealed holes that secure pump pipe strap. Sealed pump tank riser. Meter 128 gallons. HLA 42. ETM 3896. Count 21939. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
11/17/2020 |  | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 2705110222 | Larry | Royston | [9 empty] | ["None"] | ["None"] | YES | [16 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12/05/2020 | 12:00 AM
10/14/2020 |  | RoutineScheduled |  | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 1.000000 |  | Septic/ Microfast |  | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [17 empty] | Septic-6"sludge 6"scum/ Microfast-8"sludge (Recommend pump out due to large grease scum layer) Blower air filter cleaned. No breakout or spongy areas on the drainfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
04/11/2020 |  | RoutineScheduled | SD-97-240 | Culpeper | This AOSS is functioning as designed and in accord | Approved | EHD - Rappahannock-Rapidan | Wastemaster |  | Douglas | Crooks | 2.000000 |  |  |  | Pump |  | discharge | Chlorine |  | [] | [] |  | Low | Clear | 7.800000 |  |  | 2.200000 |  | 04/11/2020 |  | 3.000000 |  |  | 3.400000 |  |  | Attached to this report |  | Functioning as Designed | This AOSS is functioning as designed and in accord |  |  | 12:00 AM
12/08/2020 |  | Reportable Incident | 228-13-0174 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | Owner called due to the alarm going off. Serviced system. Checked the pump, panel, & floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream, changed the filter in the aerator. Replaced the pressure switch on the aerator and replaced the UV light bulb. The pump float is a mercury float - should be a mechanical float - it is working at this time. The septic tank needs additional risers on it so it can be properly inspected in the future. The timer is set to 2 minutes every 2 hours. Replaced 4" plug on the inspection port. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12/08/2020 | Jan 1 1900 12:00PM
11/14/2020 |  | Reportable Incident | 175-16-0403 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Prince William | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation"] | ["Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | High level alarm. Siemens processor was locked up. Cycling control breaker on and off freed it up. Will contact American Mfg to see if processor can be updated. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
07/21/2020 |  | RoutineScheduled | 99028531 | Warren | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Lord Fairfax | Onsite Wastewater Services - May Supply | 1942001022 | Sara | Tusing | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | inspection by Ds | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/28/2021 | 05:41 AM
12/02/2020 |  | RoutineScheduled | 099-07-0210-ST | King George | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Control Operation" ,"Attached Growth Medium"] | ["Distribution Pump Operation" ,"Level Sensor Operation" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Control Operation" ,"Dispersal System Operation" ,"Attached Growth Medium"] | NA | [15 empty] | Will be sent separately | Inspected | Roots growing in rope hole of pod 5 cut and dug out on both sides monitor next year. Recommended customer to cut down tree close to pods that the roots were coming from. Pod 1 looked a little wetter than the rest of the pods augered and looked a lot better. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
06/01/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 2.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Trash tank outlet lid has a hole in it large enough to allow groundwater and potentially be a safety hazard. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/27/2021 | 01:26 PM
03/31/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Biomicrobics MicroFAST |  |  |  |  | UV Light |  | ["BlowerCompressorAerator Operation","Disinfection"] | ["BlowerCompressorAerator Operation","Disinfection"] |  | Good | Clear | [15 empty] | [Comments]: Spin filter cleaned.Pump Amps 8.60 ETM 130h Cycles 1042Water Meter Reading 60300Septic Sludge 8" Scum 4"ATU Sludge 10" Scum 0Pump Sludge 0 Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/31/2020 | Jan 1 1900 4:10PM
04/22/2020 |  | Routine/Scheduled | S 800-17-0025 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | Serviced system. Checked the pump, panel, & floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. The timer is set to 2.25 minutes every 2.25 hours. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 04/22/2020 | Jan 1 1900 12:00PM
10/08/2020 |  | RoutineScheduled | SD-12-285 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Soils, Inc. | 1942001004 | Markham | Smith | 2.000000 | 1500 | Puroflo |  | Pump | Gravity | Pad | Not Applicable | 62.500000 | [] | ["Attached Growth Medium","Control Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | 1" inch sludge in septic tank | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 10/09/2020 | 12:00 AM
12/15/2020 |  | Routine/Scheduled | SD-04-203 | Fauquier | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Rappahannock-Rapidan | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Puraflo |  | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","Effluent Screens"] | ["Effluent Screens"] | YES | [17 empty] | Sample box holding effluent. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 12/15/2020 | 05:30 PM
03/12/2020 |  | Routine, Scheduled |  | Loudoun County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | None | Pump | Distribution Box | Aggregate Trench | [23 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/12/2020 | 02:21 PM
10/23/2020 | Alternative | Reportable Incident | 128-10-005 | Essex | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | Replaced failed blower. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  |  | 12:00 AM
06/22/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/14/2021 | 04:27 PM
03/20/2020 |  | Routine, Scheduled | 177-08-0137-SWP | Spotsylvania County | This AOSS should now return to normal function after having provided the above stated routine maintenance. | Approved | EHD - Rappahannock | JOHNSTON, JOSHUA C | 1934000089 | JOSHUA | JOHNSTON | 1.000000 | 1250 | Puraflo | None | Pump | Distribution Box | Aggregate Trench | None | 400.000000 |  | ["Control Operation","Effluent Screens","Level Sensor Operation"] |  | none | weak tea | [16 empty] | This AOSS should now return to normal function after having provided the above stated routine maintenance. |  | 03/24/2020 | 08:29 PM
12/07/2020 |  | Initial Visit | 107-18-0077 | Rockbridge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Central Shenandoah | Onsite Wastewater Services - May Supply | 1942001627 | Drew | Shull | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | START UP COMPLETED ON 12-07-2020 BY DKS. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 06/09/2022 | 04:10 PM
09/02/2020 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintanence requirements | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Gravity | Gravity |  | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | A septic system inspection on a conventional gravity. The state requires that all conventional septic tanks must be pumped out EVERY 5 years and filed with the state and county. The sewer line is cast iron. The septic tank has a riser on the inlet side of the tank. Tank was pumped out and inspected for any cracks or leaks and none were seen. The 8 port concrete d-box was dug up it was 12" under the ground. Was unable to camera snake header lines all lines were full of water and all lines were blocked and or crushed. at time of inspection septic system was not working | This AOSS is not functioning as designed or in accordance with the performance/maintanence requirements |  | 04/14/2021 | 04:27 PM
05/11/2020 |  | Routine/Scheduled | 196-14-0140 | Westmoreland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1250 | Microfast | None | Pump | Distribution Box | Aggregate Trench | None |  |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | Trash Tank Riser was found to be leaking ground water, and has root infiltration; in the Discharge Tank, the Floats and Plumbing have exceeded their expected life, the Junction Box had water infiltration, and the Risers on both sides of the Tank were leaking ground water and had root infiltration | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 05/26/2020 | 02:53 PM
10/08/2020 |  | RoutineScheduled | SD-11-261 / SD-12-270 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Soils, Inc. | 1942001004 | Markham | Smith | 2.000000 | 1500 | Puroflo |  | Pump | Gravity | Pad |  | 62.300000 | [] | ["Attached Growth Medium","Septic Tank Baffles","SludgeScum Accumulation","Control Operation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 10/09/2020 | 12:00 AM
07/25/2020 |  | RoutineScheduled | SD-99-232 | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Wastemaster Inc |  | Timothy | Jenkins | 2.000000 |  | ATU | Polishing SandFilter | Pump | Gravity | Discharge | Chlorination |  | [] | [] |  | Musty | Clear | 6.700000 |  | 30.000000 | 2.200000 | [12 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 07/31/2020 | 02:15 PM
01/16/2020 |  | Routine, Scheduled |  | Lancaster County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Three Rivers | BEASLEY, THOMAS W | 1934000450 | THOMAS | BEASLEY | 2.000000 | 2500 | Microfast | Septic Tank Only | Pump | Distribution Box | Aggregate Trench | None |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [5 empty] | 45.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/16/2020 | 03:30 PM
02/17/2020 |  | Routine, Scheduled | 171-06-0288 | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Lord Fairfax | SEAL, CHARLES K | 1934000144 | CHARLES | SEAL | 1.000000 |  |  | Septic Tank Only | None | None | None | None |  | ["Attached Growth Medium","Septic Tank Baffles"] | ["Attached Growth Medium","Septic Tank Baffles"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/11/2020 | 09:48 PM
09/11/2020 |  | Routine/Scheduled |  | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump | Drip | Elevated Sand Mound | UV Light |  | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  |  | 7.000000 | 3.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 09/11/2020 | Jan 1 1900 12:30PM
05/04/2020 | Alternative | RoutineScheduled | 115-05-0407 | Campbell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Virginia Septic Service LLC | 1942001512 | iain | Waugh | 1.000000 | 1500 | Septic Tank | Advantex AX20RT | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation"] | ["Control Operation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 08/30/2020 | 12:00 AM
05/20/2020 |  | Routine/Scheduled | 18-174-0031 | Prince George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Crater | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | Ecoflo | None | Pump | Distribution Box | Aggregate Trench | None |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | In the Pump Basin, the electrical Splice Box was not properly attached; the Distribution Box was found with a fracture and there were no Line Balancers present | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 06/04/2020 | Jan 1 1900 4:36PM
12/08/2020 |  | Follow-Up | 03-197-A2 | Wise | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | Wise County Health Dept |  | Rodney | Neece |  |  | ATU |  | Gravity | Gravity | Discharge | Chlorination | [10 empty] | No tablets | [11 empty] | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12/09/2020 | 12:00 AM
09/29/2020 |  | RoutineScheduled | 099-13-0097-SWP | King George | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  | ["Distribution Pump Operation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Control Operation" ,"Attached Growth Medium" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | ["Control Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Attached Growth Medium" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | YES | [15 empty] | Will be sent separately | Inspected | Riser and inlet wedge lid leaking on septic tank & pump tank. Floats set wrong, corrected. Replaced alarm buzzer. Pump has slowed, flow rates is at minimum. Proposal to be sent to homeowner for repairs. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
12/02/2020 | Alternative |  | 151-11-0091 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | KC Forge Environmental Service, LLC | 1942001034 | Kent | Cuthbertson | 1.000000 | 50,000 GPD |  |  | Pump | Gravity | Trenches | UV | 25200.000000 | [] | [] | [16 empty] | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 11/22/2020 | 03:00 PM
06/18/2020 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU | [6 empty] | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  |  | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 06/18/2020 | Jan 1 1900 9:00AM
03/17/2020 |  | Routine, Scheduled | 06-125-086 | Dickenson County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Cumberland Plateau | DEEL, DENNY M | 1942001097 | DENNY | DEEL |  |  | Norweco Singulair ATU | None | Gravity | None | Alternative Discharge | Chlorine |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens"] |  | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/20/2020 | Jan 1 1900 1:25PM
04/13/2020 |  | RoutineScheduled | 069-17-0417 | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Greenway Engineering | 1942001008 | Jeremy | Ferguson | 1.000000 | 1250 | Microfast | none | Pump | Pressure | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Level Sensor Operation","SludgeScum Accumulation"] | NA | [17 empty] | Random wet spots when pump is ran. Have had multiple visits and have dug up to find leaks with no leaks found. System holds pressure when ran. Going to check on wet spots over the next inspections. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 07/21/2020 | 10:20 AM
06/03/2020 |  |  | SD-13-184 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan |  |  | joel | pinnix | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
12/09/2020 |  | RoutineScheduled | SWP-03-282 | King George | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Ecoflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Attached Growth Medium"] | ["Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Attached Growth Medium"] | YES | [15 empty] | Will be sent separately | Inspected | When i arrived the septic tank was in high level due to clogged septic filter. Cleaned filter and removed the clog. Peat had some ponding. I augered peat looked good after. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
01/20/2020 |  | Routine, Scheduled | 136 04 768 | Gloucester County | This AOSS should now return to normal function after having provided the above stated routine maintenance. | Approved | EHD - Three Rivers | LANGFORD, CHARLES T | 1934000143 | CHARLES | LANGFORD | 1.000000 | 1000 | Clearstream | Septic Tank Only | Pump | Distribution Box | Aggregate Trench | None |  | ["BlowerCompressorAerator Operation","Effluent Screens"] | ["BlowerCompressorAerator Operation","Effluent Screens"] | [19 empty] | This AOSS should now return to normal function after having provided the above stated routine maintenance. |  | 01/27/2020 | 09:07 AM
01/16/2020 |  | Routine, Scheduled |  | Lancaster County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Three Rivers | BEASLEY, THOMAS W | 1934000450 | THOMAS | BEASLEY | 3.000000 | 3000 | EcoPod | Septic Tank Only | Pump | Distribution Box | Aggregate Trench | None |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [5 empty] | 52.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/16/2020 | 03:30 PM
03/20/2020 |  | Routine, Scheduled | 033-18-0177-SP | Caroline County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Ware, Michele P | 1942001165 | Michele | Ware |  |  | Septic Tank Only | Septic Tank Only | None | None | None | None |  |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | [16 empty] | Attached to this report |  | VENIS File Names: R0345618 (1).pdf | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/31/2020 | 05:21 PM
09/17/2020 |  | RoutineScheduled |  | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","SludgeScum Accumulation"] | ["Attached Growth Medium","SludgeScum Accumulation"] | NA | [17 empty] | Septic-8"sludge 4"scum/ Microfast-14"sludge (Septic/Microfast Tank requires pump out) Pump Tank-2"sludge/Zoeller N-140 pumps/ Pump1-11.1Amps @ 36 gpm run time now 3m/ Pump2-11.1 Amps @ 45gpm run time now-2m30s Counts: P1-844 ETM-31h 30m/ P2-829 ETM-30h 59m/ Peak-5/ High-8/ No breakout or spongy areas on the drainfield | This AOSS should now return to normal function after having provided the above state routine maintenance. |  |  | 12:00 AM
12/22/2020 |  | RoutineScheduled | 099-09-0037-SP | King George | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 |  | 04/09/2021 | 03:25 PM
07/27/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Ecoflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/27/2021 | 01:26 PM
07/23/2020 |  | Routine, Scheduled | 175-06-0804 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Orenco Advantex |  |  |  |  | None |  | ["Effluent Screens"] | ["Effluent Screens"] |  | Good | Clear | [15 empty] | Pump Amps 10.56/7.23 Septic Sludge 12" Scum 0.25 ATU Sludge 8' Scum 0 Pump Sludge 3" Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 07/23/2020 | 03:03 PM
12/05/2020 |  | RoutineScheduled | 2049-97-153 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Wastemaster Inc |  | Timothy | Jenkins | 2.000000 |  | Recirculating Sand Filter |  | Pump | Gravity | Discharge | Chlorination |  | [] | [] |  | Musty | Clear | 6.900000 |  |  | 1.800000 | [12 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12/10/2020 | 01:20 PM
03/11/2020 |  | Routine, Scheduled | 033-18-0154-SP | Caroline County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Ware, Michele P | 1942001165 | Michele | Ware |  |  | Septic Tank Only | Septic Tank Only | None | None | None | None |  |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/12/2020 | 12:15 PM
11/24/2020 |  | Routine/Scheduled | 06-120-0837A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 | 1500 | Ecoflo |  | Gravity |  |  |  |  | ["Control Operation","Distribution Pump Operation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 11/24/2020 | Jan 1 1900 10:00PM
06/09/2020 |  | Routine/Scheduled | 04-118-0083 | Charles City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chickahominy | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1250 | Clearstream ATU | None | Pump | Distribution Box | Aggregate Trench | None |  |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | The Septic Tank was found buried lower than the Aeration Tank, which causes the Septic Tank to improperly enter into High/Flood Levels, and the Riser has evidence of leaking; the High Level Alarm Float in the Aeration Tank is not functioning, the Air Line is not serviceable, and the Mute Button was found stuck; the Discharge Riser was not properly sealed, and the Floats are not properly secured; the Surge Box was found cracked, and the seal was broken around the Forcemain Line | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 06/16/2020 | Jan 1 1900 11:31AM
01/15/2020 |  | Routine, Scheduled |  | Richmond City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Richmond | BEASLEY, THOMAS W | 1934000450 | THOMAS | BEASLEY | 1.000000 | 2000 | Clearstream ATU | Septic Tank Only | Pump | Drip | Drip Tubing | None |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [5 empty] | 30.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/15/2020 | Jan 1 1900 4:00PM
05/12/2020 |  | RoutineScheduled | 196-06-361 | Westmoreland | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Three Rivers | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Distribution Pump Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Distribution Pump Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Upon arrival the blower was turned off. Manufacturer recommendations allow for turning the blowr off in the winter on a summer use property. They recommend maintaining normal operation on a weekend property. The pump tank is leaking at the base of the riser. We recommend excavating by hand and resealing. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. |  | 04/09/2021 | 03:25 PM
07/22/2020 |  | RoutineScheduled | SD-96-491 | Fauquier | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Rappahannock-Rapidan | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic Tank | Pump Tank | Pump | Pressure | Drip | Not Applicable |  | ["Dispersal System Operation"] | ["Dispersal System Operation"] | NA | [17 empty] | Pump Tank-2"sludge/ System does not need a pump out/Drip filters were clogged. Cleaned filters and rates now are Zone 1-4.5/ Zone2-4.8/ Recommend clearing the drip field. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  |  | 12:00 AM
09/18/2020 |  | Routine, Scheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green | [9 empty] | ["None"] | ["None"] |  | Acceptable | Tan | [15 empty] | Septic Sludge 13" Scum 0.25 ATU Sludge 0 Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 09/18/2020 | Jan 1 1900 9:39AM
05/01/2020 |  | RoutineScheduled |  | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | [9 empty] | ["Attached Growth Medium"] | ["Attached Growth Medium"] | [18 empty] | Septic tank had 6" sludge and 2" scum Pump tank had 2" sludge. Fluffed peat. CC1-37499 ETM1-77h 9m CC2-37689 ETM2-77h 50m | This AOSS should now return to normal function after having provided the above state routine maintenance. |  |  | 12:00 AM
09/10/2020 |  | Routine/Scheduled | 02-120-0905A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. |  |  | Puraflo |  | Pump |  |  |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 09/10/2020 | Jan 1 1900 3:00AM
01/06/2020 |  | Routine, Scheduled | C07-180-0258 | Roanoke | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Alleghany-Roanoke | Advanced Environmental & Septic, LLC | 1934000259 | Rodney | Rice | 1.000000 |  | Microfast |  | Pump | Distribution Box |  | None |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [18 empty] | [Comments]: septic tank and pump tank need to be pumped. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/06/2020 | Jan 1 1900 10:00AM
08/19/2020 |  | Routine, Scheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Orenco Advantex |  |  |  |  | None |  | ["Attached Growth Medium","Effluent Screens","Recirculation Pump"] | ["Attached Growth Medium","Effluent Screens","Recirculation Pump"] |  | Acceptable | Clear | [5 empty] | 08/19/2020 | Pump tank | 10.000000 | [7 empty] | Pump Amps 8.34 Pump Amps 9.71/9.89 Septic Sludge 3" Scum 0 ATU Sludge 4" Scum 0 Pump Sludge 0 Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 08/19/2020 | Jan 1 1900 3:15PM
12/04/2020 |  | Routine/Scheduled | 199-16-0003 | York | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Peninsula | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 2000 | Norweco Singulair ATU |  | Gravity | Distribution Box | Aggregate Trench |  | 450.000000 |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | Musty | Clear | [15 empty] | Routine Service Trash Tank - normal level Aeration Tank - aspirator serviced Clarifier - filter serviced. Distribution Box - concrete - all laterals accepting effluent. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 12/07/2020 | Jan 1 1900 8:30AM
06/25/2020 |  | RoutineScheduled | 08-195-219-DIS | Washington | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Mount Rogers | S.E.P.T.I.C., Inc. |  | Denny | Deel |  |  | FAST |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
10/16/2020 |  | RoutineScheduled | 139-05-0119 | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | dovel enterprises |  | jerry | dovel | 1.000000 | 1000 | 1000 |  | Pump | Pressure | Drip |  |  | [] | [] | YES | [16 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 10/29/2020 | 12:00 AM
10/16/2020 |  | Routine/Scheduled |  | Frederick | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Lord Fairfax | POWELLS PLUMBING, INC. | 1942001036 | Kurt | Holthaus | 1.000000 | 1000 | Sandfilter, Recirculating |  | Pump | Distribution Box | Aggregate Trench |  | 600.000000 | ["Distribution Pump Operation","Effluent Screens","Sludge/Scum Accumulation"] | ["Distribution Pump Operation","Effluent Screens","Sludge/Scum Accumulation"] | N/A | [17 empty] | Annual Inspection - Replaced effluent filter, sewer pump, pumped pump chamber and septic tank. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 11/17/2020 | 11:58 AM
06/12/2020 | Alternative | RoutineScheduled | 166-12-181 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers |  |  | joel | pinnix | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
06/17/2020 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Soils, Inc. | 1940001392 | Markham | Smith | 2.000000 | 1500 | Mirofast 0.75 in a Hanover 1500 top seam tank | ZonerMaster | Pump | Pressure | Drip | UV |  | [] | ["Attached Growth Medium","Septic Tank Baffles","SludgeScum Accumulation","Dispersal System Operation","Control Operation"] | NA | None | [6 empty] | 06/27/2020 | Sample Chamber | 23.000000 | [8 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 07/31/2020 | 12:00 AM
05/11/2020 |  | Routine/Scheduled | 09-120-0117A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. |  |  | Hoot |  | Pump |  |  |  |  | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 05/11/2020 | Jan 1 1900 12:15PM
05/04/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | SES MidAtlantic LLC | 1942001203 | James | Green | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter" ,"Dispersal System Operation"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. Hydraulic unit leaking. | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 |  | 04/15/2021 | 09:00 AM
10/06/2020 |  | Routine, Scheduled | 175-17-0416 | Prince William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Biomicrobics MicroFAST |  | Pump | Drip | Drip Tubing | None |  | ["Blower/Compressor/Aerator Operation"] | ["Blower/Compressor/Aerator Operation"] |  | Acceptable | Good | [15 empty] | Spin filter cleaned. Water Meter Reading 72800 Septic Sludge 8" Scum 0 ATU Sludge 12" Scum 0 Pump Sludge 2" Scum 0 Hydraulic unit housing cracked. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 10/06/2020 | 04:20 PM
05/14/2020 |  | Routine, Scheduled | 175-03-0826 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Aquarobic Mini Plant |  |  |  |  | None |  | ["Blower/Compressor/Aerator Operation"] | ["Blower/Compressor/Aerator Operation"] |  | Good | Good | [15 empty] | Pump Amps 5.83 Blower Amps 2.05 Septic Sludge 6" Scum 0 Mound needs grass cutting. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 05/14/2020 | 11:31 AM
06/08/2020 |  | RoutineScheduled | 109-07-0338 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Ecoflo |  | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation","Attached Growth Medium"] | ["Distribution Pump Operation","Effluent Screens","Attached Growth Medium"] | NA | Musty | [15 empty] | Inspected | Sludge levels- 6-12" Sludge in Septic tank. Tank was pumped and internally inpsected after my Visit by , Peat dry, little use and in good condition for age | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 06/08/2020 | 05:30 PM
10/31/2020 |  | RoutineScheduled | 133 17 0272 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1000 | Advantex |  | Pump | Pressure | Drip |  |  | ["None"] | ["None"] | [18 empty] | Annual inspection. 14" of solids in septic tank. Cleaned septic tank filter. Cleaned drip field spin filter. Flushed treatment unit manifold. Tested floats, pumps and alarm. Flushed drip field. Very slimy condition in treatment unit. Suspect toxic substance. Septic tank needs to be pumped out to alleviate toxic condition and empty solids from septic tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 11/06/2020 | 07:03 PM
09/03/2020 |  | Routine/Scheduled | 149-STS-10167 | Prince George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Crater | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. |  |  | Aqua Klear |  | Pump |  |  |  |  | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [9 empty] | 9.000000 | [7 empty] | Grab Bod sample | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 09/03/2020 | Jan 1 1900 10:00AM
10/19/2020 |  | Reportable Incident |  | Greene | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Blue Ridge | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Distribution Pump Operation" ,"Control Operation" ,"Auxiliary Filter"] | ["Distribution Pump Operation" ,"Control Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | High level alarm caused by slow drip rate. Cleaned dirty disc filters, pump intake, and secondary backwash valves. Highly recommend the addition of an effluent filter and lid to grade on septic tank. Recommended pump out and back flush of pump tank to try to eliminate debris. Also recommended to no longer use garbage disposal. Repaired leak at air release valve. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
02/14/2020 |  | Routine, Scheduled | 234-14-411 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesapeake | R & K Septic, Inc. |  | Tina | Van Holten |  |  | Clearstream ATU |  | Pump | Drip | Elevated Sand Mound | UV Light |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] |  |  | 4.71 | 4.110000 | 5.000000 | [13 empty] | [Comments]: Replaced UV Bulb | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/14/2020 | Jan 1 1900 9:45AM
11/17/2020 |  | Routine, Scheduled | 153-STS-20299 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Biomicrobics MicroFAST |  |  |  |  | None |  | ["Blower/Compressor/Aerator Operation"] | ["Blower/Compressor/Aerator Operation"] |  | Acceptable | Clear | [5 empty] | 11/17/2020 | Pump tank | 12.000000 | [7 empty] | Spin filter cleaned. Pump Amps 12.42 ETM 31 hrs Cycles 196 Water Meter Reading 22000 Septic Sludge 6" Scum 0 ATU Sludge 5" Scum 0 Pump Sludge 0 Scum 0 On 5 mins Off 2 hrs 50 mins | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 11/17/2020 | 01:10 PM
12/08/2020 | Alternative | RoutineScheduled | 159-08-180 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Church View Septic Service Inc. | 1942001302 | Charles | Langford | 1.000000 | 1000 | Clearstream |  | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation"] | ["Distribution Pump Operation"] | NA | [16 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12/08/2020 | 12:00 AM
10/26/2020 |  | RoutineScheduled | 033-08-0114-SR | Caroline | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  | ["Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Control Operation" ,"Attached Growth Medium" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Level Sensor Operation"] | ["Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Control Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Attached Growth Medium"] | YES | [15 empty] | Will be sent separately | Inspected | Inlet wedge lids leaking on septic tank and pump tank. Pump tank needs to be pumped out. Proposal to be sent to homeowner to reseal wedge lids. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
02/17/2020 |  | Routine, Scheduled | 10-100-0366 | Accomack County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Eastern Shore | DUER, PETE C | 1942001051 | PETE | DUER | 1.000000 | 1000 | Septic Tank Only | Eljen Geotextile Sandfilter | Pump | None | None | None |  | ["None"] | ["None"] | [18 empty] | [Comments]: Aoss Inspection. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/24/2020 | 11:37 AM
06/09/2020 |  | RoutineScheduled | 175-10-0129 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast |  | Pump | Gravity | Trenches | UV |  | ["SludgeScum Accumulation","BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [9 empty] | 73.000000 | [5 empty] | Attached to this report |  | Septic-6"sludge 0"scum/ Microfast-12"sludge (Pump out required) BOD results should improve after pump out/ Pump tank-3"sludge ( pump out needed due to sludge close to the pump intake) No breakout or spongy areas on the drainfield Blower air filter cleaned/ Counts: pump-3797 ETM-414.24/ Drainfield boxes uncovered and in good shape, marked with 4 pipes each. Some holes around the system components from animals digging. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  |  | 12:00 AM
01/28/2020 |  | Routine, Scheduled | 179-14-0309-STWP | Stafford County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | None | None | Pump | Distribution Box | Aggregate Trench |  |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/02/2020 | 11:52 AM
01/06/2020 |  | Routine, Scheduled |  | Essex County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Three Rivers | Madison Environmental LLC | 1934 000061 | Larry | Madison, Jr. |  |  | Clearstream ATU |  | Pump |  |  |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/06/2020 | 03:30 AM
02/12/2020 |  | Routine, Scheduled |  | Prince William County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Clearstream |  | Pump |  |  | None |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] |  | Good | Good | [5 empty] | 02/12/2020 |  | 10.000000 | [7 empty] | [Comments]: Pump Amps 9.80 ETM 580h Cycles 5333Septic Sludge 9" Scum 3"ATU Sludge 2" Scum 0Pump Sludge 4" Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/12/2020 | 04:50 PM
06/11/2020 |  | RoutineScheduled | 04-125-072 | Dickenson | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. |  | Denny | Deel |  |  | FAST |  | Gravity | Gravity | Mound | Not Applicable | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
10/10/2020 |  | RoutineScheduled | SD-12-96 | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Wastemaster Inc |  | Timothy | Jenkins | 2.000000 |  | ATU | Post Air | Pump | Gravity | Discharge | UV |  | [] | [] |  | Musty | Clear | 7.200000 | 8.600000 |  |  |  | 10/10/2020 |  | 1.800000 |  | 0.800000 | 4.000000 | [5 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 10/26/2020 | 09:45 AM
04/09/2020 |  | Routine, Scheduled | 175-18-0399 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Biomicrobics MicroFAST |  |  |  |  | UV Light |  | ["Blower/Compressor/Aerator Operation"] | ["Blower/Compressor/Aerator Operation"] |  | Good | Clear | [5 empty] | 04/09/2020 | Pump tank | 22.000000 | [7 empty] | Spin filter cleaned. Pump Amps 7.70 ETM 130 h 32 m Cycles 595 Water Meter Reading 5030 Septic Sludge 6" Scum 4' Pump Sludge 0 Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/09/2020 | 03:39 PM
08/14/2020 |  | Pump-Out Only |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU | [8 empty] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 08/14/2020 | Jan 1 1900 2:00PM
07/06/2020 |  | Reportable Incident | 700-STS-6889 | Newport News | This AOSS should now return to normal function after having provided the above state routine maintenance | Approved | EHD - Peninsula | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | None | None | Gravity | Distribution Box | Aggregate Trench | None | 450.000000 | ["Dispersal System Operation"] | ["Dispersal System Operation"] | N/A | [17 empty] | Owner constructed deck over septic tank and wheelchair ramp over / adjoining to distribution box, damaging same. Replaced damaged distribution box with new - absorption tile = terracotta tile - conveyance line spliced, terracotta tile spliced to new corrugated pipe. | This AOSS should now return to normal function after having provided the above state routine maintenance |  | 07/07/2020 | Jan 1 1900 1:00PM
04/27/2020 | Alternative | RoutineScheduled | 166-13-097 | Northumberland | This AOSS is functioning as designed and in accord | Approved | EHD - Three Rivers | [13 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accord |  |  | 12:00 AM
10/05/2020 |  | Initial Visit | 177-STS-87544 | Spotsylvania | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | EZ Treat Sandfilter | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NO | [15 empty] | Will be sent separately | Inspected | START-UP INSPECTION | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/09/2021 | 03:25 PM
09/02/2020 |  | RoutineScheduled |  | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic Tank | Pump Tank/ Puraflo | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium"] | ["Attached Growth Medium"] | NO | [17 empty] | Septic tank-6"sludge 0"scum/ Pump Tank-2"sludge (No pump out needed at this time) Puraflo media fluffed during inspection and is in good shape. Counts: cc1-4273 ETM-74.35 h/ cc2-4235 ETM-70.51 h/ No breakout or spongy areas on the drainfield. Pumps and controls operating properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
08/20/2020 |  | RoutineScheduled | 179-14-0283-SWP | Stafford | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Septic Works LLC | 1942001080 | michael | smith | 1.000000 |  | Orenco Advantex | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | some erosion around septic tank exposing septic tank recommend adding dirt around area | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/25/2021 | 08:10 AM
01/17/2020 |  | Routine, Scheduled |  | Loudoun County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim |  |  | None | None | Pump | Distribution Box | Aggregate Trench | [5 empty] | YES | YES | [15 empty] | [Comments]: Anua tank needs pumped out | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/02/2020 | 04:43 AM
01/09/2020 |  | Routine, Scheduled | 099-14-0038-SR | King George County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Ware, Michele P | 1942001165 | Michele | Ware |  |  | Septic Tank Only | Septic Tank Only | None | None | None | None |  |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/10/2020 | 09:35 AM
03/03/2020 |  | Routine, Scheduled | 2008-143-0183 | Henrico County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Henrico | [8 empty] | Pump |  |  |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/03/2020 | 12:30 PM
02/21/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Fairfax | MCKIM, STEPHEN E | 1934000043 | STEPHEN | MCKIM |  |  | Septic Tank Only | Septic Tank Only | None | None | None | None | [21 empty] | [Pumpout Comments]: Pumped out septic/atu/pump tank | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/02/2020 | Jan 1 1900 8:41AM
10/15/2020 |  | Routine/Scheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | POWELLS PLUMBING, INC. | 1942001036 | Kurt | Holthaus | 1.000000 | 1000 | Sandfilter, Recirculating |  | Pump | Distribution Box | Aggregate Trench |  | 450.000000 | ["None"] | ["None"] | N/A | [17 empty] | Annual Inspection - No repairs or service needed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 10/16/2020 | 10:18 AM
09/14/2020 |  | Pump-Out Only |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | POWELLS PLUMBING, INC. | 1942001036 | Kurt | Holthaus | 1.000000 | 1000 | Multiflo FTB |  | Pump | Distribution Box | Aggregate Trench |  |  | ["Sludge/Scum Accumulation"] | ["Sludge/Scum Accumulation"] | N/A | [17 empty] | Pumped septic tank and Multiflo. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 10/09/2020 | 02:00 PM
07/08/2020 | Alternative | RoutineScheduled | 149-17-0025 | King & Queen | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Church View Septic Service Inc. | 1942001302 | Charles | Langford | 1.000000 | 1000 | Aquasafe |  | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens","SludgeScum Accumulation"] | ["Effluent Screens"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
11/16/2020 |  | RoutineScheduled | 181-06-0267 | Rockbridge | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Central Shenandoah | Valley Soil & Environmental Consulting, LLC | 1942001218 | John | Lam | 4.000000 | 4000 | Septic tank only |  | Pump | Pressure | Trenches | Not Applicable | 600.000000 | ["Control Operation","Effluent Screens"] | ["Effluent Screens"] | YES | [17 empty] | LPD system #4; HD ID # 181-04-0278; Cleaned septic tank effluent filters at all 4 dwellings; Lot 23: 7" solids, added handle to filter; Lot 25: 7" solids; Lot 28: 6" scum and 10" solids; Lot 30: 12" solids. Transfer pump: 8.55 amps; LPD pump: 15.62 amps; alarm light is "ON" at transfer pump control panel and panel buzzer does not work; transfer pump tank at normal water level and alarm float is functional; LPD pump control panel buzzer not functional but alarm light is functional. The transfer pump control panel or panel circuit board will require replacement in order to make the alarm system operational. Recommend replacing both control panels with control panels without a circuit board. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. |  | 12/04/2020 | 12:00 AM
07/29/2020 |  | RoutineScheduled | 179-09-0104-SWP | Stafford | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Recirculation Pump" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Control Operation" ,"Attached Growth Medium" ,"Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Level Sensor Operation"] | ["Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Attached Growth Medium" ,"Auxiliary Filter" ,"Control Operation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Recirculation Pump"] | YES | [15 empty] | Will be sent separately | Inspected | . Replaced split drip filter. Repaired broken flex line in drip manifold. Replaced bad emitter in dripfield. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
12/21/2020 |  | RoutineScheduled | 047-17-198 | Culpeper | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Attached Growth Medium" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | The inlet & outlet risers on the pump tank are leaking. If you get alarms during periods of heavy rains, we would recommend excavating by hand and resealing the risers. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/09/2021 | 03:25 PM
06/11/2020 |  | Routine/Scheduled | 2002-143-0227 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Henrico | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1500 | Orenco Advantex | None | Pump | Distribution Box | Aggregate Trench | None |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | [17 empty] | The Recirculation Pump has exceeded its expected life; the Advantex Media Sheets have exceeded their expected life, and the Media Unit Lid's support Struts have failed; in the Discharge Tank, the Float Tree is not properly secured, and the Floats & Vortex Filter have all exceeded their expected life; the Control Panel has exceeded its expected life; | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 06/16/2020 | 04:07 PM
11/02/2020 | Alternative | RoutineScheduled | 171-09-0007 | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | None | Clear | 6.280000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 11/06/2020 | 03:50 PM
10/26/2020 |  | RoutineScheduled | 154-08-0299 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | All In Septic Services | 1942001442 | Dennis | Mitchell | 2.000000 | 2500 | MicroFas |  | Pump | Pressure | Drip | Not Applicable |  | [] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Effluent Screens"] | YES | Musty | Clear | [14 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 10/26/2020 | 03:30 PM
04/23/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Payment | EHD - Loudoun | Great Falls Septic Service, Inc | 1942001301 | Josh | Hott |  |  | Delta Environmental Products, UC Series | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/27/2021 | 11:51 AM
07/16/2020 | Alternative | Routine/Scheduled | 128-04-172 | Essex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | Biomicrobics MicroFAST | None | Pump | Drip | Drip Tubing | None | 450.000000 |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | Musty | Clear | [15 empty] | Routine service conducted. Trash tank in normal operating level. FAST unit in normal operating level - blower serviced. Discharge tank in normal operating level - discharge pump serviced. Drip headworks serviced - drip screen serviced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 07/17/2020 | 07:30 AM
01/15/2020 |  | Routine, Scheduled | 228-15-0296 A | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Virginia Beach | [8 empty] | Pump | Drip | Elevated Sand Mound | UV Light |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] |  |  |  | 7.000000 | 4.000000 | [13 empty] | [Comments]: Replaced alarm buzzer | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/15/2020 | Jan 1 1900 1:30PM
08/10/2020 |  | RoutineScheduled | 07-100-1047 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Bundick Well & Pump | 1942001051 | Peter | Duer | 1.000000 | 1250 | Septic Tank | Purflo | Pump | Pressure | Pad | Not Applicable | 600.000000 | ["None"] | ["None"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 11/05/2020 | 11:35 AM
03/18/2020 |  | Routine, Scheduled |  | Loudoun County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | None | None | Pump | Manifold | [23 empty] | [Comments]: Septic tank riser concrete lid needs replaced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/12/2020 | 02:21 PM
10/14/2020 |  | Routine/Scheduled | 2019-143-0005 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Old Dominion Onsite, Inc. | 1942001549 | Russell | Revis | [11 empty] | N/A | [7 empty] | 10/13/2020 | Pump Chamber | 3.000000 |  | 30.000000 | [6 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 03/24/2021 | 08:30 AM
03/09/2020 |  | Routine, Scheduled | 08-120-0496A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesterfield | Madison Environmental LLC |  | Larry | Madison, Jr. |  |  | Hoot |  | Pump |  |  |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [18 empty] | Lab results not reported by Operator, EHS chose "No" in order to allow saving updated entry. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/09/2020 | Jan 1 1900 12:00PM
04/11/2020 |  | Routine, Scheduled |  | Prince William County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Prince William | JENKINS, TIMOTHY R | 1942001062 | TIMOTHY | JENKINS | 1.000000 |  | Aero-flo ATU | Sandfilter, Recirculating | Pump | Drip | Alternative Discharge | None |  | ["Recirculation Pump","SludgeScum Accumulation"] | ["None"] |  | Musty | Clear | 6.800000 |  | 70.000000 | 2.200000 | [11 empty] | [Pumpout Comments]: Highly recommend having all tanks pumped out. High solid levels will soon carry over to sand filters. [Comments]: System operating properly at this time | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/23/2020 | 03:30 PM
05/30/2020 |  | RoutineScheduled | 177-06-0063-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Wastemaster Inc |  | Timothy | Jenkins | 2.000000 |  | ATU |  | Gravity | Gravity | Drip |  |  | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 06/29/2020 | 04:00 PM
02/25/2020 |  | Routine, Scheduled |  | Loudoun County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | None | None | Pump | Manifold | [23 empty] | [Comments]: Snakes in valve boxes. Careful when opening and adjusting valves. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/16/2020 | 11:28 AM
05/18/2020 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Payment | EHD - Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 2.000000 |  | Orenco Advantex | Orenco Advantex | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Dispersal System Operation"] | ["Control Operation" ,"Dispersal System Operation"] | NA | [7 empty] | 05/18/2020 |  | 4.000000 | [5 empty] | Will be sent separately | Inspected | Output function on discharge pump 2 was not operational. Replaced board in panel | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 04/26/2021 | Jan 1 1900 9:04AM
02/27/2020 |  | Routine, Scheduled |  | Prince George County | This AOSS should now return to normal function after having provided the above stated routine maintenance. | Paid | EHD - Crater | Madison Environmental LLC | 1934 000061 | Larry | Madison, Jr. |  |  | Clearstream ATU |  | Pump | Distribution Box |  |  |  | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | [19 empty] | This AOSS should now return to normal function after having provided the above stated routine maintenance. |  | 02/27/2020 | Jan 1 1900 1:00AM
05/08/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Payment | EHD - Loudoun | Great Falls Septic Service, Inc | 1942001301 | Josh | Hott | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/27/2021 | 11:51 AM
04/15/2020 |  | Routine, Scheduled |  | Essex County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Three Rivers | Cuthbertson, Kent | 1942001034 | Kent | Cuthbertson | 1.000000 | 428 | Clearstream ATU | Septic Tank Only | Pump | Distribution Box | Aggregate Trench | None |  | ["None"] | ["None"] | [18 empty] | [Pumpout Comments]: No pump out is required based on the observations stated above. [Comments]: Inspected the high water alarm, control panel, aerator, and all floats. Performed a 1 minute draw down test to confirm timer seting. Unit is well maintained and there are no solids in the trash tank, the pump tank is only one third full...the unit is used only periodically. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/18/2020 | 07:34 AM
04/29/2020 |  | RoutineScheduled | 099-18-0157 C-SWP | King George | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Attached Growth Medium" ,"Auxiliary Filter" ,"Control Operation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | ["Attached Growth Medium" ,"Control Operation" ,"Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | YES | [15 empty] | Will be sent separately | Inspected | BOD collected, waiting results. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
10/16/2020 |  | Routine/Scheduled | 06-142-0006 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chickahominy | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1500 | Orenco Advantex |  | Pump | Distribution Box | Aggregate Trench | None | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | None | Clear | [15 empty] | Real Estate Inspection - Service Processing Tank - normal operating level - RSV, Recirc. Pump & Effluent screen serviced. Treatment Module - media drapes & spray grid serviced Pump Tank - discharge pump serviced - float sensors and controls operating properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 10/16/2020 | Jan 1 1900 7:50AM
11/11/2020 |  | Follow-Up | 153-STS-20240 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Soils, Inc. | 1940001392 | Markham | Smith | 2.000000 | 1500 | Mirofast 0.75 in a Hanover 1500 top seam tank |  | Pump | Gravity | Trenches | Not Applicable | 750.000000 | [] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","SludgeScum Accumulation","Septic Tank Baffles"] | NA | None | [16 empty] | Half-seam tank, compartment 1 had 0 sludge. Compartment 2 had 2 inches of sludge. Pump chamber had 0 sludge. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 11/11/2020 | 12:40 PM
07/13/2020 |  | Follow-Up | SD-10-208 | Fauquier | This AOSS should now return to normal function after having provided the above state routine maintenance | Approved | EHD - Rappahannock-Rapidan | SES Mid Atlantic | 1942001236 | S. Michael | Lynn | 1.000000 | 20000 | EcoPod | EcoPod | Pump | Pressure | Drip | Not Applicable | 6742.000000 | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | N/A | Pungent | Cloudy | [15 empty] | Blower on stage 1 has been down due to VFD issue. Works sometimes, times out and overheats sometimes. Piping re routed using 2 5 HP blowers for now. | This AOSS should now return to normal function after having provided the above state routine maintenance |  | 07/13/2020 | 05:00 PM
02/19/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Fairfax | MAJEWSKI, SHANE | 1934000134 | SHANE | MAJEWSKI | 1.000000 | 1500 | Septic Tank Only | Septic Tank Only | Pump | Distribution Box | Aggregate Bed | None | 600.000000 | ["None"] | ["None"] | [18 empty] | [Comments]: Maintenance Inspection Open pods | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/06/2020 | Jan 1 1900 8:19AM
01/17/2020 |  | Routine, Scheduled |  | Loudoun County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | EcoPod | None | Gravity | Distribution Box | Gravel-Less Trench | [23 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/02/2020 | 04:43 AM
02/13/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Fairfax | Hott, Joshua D. | 1942001301 | Joshua | Hott | 1.000000 | 2000 | Septic Tank Only | Microfast | Pump | Distribution Box | Aggregate Trench | None |  | ["None"] | ["None"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/18/2020 | Jan 1 1900 3:03PM
10/27/2020 |  | Follow-Up | 099-18-0120 C-SWP | King George | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart |  |  | Orenco Advantex | none | Pump | Gravity | Drip | UV |  |  |  | NA | [9 empty] | 8.000000 |  | 1.800000 |  |  |  | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
12/04/2020 | Alternative | Routine/Scheduled | 157-05-269 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | PremierTech, EFX |  | Pump | None | Aggregate Bed | None | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | Musty | Clear | [15 empty] | Routine Service Primary Septic Tank - normal level - effluent screen serviced. Pump Basin - normal level - intact - pump, float sensors & controls operating. Biofilter - Fiberglass - intact - peatmoss in poor condition - raked / turned. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 12/07/2020 | 07:45 AM
11/17/2020 |  | RoutineScheduled | 061-19-147 | Fauquier | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Clearstream | none | Pump | Gravity | Drip | UV |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [7 empty] | 11/17/2020 |  | 126.000000 |  | 1600.000000 |  |  |  | Will be sent separately | Inspected | Treatment did not look good, failed sampling requirements. Return line gauge reading zero duri g first test cycle and ball valve was shut. After changing very dirty and slimy spin filter, pressure increased to 5 psi. This is still below minimum pressure needed for Geoflow emitters to work. It is questionable if pump can achieve flushing velocity and impossible to measure, with any degree of accuracy, without a flow meter. Observed multiple wet/soggy areas at the toe of the mound. Alarm horn was muted (switch turns off the horn). Design engineer is reported to be retired and not returning phone calls. Owner should reach out to AOSE, Clearstream representative, and builder for resolution. | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
06/05/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/27/2021 | 01:26 PM
06/26/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/14/2021 | 04:27 PM
04/06/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Fairfax | BLEVINS, JOEL R, SR | 1934000415 | JOEL | BLEVINS |  |  | Microfast | Septic Tank Only | None | None | None | None |  | ["None"] | ["None"] | [18 empty] | [Comments]: Compressor is strong, cleaned the air filter and the ditches are dry. There is 18" of sludge in treatment tank - suggest getting it pumped. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/07/2020 | Jan 1 1900 12:24PM
01/31/2020 |  | Routine, Scheduled |  | Lancaster County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Three Rivers | Cuthbertson, Kent | 1942001034 | Kent | Cuthbertson |  |  | Septic Tank Only | Septic Tank Only | Pump | Distribution Box | None | UV Light |  | ["None"] | ["Disinfection"] | [16 empty] | Attached to this report |  | [Lab Comments]: All samples were less than permit limis. High UV caused us to clean the UV system as mentioned above. [Comments]: Cleaned the UV set and polished all light casings. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/12/2020 | 08:41 AM
08/12/2020 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 2705051738 | Joshua | Hott | 1.000000 | 1500 | Septic | Puraflo |  |  | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
11/09/2020 |  |  | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001301 | Joshua | Hott | [9 empty] | [] | [] | [8 empty] | 11/30/2020 | Sample Chamber | 6.000000 | [5 empty] | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
09/25/2020 |  | RoutineScheduled | 03-163-0175sr | New Kent | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chickahominy | Onsite Maintenance Team | 1942001039 | Corey | Braxton | 3.000000 |  | Microfast |  | Pump |  |  |  |  | [] | ["Attached Growth Medium","Level Sensor Operation","BlowerCompressorAerator Operation","Control Operation"] | NA | Musty | Cloudy | 6.900000 | 3.000000 | [14 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. |  |  | 12:00 AM
11/02/2020 |  | Initial Visit | 16-174-0182 | Prince George | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Crater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | Owner called due to the red light being on. Serviced system. Checked the pump, panel, & floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. Installed a re-build kit on the aerator. Re-wired panel. Replaced the alarm float, timer, and alarm light bulb. The timer is set to 6.5 minutes every 2 hours. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 11/02/2020 | Jan 1 1900 12:00PM
09/15/2020 |  | RoutineScheduled |  | Rockingham | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | Repaired switch in conrol panel | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance |  | 04/26/2021 | 09:04 AM
04/09/2020 |  | Routine, Scheduled | SD-02-374 | Culpeper County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | JENKINS, TIMOTHY R | 1942001062 | TIMOTHY | JENKINS | 1.000000 |  | Biomicrobics MicroFAST | Septic Tank Only | None | Drip | Alternative Discharge | Chlorine |  | ["None"] | ["None"] | [18 empty] | [Comments]: No Discharge from Wetlands | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/22/2020 | 02:00 AM
07/28/2020 |  | RoutineScheduled | S18-111-0027 | Botetourt | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1000 | Biomicrobics Fast |  | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | NA |  | Clear | 7.330000 | 10.100000 |  |  | 17.5 c | 07/28/2020 | Pump Chamber | 237.000000 |  |  | 20.700000 |  |  | Will be sent separately | Inspected | 6 Month Initial Laboratory sampling of an advantex AX20RT -DO 10.1, Ph 7.33 , Temp 17.5, TSS 20.70 , BOD 237 PACE LAB A week prior we came out for a service call and found a loose wire on the blower. It was corrected and running fine for the treatment however no port to sample thus we collected from the pump tank. Thus the lab results are higher due to 1 week operation. System is fully operational | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 07/29/2020 | Jan 1 1900 9:30AM
01/17/2020 |  | Routine, Scheduled | {FIPSCode}-STS-1358 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesapeake | R & K Septic, Inc. |  | John | Butt, Jr |  |  | Clearstream ATU |  | Pump | Drip | Elevated Sand Mound | UV Light |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] |  |  | 5.31 | 8.310000 | 4.000000 | [13 empty] | [Comments]: Needs new UV | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/17/2020 | Jan 1 1900 12:30PM
11/13/2020 |  | Routine, Scheduled | 175-16-0241 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | EZ Treat Sandfilter |  |  |  |  | None |  | ["Dispersal System Operation","Effluent Screens"] | ["Dispersal System Operation","Effluent Screens"] |  | Acceptable | Clear | [15 empty] | Pump Amps 8.60 Septic Sludge 10" Scum 0 Pump Sludge 3" Scum 0 On 1 min 50 secs Off 11 minutes | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 11/13/2020 | 01:23 PM
11/04/2020 |  | RoutineScheduled | 107-07-0278 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Pump | Pressure | Drip | Not Applicable |  | ["Effluent Screens","Auxiliary Filter"] | ["Effluent Screens","Auxiliary Filter"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 06/02/2021 | 12:00 AM
12/16/2020 | Alternative | Routine/Scheduled | 136-03-567 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | None | None | Pump | Distribution Box | Gravel-Less Trench | None | 450.000000 |  | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | [17 empty] | Real Estate Inspection Real Estate Inspection - COSS - pump to gravity. Septic tank - normal level - intact - pumped for inspection. Pump Tank - normal level - pump, float sensors & controls operating. Distribution box - plastic - intact - all laterals accepting effluent. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 12/17/2020 | 09:00 AM
05/05/2020 |  | RoutineScheduled | 179-08-0115-SWP | Stafford | This AOSS is not functioning as designed or in accordance with the performance/Maintenance requirements | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["Dispersal System Operation" ,"BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | It appears that water is coming to the surface at the distal end of the lower drainfield line. We recommend uncovering the distribution box and checking to be sure that water is flowing evenly to the drainfield lines. | This AOSS is not functioning as designed or in accordance with the performance/Maintenance requirements |  | 04/09/2021 | 03:25 PM
02/21/2020 |  | Reportable Incident | 099-06-0342-SWP | King George County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001350 | Mike | Cook | 1.000000 |  | EcoPod | None | Pump | Drip | Drip Tubing | [22 empty] | [Comments]: Blower failed, replaced Fuji compressor. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/25/2020 | 07:16 AM
09/02/2020 |  | Initial Visit | 09-174-0111 | Prince George | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Crater | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 2000 | Norweco Singulair ATU | None | Pump | Distribution Box | Aggregate Trench | None | 450.000000 | ["Blower/Compressor/Aerator Operation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | Pungent | Discolored | [15 empty] | System / processing tank pumped empty for storage. Initial Visit - Alarm 08/31/2020 - System not functioning - discharge pump electrical connections destroyed by lawn care operations - requires pumpout and repair. 09/01/2020 - Processing tank pumped empty by "others" - Discharge tank left in high level condition. 09/02/2020 - Aspirator inspected and is in failure - requires replacement, discharge pump - new electrical splice box installed, new electrical wiring pulled to discharge tank - pump and float sensors placed back into operation. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 09/02/2020 | Jan 1 1900 2:00PM
04/06/2020 |  | Routine, Scheduled | 175-90-0082 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green |  |  |  |  | Pump | Manifold | Aggregate Trench | None |  | ["Effluent Screens"] | ["Effluent Screens"] | [18 empty] | Demand control panel to LPD. 3 1/2" draw down per minute Pump Amps 19.47 Septic Sludge 1" Scum 0 Pump Sludge 1" Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/06/2020 | 08:07 AM
10/27/2020 |  | Follow-Up | 061-19-146 | Fauquier | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Clearstream | none | Pump | Gravity | Drip | UV |  |  |  | NA | [7 empty] | 10/27/2020 |  | 8.000000 |  | 1.800000 |  |  |  | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
11/10/2020 |  | RoutineScheduled |  | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Environmental Systems Service | 1942001050 | Troy | Jenkins | 2.000000 |  | Septic Tank | Septic Tank |  |  | Drip |  | 1482.000000 | ["None"] | ["None"] |  |  |  | 6.960000 |  |  |  |  | 11/10/2020 | Sample Tap | 15.000000 |  |  | 14.000000 | 68.300000 |  | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12/08/2020 | 12:00 AM
08/18/2020 | Alternative | Routine/Scheduled | 166-06-197 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | Ecoflo | None | Pump | Distribution Box | Aggregate Trench | None | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | Musty | Clear | [15 empty] | Routine Service conducted. Primary septic tank in normal level - effluent screen serviced. PeatBiofilter serviced - Peat is wet and had some ponding present - drained following rake out Pump Station in normal level - pump, float sensors and controls operating properly. Distribution box - plastic - Above normal level - heavy rain events last several days. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 08/25/2020 | 02:00 PM
06/10/2020 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump | Drip | Elevated Sand Mound | UV Light |  | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  | 12.36 | 6.720000 | 3.700000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 06/10/2020 | Jan 1 1900 1:00PM
12/15/2020 |  | RoutineScheduled | 109-07-0396 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 750 | MultiFlo ATU |  | Pump | Pressure | Drip |  |  | ["None"] | ["None"] | [18 empty] | Annual inspection. 12" of solids in septic tank. Tested pump and level controller. Cleaned drip manifold spin filter. Tested alarm. Aeration is adequate. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12/18/2020 | 07:03 PM
06/22/2020 |  | RoutineScheduled | 179-09-0007-SP | Stafford | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Distribution Pump Operation" ,"Auxiliary Filter"] | ["Distribution Pump Operation" ,"Auxiliary Filter"] | NA | [7 empty] | 06/22/2020 |  | 15.000000 | [5 empty] | Will be sent separately | Inspected | Routine inspection. Treatment looks good. Drip rate apparently back to normal. School needs to remove tree growing in dripfield in front of air release valves in upper zone. High level count at 67,039. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
06/08/2020 |  | RoutineScheduled | 179-18-0429-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | 90-Day Inspection. | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 |  | 04/09/2021 | 03:25 PM
10/20/2020 |  | Initial Visit | 099-STS-87654 | King George | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson |  |  | Orenco Advantex | none | Pump | Gravity | Drip | UV |  | ["Control Operation"] | ["Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Both zones dripping around 50% above design. Verified both solenoid valves completely shut, check valves holding, and no effluent to surface (from drip tubing leaks). Reduced run time to maintain proper dose. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
12/21/2020 |  | Reportable Incident |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | SES MidAtlantic LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Gravity | Gravity | Drip | Not Applicable |  | ["Control Operation"] | ["Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Installed new control panel & hydraulic unit. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/15/2021 | 09:00 AM
04/23/2020 |  | Routine/Scheduled |  | Warren | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Lord Fairfax | POWELLS PLUMBING, INC. | 1942001036 | Kurt | Holthaus | 1.000000 | 1000 |  |  | Pump | Manifold | Aggregate Trench |  | 450.000000 | ["Effluent Screens","Level Sensor (Float) Operation"] | ["Effluent Screens","Level Sensor (Float) Operation"] | N/A | [17 empty] | Annual Inspection - Replaced 3 floats and serviced effluent screen(s). | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 05/13/2020 | 08:29 AM
06/23/2020 |  | RoutineScheduled | 179-18-0284-SP | Stafford | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Effluent Screens" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Effluent Screens" ,"Recirculation Pump"] | YES | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/09/2021 | 03:25 PM
10/15/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | An inspection was done on an alternative septic system. The state requires that all alternative systems must be inspected EVERY year and filed with the state and county. The septic control panel is an exterior time dose. There is 1 pvc cleanout . The sewer line was camera snaked and was clear. The septic tank was pumped out . The ATU tank and air blower were inspected. The pump tank, pump, floats and force main were inspected. The 14 port concrete d-box was dug up it was 4" under the ground. All 7 header lines were camera snaked and were clear. The drain field was probed and dry. At time of inspection all components were in working condition | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/14/2021 | 04:27 PM
12/03/2020 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Gravity | Gravity |  | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | an inspection on a conventional pump septic system. The state requires that all conventional septic tanks must be pumped out EVERY 5 years and filed with the state and county. The septic control panel is a interior demand dose panel. There is 1 clean out near the house. It was behind the air conditioner. The pvc sewer line was camera snaked and was clear. The septic tank has a concrete riser on the outlet side of the tank. The septic tank was pumped out and the tank was inspected for any leaks and none were found. The pump tank, pump, floats and force main were inspected. The 9 port plastic d-box was dug up it was 10" under the ground. The 6 header lines were camera snaked and were clear. the drain field was probed and dry. at time of inspection all components were in working condition. | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 |  | 04/14/2021 | 04:27 PM
05/13/2020 |  | Reportable Incident |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [11 empty] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 05/13/2020 | Jan 1 1900 11:30AM
07/08/2020 | Alternative | Initial Visit | 157-98-129 | Mathews | This AOSS should now return to normal function after having provided the above state routine maintenance | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | Advanced Septic | None | Pump | Distribution Box | Aggregate Bed | None | 450.000000 |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | [17 empty] | Septic tank and pump tank pumped empty to effect repairs. Install in accordance with HDID 157-20-0001. Existing Puraflo pad/bed abandoned in place. Existing pump tank converted to Anua PuraSys Sequential Batch Reactor. New absorption bed installed. Existing septic tank and pump tank pumped empty to effect repairs. | This AOSS should now return to normal function after having provided the above state routine maintenance |  | 07/09/2020 | 08:30 AM
12/08/2020 |  | RoutineScheduled | 181-10-0056 | Rockbridge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Hunter E. Ayres, General Contractor | 1942001166 | Hunter | Ayres | 2.000000 | 4000 | Ecopod | Biomicrobics MicroFAST | Pump | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","Effluent Screens"] | ["Auxiliary Filter","Effluent Screens"] | YES | [17 empty] | Filters checked and cleaned. All control panels and pumps functioning properly. No apparent leaks in system or drain field area. System did not need to be pumped. Lids were properly secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 01/08/2021 | 08:10 AM
10/12/2020 |  | Pump-Out Only |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | POWELLS PLUMBING, INC. | 1942001036 | Kurt | Holthaus |  |  | Microfast | [6 empty] | ["Sludge/Scum Accumulation"] | ["Sludge/Scum Accumulation"] | N/A | [17 empty] | Pumped Microfast | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 11/18/2020 | 04:52 PM
09/04/2020 |  | RoutineScheduled | 099-09-0062-DS | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Wastemaster Inc |  | Timothy | Jenkins | 2.000000 |  | Advantex |  | Pump | Gravity | Discharge | UV |  | [] | [] |  | Musty | Clear | 7.200000 | 5.800000 |  |  |  | 09/04/2020 |  | 9.000000 |  | 0.800000 | 58.700000 |  |  | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 10/06/2020 | 12:15 PM
01/20/2020 |  | Pump-Out Only | 800-11-0138 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Western Tidewater | R & K Septic, Inc. |  | Tina | Van Holten | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/20/2020 | Jan 1 1900 2:00PM
09/22/2020 |  | RoutineScheduled | 175-04-0196 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | Aquarobic Services | 1934000142 | Michael | Blake |  |  | none | none | Pump | Gravity | Mound | Not Applicable |  | ["Auxiliary Filter" ,"Control Operation"] | ["Auxiliary Filter" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Air pre-filter cleaned. Pump standby light bulb was burnt out, replaced it. Bottom flange of blower housing exposed from settling, not causing any problems at this time. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 07/01/2022 | 10:30 AM
01/06/2020 |  | Routine, Scheduled | 05-160-0446 | Montgomery County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1934000259 | Rodney | Rice | 1.000000 |  | Delta Environmental Products, DF Series |  | Pump | Drip | Drip Tubing | None | 34.000000 |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/06/2020 | 03:30 PM
10/09/2020 |  | Routine, Scheduled | 175-17-0098 | Prince William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Biomicrobics MicroFAST |  | Pump | Drip | Drip Tubing | UV Light |  | ["Blower/Compressor/Aerator Operation"] | ["Blower/Compressor/Aerator Operation"] |  | Acceptable | Clear | [15 empty] | Spin filter cleaned. Pump Amps 7.63 ETM 760 hrs 20 mins Cycles 3972 Water Meter Reading 235900 Septic Sludge 1" Scum 0 ATU Sludge 1" Scum 0 Pump Sludge 0 Scum 0 UV Bulb needs replacing. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 10/09/2020 | 08:50 AM
04/04/2020 |  | Routine, Scheduled |  | Warren County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Lord Fairfax | DOVEL, JERRY A | 1942001116 | JERRY | DOVEL | 1.000000 |  | Advanced Septic | Septic Tank Only | None | Distribution Box | None | None | [22 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/22/2020 | 10:10 AM
12/15/2020 |  | Routine, Scheduled | 153-STS-20278 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Biomicrobics MicroFAST |  | Pump | Drip | Drip Tubing | None |  | ["Blower/Compressor/Aerator Operation","Level Sensor (Float) Operation"] | ["Blower/Compressor/Aerator Operation"] |  | Acceptable | Clear | [5 empty] | 12/15/2020 | Pump tank | 14.000000 | [7 empty] | Needs new low water float. Pump 1 Amps 11.25 ETM 68 hrs Cycles 713 Water Meter Reading 43750 Septic Sludge 5" Scum 0 ATU Sludge 4" Scum 0 Pump Sludge 0 Scum 0 On 6 mins Off 2 hrs 51 mins | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 12/15/2020 | 12:20 PM
07/17/2020 |  | Follow-Up |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | POWELLS PLUMBING, INC. | 1942001036 | Kurt | Holthaus | 1.000000 | 1500 | Microfast |  | Pump | Drip | Drip Tubing |  |  | ["Sludge/Scum Accumulation"] | ["Sludge/Scum Accumulation"] | N/A | [17 empty] | Pumped Microfast. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 07/31/2020 | 11:00 AM
04/24/2020 |  | Routine, Scheduled | 109-10-0153 | Bedford County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Central | WAUGH, IAIN C | 1942001512 | IAIN | WAUGH | 1.000000 | 1000 | Septic Tank Only | Puraflo | Pump | Distribution Box | Aggregate Trench | None |  | ["Attached Growth Medium","Effluent Screens"] | ["Attached Growth Medium","Effluent Screens"] | [18 empty] | [Comments]: Septic Tank minimal scum - 6" Sludge Pump Tank 6" Sludge Pump Functional, Both Alarm Functional Cleaned Effluent filter- not bad Turned peat in all pods- Ponds in pods 1 & 2 Pods 3 & 4 no water. Water drained after turning peat, peat in avg condition for age | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/24/2020 | 10:27 PM
10/01/2020 |  | RoutineScheduled | 033-17-0189-SP | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions | 2705163102 | Michele | Ware | 2.000000 |  | Norweco | [6 empty] | [] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 10/01/2020 | 12:00 AM
09/22/2020 |  | Routine/Scheduled | 2007-126-021 | Dinwiddie | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Crater | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. |  |  | Norweco Singulair ATU |  | Pump | Drip |  |  |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 09/22/2020 | Jan 1 1900 2:00AM
06/04/2020 |  | Routine, Scheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Biomicrobics MicroFAST |  |  |  |  | None |  | ["Blower/Compressor/Aerator Operation"] | ["Blower/Compressor/Aerator Operation"] |  | Good | Clear | [15 empty] | Pump Amps 11.54 ETM 28 h 43 m Cycles 545 Pump Amps 11.34 ETM 26 h 59 m Cycles 555 Septic Sludge " Scum 3" ATU Sludge 14" Scum 0 Pump Sludge 0 Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 06/04/2020 | Jan 1 1900 12:20PM
12/21/2020 |  | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 2705110225 | Larry | Royston | [9 empty] | ["Control Operation","Distribution Pump Operation","Disinfection","Dispersal System Operation"] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation"] | NA | [16 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12/21/2020 | 12:00 AM
08/11/2020 |  | RoutineScheduled |  | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Ashleys Septic Service | 1930332 | Shane | Majewski | 1.000000 | 1200 |  |  | Pump | Gravity | Pad | Not Applicable | 600.000000 | ["None"] | ["None"] | YES | [16 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 08/14/2020 | Jan 1 1900 12:00AM
07/08/2020 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump | Drip | Elevated Sand Mound | UV Light |  | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  | 2.52 | 7.830000 | 4.700000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 07/08/2020 | Jan 1 1900 1:15PM
07/11/2020 |  | RoutineScheduled | 18-113-093 | Buchanan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. |  | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Effluent Screens"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
02/19/2020 |  | Routine, Scheduled |  | Loudoun County | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Paid | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | None | Pump | Distribution Box | Aggregate Trench | [22 empty] | [Comments]: Pump tank needs pumped out. The have a lot of landscaping around them and the roots are getting into the pods. Landscaping needs removed and roots removed from pods | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 04/12/2020 | 02:21 PM
03/30/2020 |  | Routine, Scheduled |  | Fluvanna County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Blue Ridge | CLARK, MICHAEL J | 1934000023 | MICHAEL | CLARK |  |  | Septic Tank Only | Septic Tank Only | None | None | None | None |  |  | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/12/2020 | 04:46 AM
07/18/2020 |  | RoutineScheduled | 171-04-0431 | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | dovel enterprises |  | jerry | dovel | 1.000000 |  | 1000 |  | Pump |  | Drip |  |  | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
02/18/2020 |  | Routine, Scheduled | SWP-04-21 | Stafford County | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Puraflo | None | Pump | Distribution Box | Aggregate Trench |  |  | ["Effluent Screens","None","SludgeScum Accumulation"] | ["Disinfection","Effluent Screens","None"] | [18 empty] | [Comments]: The peat in the Puraflo mudules is saturated. Additionally, water is coming to the ground surface in the dispersal area. We recommend contacting an Alternative Onsite Soil Evaluator (AOSE) for repair or replacement options. We also recommend pumping the septic tank due to scum and sludge accumulation. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 03/02/2020 | 11:52 AM
04/01/2020 |  |  | 139-07-032 | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | SEAL’S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | tank only | PuraFlo | Gravity | Pressure | Trenches | Not Applicable |  | ["Attached Growth Medium","Septic Tank Baffles"] | ["Attached Growth Medium","Septic Tank Baffles"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 04/01/2020 | 12:00 AM
05/20/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/27/2021 | 01:26 PM
09/30/2020 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump | Drip | Elevated Sand Mound | UV Light |  | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  | 4.83 | 6.520000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 09/30/2020 | Jan 1 1900 10:00AM
06/10/2020 |  |  | 043-04-0144 | Clarke | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 2705110225 | Larry | Royston | [9 empty] | ["None"] | ["None"] | YES | [16 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 08/17/2020 | 12:00 AM
01/20/2020 |  | Routine, Scheduled | 02-195-150 SR | Washington County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Mount Rogers | DEEL, DENNY M | 1942001097 | DENNY | DEEL |  |  |  | None | Pump | Distribution Box | Aggregate Bed | None | 200.000000 | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation"] |  | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/05/2020 | Jan 1 1900 4:50PM
05/18/2020 |  | RoutineScheduled | 09-113-057 | Buchanan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | Septic Inc |  | Denny | Deel |  |  |  |  | Gravity | Gravity | Discharge | UV | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Level Sensor Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Level Sensor Operation"] | true | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
11/16/2020 |  | RoutineScheduled | 179-10-0086-SWP | Stafford | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Recirculation Pump" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Auxiliary Filter" ,"Attached Growth Medium" ,"Control Operation"] | ["Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Auxiliary Filter" ,"Attached Growth Medium" ,"Control Operation" ,"Dispersal System Operation"] | YES | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
04/29/2020 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Eco Virginia | 1942001235 | William | Poindexter | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 |  | 06/03/2021 | 05:53 AM
05/12/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/27/2021 | 01:26 PM
09/11/2020 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump | Drip | Elevated Sand Mound | UV Light |  | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  |  | 7.410000 | 5.000000 | [13 empty] | Replaced aerator and air sensor | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 09/11/2020 | Jan 1 1900 10:30AM
03/25/2020 |  | Routine, Scheduled | 181-01-0084 (LEGACY ALT. SYSTEM) | Rockbridge County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Central Shenandoah |  |  |  |  | 1.000000 | 1000 |  | Septic Tank Only | Pump | None | None | None |  | ["None"] | ["None"] | [18 empty] | [Comments]: Filters checked and cleaned. System did not need to be pumped. Control panel functioning properly. No apparent leaks in system or drain field area. Lid properly secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/30/2020 | 30-12-1899 05:38 PM
04/01/2020 |  | RoutineScheduled | 17-152-009 | Lee | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | Septic Inc |  | Denny | Deel |  |  | Clearstream |  | Gravity | Gravity |  | Not Applicable | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
02/17/2020 |  | Routine, Scheduled |  | Albemarle County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Blue Ridge | ARNOLD, ARCHIE G | 1942001291 | ARCHIE | ARNOLD | 1.000000 | 1000 | Aqua Safe ATU | Septic Tank Only | Pump | Drip | Drip Tubing | UV Light | 300.000000 | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] |  | Earthy | Clear | [15 empty] | [Comments]: O&M: Flushed drip lines, cleaned effluent filter, air filter,disk filter. Performed typical maintenance. System working as intended. 6" Sludge in septic tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/12/2020 | 03:42 PM
03/05/2020 |  | Routine, Scheduled | 04-142-0002 | Hanover County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chickahominy | Old Dominion Onsite, Inc. |  | Jason | Hackler | 1.000000 | 1500 | Orenco Advantex |  | Pump | Distribution Box | Aggregate Trench | None |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | [18 empty] | [Pumpout Comments]: Pumped out Septic tank and refilled. [Comments]: Septic tank pumped and refilled, Biotube filter and housing cleaned. Lift strut added to AX20 lid. Vent sock filter replaced. replaced silence button. Drainfield surface needs to be smoothed out to promote surface drainage. System appears to be functioning normally. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/05/2020 | Jan 1 1900 8:12AM
08/06/2020 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Gravity | Gravity |  | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Sale inspection on a conventional pump septic system. The control panel is a interior demand. There is 1 pvc cleanout. The pvc sewer line was camera snaked and was clear. The septic tank was buried 30" under the ground. The T's are pvc and saw no cracks or leaks in the tank. The pump tank, pump, floats and force main were inspected. The 10 port concrete d-box was at ground level. All 9 header lines were camera snaked and were clear. The drain field was probed and dry. At time of inspection all components inspected were in working condition. | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 |  | 04/14/2021 | 04:27 PM
07/10/2020 |  | RoutineScheduled | 13-163-0024 | New Kent | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chickahominy | Onsite Maintenance Team | 1942001039 | Corey | Braxton | 3.000000 |  | Clear stream N600 |  | Pump | Pressure | Drip |  | 350.000000 | ["BlowerCompressorAerator Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation","Effluent Screens"] | ["BlowerCompressorAerator Operation","Distribution Pump Operation","Level Sensor Operation","Effluent Screens"] | NA | Musty | Cloudy | 6.900000 | 3.000000 |  |  | turbidity 51 | [10 empty] | Blower was repaired | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 07/10/2020 | 12:00 AM
10/05/2020 |  | RoutineScheduled | 043-16-0175 | Clarke | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Greenway Engineering | 1942001008 | Jeremy | Ferguson | 1.000000 | 1500 | Microfast | none | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","SludgeScum Accumulation"] | NA | [17 empty] | Client will have ST pumped out in the spring time. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 10/05/2020 | 10:55 AM
05/18/2020 |  | RoutineScheduled |  | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 | Pending Payment | EHD - Rappahannock | WasteMaster, Inc. | 1942001062 | Tim | Jenkins |  |  | Puraflo | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Peat in good condition with no minor compaction to grid. no ponding. | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 |  | 06/21/2021 | 10:37 AM
12/31/2020 | Alternative | RoutineScheduled | 151-11-0091 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | KC Forge Environmental Service, LLC | 1942001034 | Kent | Cuthbertson |  |  |  |  | Pump | Gravity | Trenches | UV | 25780.000000 | [] | [] | YES | [15 empty] | Attached to this report |  | Due to reasons explained in the report attachment, TSS was exceeded twice during December but is being addressed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 02:00 PM
01/10/2020 |  | Routine, Scheduled | 03-125-154 | Dickenson County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Cumberland Plateau | DEEL, DENNY M | 1942001097 | DENNY | DEEL |  |  | Septic Tank Only | Septic Tank Only | None | None | None | None | [11 empty] | 03/17/2020 |  | 5.480000 |  |  | 1.400000 |  |  | Attached to this report |  | [Lab Comments]: 2020 YEARLY MONITORING RESULTS [Comments]: UPLOADING MONITORING ONLY VENIS File Names: MoscoeYates2020.pdf | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/27/2020 | Jan 1 1900 3:58PM
04/09/2020 |  | Routine, Scheduled |  | Prince William County | This AOSS should now return to normal function after having provided the above stated routine maintenance. | Paid | EHD - Prince William | SEAMON, CHARLIE L | 1942001108 | CHARLIE | SEAMON |  |  | Septic Tank Only | Microfast | Pump | Distribution Box | Aggregate Trench | None |  | ["BlowerCompressorAerator Operation","Level Sensor Operation"] | ["BlowerCompressorAerator Operation","Level Sensor Operation"] | [18 empty] | [Comments]: Performance Inspection:Microfast Pump to Drain- field. Septic-6"sludge 2"scum/ Microfast-4"sludge Pump tank-0"sludge. No pump out required. Blower air filter cleaned. Counts: Peak-0/High-6/Pump-247 ETM-20h 21m/ Run time changed to 6m 33s for 32 gpm rate and 210 dose. Repaired float bracket. | This AOSS should now return to normal function after having provided the above stated routine maintenance. |  | 04/14/2020 | 06:32 AM
07/23/2020 |  | Initial Visit | {FIPSCode}-STS-5761 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesapeake | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1500 | Orenco Advantex | None | Pump | Distribution Box | Aggregate Trench | None | 600.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | None | Clear | [15 empty] | Initial Visit - Real Estate inspection Processing Tank - normal operating level - RSV, Effluent screen & Recirc. pump serviced. AdvanTex Module - Media washed, spray grid serviced. Discharge tank - normal operating level - pump, float sensors and controls operating as designed. Distribution box located - balanced properly - four laterals accepting effluent. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 07/24/2020 | Jan 1 1900 7:30AM
10/27/2020 |  | Follow-Up |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | SES MidAtlantic LLC | 1942001203 | James | Green | 2.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium"] | ["Attached Growth Medium"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced peat in (7) modules. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/15/2021 | 09:00 AM
07/07/2020 |  | RoutineScheduled | 177-19-0099-SP | Spotsylvania | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | 90-DAY INSPECTION | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/09/2021 | 03:25 PM
07/21/2020 | Alternative | Reportable Incident | 119-STS-93597 | Middlesex | This AOSS should now return to normal function after having provided the above state routine maintenance | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | None | None | Gravity | Distribution Box | Aggregate Trench | None | 450.000000 |  | ["Dispersal System Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | [17 empty] | Pumped septic tank to facilitate repairs. Install - Repair Installed new 4" building sewer Installed new 1000g concrete septic tank Installed new 4" PVC conveyance line Installed new 8 port concrete distribution box Spliced to existing header lines | This AOSS should now return to normal function after having provided the above state routine maintenance |  | 08/07/2020 | 07:45 AM
06/29/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/27/2021 | 01:26 PM
03/18/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Puraflo |  | Pump |  |  | None |  | ["Effluent Screens"] | ["Effluent Screens"] |  | Good | [16 empty] | [Comments]: Puraflo peat is good.Pump 1 Amps 11.60 ETM 14988h Cycles 9787Pump 2 Amps 11.51 ETM 14980h Cycles 9757Septic Sludge 6" Scum 0Pump Sludge 1" Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/18/2020 | Jan 1 1900 11:40AM
12/31/2020 |  | RoutineScheduled | 139-06-358 | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | [6 empty] | Advantex |  | Pump | Pressure | Drip |  |  | ["Attached Growth Medium","Auxiliary Filter"] | ["Attached Growth Medium","Auxiliary Filter"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12/31/2020 | 12:00 AM
03/18/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Puraflo |  | Pump |  |  | None |  | ["Effluent Screens"] | ["Effluent Screens"] |  | Good | [16 empty] | [Comments]: Puraflo peat is good.Pump 1 Amps 13.33 ETM 17775h Cycles 22888Pump 2 Amps 13.40 ETM 18065h Cycles 21966Septic Sludge 7" Scum 1"Pump Sludge 1" Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/18/2020 | Jan 1 1900 10:40AM
12/08/2020 |  | RoutineScheduled |  | Warren | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NO | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/26/2021 | 09:04 AM
07/17/2020 |  | RoutineScheduled | 14-142-0330 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Old Dominion Onsite, Inc. | 1942001134 | John | Ewing | [9 empty] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump"] | NA | [17 empty] | Cleaned manifold and effluent filter, checked pump and float operation. System is functioning well. Noted a large amounts of solids accumulating in septic tank, recommend pumpout. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 07/17/2020 | Jan 1 1900 11:35AM
06/18/2020 |  | RoutineScheduled | 2006-143-0166 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Microfast |  |  |  | Drip |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 09/11/2020 | 12:00 AM
11/24/2020 |  | Reportable Incident | 175-11-0491 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green | [9 empty] | ["Distribution Pump Operation"] | ["Distribution Pump Operation"] | [18 empty] | Installed StaRite 1/2 hp 10 gpm/115v pump. | This AOSS should now return to normal function after having provided the above state routine maintenance |  | 11/24/2020 | 04:00 PM
09/29/2020 |  | Routine/Scheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | POWELLS PLUMBING, INC. | 1942001036 | Kurt | Holthaus | 1.000000 | 1000 | Puraflo |  | Pump | Distribution Box | Aggregate Trench |  | 450.000000 | ["Effluent Screens"] | ["Effluent Screens"] | N/A | [17 empty] | Annual Inspection - Serviced effluent screen(s). | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 09/30/2020 | 09:40 AM
06/26/2020 |  |  | 043-04-0095 | Clarke | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 2705110225 | Larry | Royston | [9 empty] | ["None"] | ["None"] | YES | [7 empty] | 06/26/2020 | Pump Chamber | [7 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 09/02/2020 | 12:00 AM
06/10/2020 |  | RoutineScheduled | {FIPSCode}-STS-1948 | Dickenson | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Control Operation","BlowerCompressorAerator Operation","Effluent Screens","Disinfection"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
04/10/2020 |  | Routine, Scheduled | C102-06-0086 | Alleghany County | This AOSS should now return to normal function after having provided the above stated routine maintenance. | Approved | EHD - Alleghany-Roanoke | AYRES, HUNTER E | 1942001166 | HUNTER | AYRES |  |  | Septic Tank Only | Septic Tank Only | None | None | None | None | [21 empty] | [Comments]: This property has not been occupied since last years inspection. No power hooked up to system. | This AOSS should now return to normal function after having provided the above stated routine maintenance. |  | 04/11/2020 | Jan 1 1900 8:47AM
02/12/2020 |  | Routine, Scheduled |  | Prince William County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Orenco Advantex |  | Pump | Drip | Drip Tubing | None |  | ["Effluent Screens"] | ["Effluent Screens"] |  | Good | Good | [15 empty] | [Comments]: Spin filter cleaned.Pump Amps 9.98 / 11.40Water Meter Reading 487600Septic Sludge 12" Scum 1"ATU Sludge 10" Scum 0Pump Sludge 6" Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/12/2020 | 06:00 PM
06/29/2020 |  | Routine, Scheduled | 175-11-0348 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green | [9 empty] | ["Effluent Screens"] | ["Effluent Screens"] | [18 empty] | Panel #1 Pump Amps 10.86 Pump Sludge 3" Scum 0 Panel #2 Pump Amps 8.44/5.46 Pump Sludge 1" Scum 0.25 Panel #3 Pump Amps 7.36 Pump Sludge 0 Scum 0 Panel #4 Pump Amps 8.87 Pump Sludge 0 Scum 0 Panel #5 LPD Pump Tank Pump Amps #1 37.17 Pump Amps #2 38.51 Pump Sludge 0 Scum 0 #1 Septic Sludge 4" Scum 0 #2 Septic Sludge 3" Scum 0 Grease Tank Sludge 3" Scum 0 Water Meter Reading 846800 Sample results sent to PWCHD | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 06/29/2020 | 10:30 AM
05/21/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Payment | EHD - Loudoun | Great Falls Septic Service, Inc | 1942001301 | Josh | Hott |  |  | Delta Environmental Products, UC Series | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/27/2021 | 11:51 AM
06/18/2020 |  | Initial Visit | 137-STS-22120 | Orange | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Start-Up Inspection. | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 |  | 04/09/2021 | 03:25 PM
09/11/2020 |  |  | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Fairfax | McKim Construction | 1942001330 | Michelle | McKim | 2.000000 |  |  |  | Gravity | Pressure | Drip | UV |  | ["Disinfection"] | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [17 empty] | UV light is bad | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. |  | 11/13/2020 | 12:00 AM
01/22/2020 |  | Routine, Scheduled |  | Dinwiddie County | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Paid | EHD - Crater | Madison Environmental LLC | 1934 000061 | Larry | Madison, Jr. |  |  | Clearstream ATU |  | Pump |  |  |  |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | [Comments]: UV controller needs replacement. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 01/22/2020 | Jan 1 1900 10:00AM
06/04/2020 |  | Routine/Scheduled | 17-174-0222 | Prince George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Crater | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. |  |  | Clearstream ATU |  | Pump |  |  |  |  | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 06/04/2020 | Jan 1 1900 9:45AM
03/07/2020 |  | Routine, Scheduled |  | Page County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Lord Fairfax | DOVEL, JERRY A | 1942001116 | JERRY | DOVEL | 1.000000 |  | Puraflo | Septic Tank Only | None | Distribution Box | None | None | [22 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/07/2020 | 07:44 PM
02/12/2020 |  | Routine, Scheduled |  | Albemarle County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Blue Ridge | Old Dominion Onsite, Inc. |  | Robert | Nicholas | [9 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump"] | [18 empty] | [Comments]: Cleaned effluent filter, flushed manifold. checked float and pump operation. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/12/2020 | 10:45 AM
06/09/2020 | Alternative | Routine/Scheduled | 136-18-0057 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | Biomicrobics MicroFAST |  | Pump | Distribution Box | Aggregate Trench | None | 600.000000 |  | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | Musty | Clear | [15 empty] | Routine service conducted. Primary Septic at normal operating level - 6" sludge present. Aeration operating properly - rotary compressor serviced. U.V. disinfection operating properly - serviced. Discharge pump and controls operating properly - pump serviced. Distribution box at normal operating level. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 06/10/2020 | 03:15 PM
05/06/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | SES MidAtlantic LLC | 1942001203 | James | Green | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/15/2021 | 09:00 AM
05/02/2020 |  | RoutineScheduled | 133 19 0068 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1000 | Advantex |  | Gravity | Gravity | Trenches |  |  | ["None"] | ["None"] | [18 empty] | 8" of solids in septic tank. Cleaned septic tank filter. Flushed treatment unit spray manifold. Tested floats, pump and alarm. Adjusted override cycle counts. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 09/18/2020 | 07:03 PM
12/02/2020 |  | RoutineScheduled | 2015-143-0015 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Clearstream | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 01/04/2021 | 12:00 AM
06/24/2020 |  | Routine/Scheduled | 19-120-0209AR | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesterfield | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | PremierTech, EFX |  | Pump | Distribution Box | Aggregate Trench |  | 600.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | Musty | Clear | [15 empty] | Routine service conducted. Septic tank in normal operating level - effluent screen serviced. EcoFlo module serviced - peatbiofilter raked Pump Basin intact - pump and float sensors functioning Distribution box intact and at normal operating level | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 06/25/2020 | Jan 1 1900 3:30PM
10/01/2020 |  | RoutineScheduled | 069120317 | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Combs Wastewater Management LLC | 1942001353 | Amy | Combs | 3.000000 | 1500 |  |  | Pump | Gravity | Drip | Not Applicable | 450.000000 | [] | ["Auxiliary Filter","Control Operation","BlowerCompressorAerator Operation","Distribution Pump Operation","Level Sensor Operation"] | YES | None | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12/28/2020 | 12:00 AM
02/25/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Paid | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Biomicrobics MicroFAST |  | Pump | Drip | Drip Tubing | UV Light |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] |  | Good | Clear | [15 empty] | [Comments]: D/F toe has standing water. ATU needs new lid.Spin filter cleaned.Pump Amps 8.05 ETM 207h 8m Cycles 1027Water Meter Reading 61500Septic Sludge 6" Scum 14"ATU Sludge 11" Scum 0Pump Sludge 1" Scum 0 | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 02/25/2020 | Jan 1 1900 1:02PM
10/06/2020 |  | Routine/Scheduled | 04-160-0233 | Montgomery | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Orenco Advantex |  | Gravity | Distribution Box | Aggregate Trench | None |  | ["None"] | ["Control Operation","Level Sensor (Float) Operation","Recirculation Pump","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | [18 empty] | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 10/06/2020 | 07:00 PM
08/05/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Hydro-Action ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/27/2021 | 01:26 PM
04/29/2020 |  | RoutineScheduled | 2005-143-0186 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Puraflo |  |  |  | Pad |  |  | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
06/09/2020 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump | Drip | Elevated Sand Mound | UV Light |  | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  |  | 7.000000 | 5.000000 | [13 empty] | Replaced UV Bulb | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 06/09/2020 | Jan 1 1900 11:00AM
03/25/2020 |  | Routine, Scheduled |  | Loudoun County | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Paid | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | None | None | Pump | Distribution Box | Aggregate Trench | [22 empty] | [Comments]: septic tank needs pumped out | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 04/12/2020 | 02:21 PM
12/09/2020 | Alternative | Routine/Scheduled | 157-10-0105 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | Serviced system. Checked the pump, panel, & floats (ok). Changed the diffuser in the Clearstream, changed the filter in the aerator, and changed the mesh screen in the spinfilter. Could not locate the vacuum breakers. The timer is set to 8 minutes every 1 hour. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12/09/2020 | 12:00 PM
01/16/2020 |  | Follow-Up |  | Culpeper County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 2.000000 |  | None | None | Pump |  |  | UV Light | [21 empty] | [Comments]: Influent sample results came back at 277 mg/L for BOD5 and 101 mg/L for TSS. Manager said effluent in discharge tank already looks much better. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/03/2020 | 05:52 AM
10/23/2020 |  | RoutineScheduled |  | Augusta | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter"] | ["Control Operation" ,"Auxiliary Filter"] | NA | [7 empty] | 10/23/2020 |  | 168.000000 | [5 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/26/2021 | 09:04 AM
09/14/2020 |  | Routine/Scheduled | 2005-143-0222 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Old Dominion Onsite, Inc. | 1942001134 | John | Ewing | 1.000000 | 1000 | Clearstream |  | Pump | Distribution Box | Aggregate Trench | None | 200.000000 | ["Blower/Compressor/Aerator Operation","Control Operation","Effluent Screens","Level Sensor (Float) Operation"] | ["Blower/Compressor/Aerator Operation","Disinfection","Effluent Screens","Level Sensor (Float) Operation"] | N/A | [17 empty] | Compressor Filter was changed. Alarm floats were checked and audible alarm worked correctly. Compressor alarm was tested and worked correctly. Recommend pumping out treatment tank at next pump out. Counters: Event = 58937 Time = 296.42 hours | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 09/14/2020 | 10:14 AM
07/28/2020 |  | RoutineScheduled | 099-19-0027 SP | King George | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | 90-Day Inspection | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 |  | 04/09/2021 | 03:25 PM
06/23/2020 |  | Routine, Scheduled | 175-18-0488 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | EZ Treat Sandfilter |  |  |  |  | UV Light |  | ["Blower/Compressor/Aerator Operation","Disinfection","Effluent Screens"] | ["Blower/Compressor/Aerator Operation","Disinfection","Effluent Screens"] |  | Good | Clear | [5 empty] | 06/23/2020 | Discharge | 9.000000 |  | 3.000000 | 30.000000 |  |  |  |  | Pump 1 ETM 298 hrs 09 mins Cycles 35529 Pump 2 ETM 13 hrs 45 mins Cycles 1452 Septic Sludge 3" Scum 1" ATU Sludge 3" Scum 0 Pump Sludge 3" Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 06/23/2020 | 02:48 PM
01/30/2020 |  | Routine, Scheduled | 08-120-0485A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesterfield | Madison Environmental LLC |  | Larry | Madison, Jr. |  |  | Hoot |  | Pump |  |  |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | [Comments]: Rebuilt blower Lab results not reported by Operator, EHS chose "No" in order to allow saving updated entry. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/30/2020 | Jan 1 1900 11:00AM
03/17/2020 |  | Routine, Scheduled | 179-18-0445-SP | Stafford County | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Norweco Singulair ATU | None | Gravity | Distribution Box | Aggregate Trench |  |  | ["Dispersal System Operation"] | [19 empty] | [Comments]: 90-Day InspectionCable was trenched through drainfield. Builder has been advised. We recommend contacting the system design for further evaluation. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 04/06/2020 | 02:46 PM
08/17/2020 |  | Reportable Incident |  | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [9 empty] | ["Blower/Compressor/Aerator Operation","Control Operation"] | ["Blower/Compressor/Aerator Operation","Control Operation"] | N/A | [17 empty] | Replaced aerator | This AOSS should now return to normal function after having provided the above state routine maintenance |  | 08/17/2020 | Jan 1 1900 1:15PM
09/01/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Septic tank riser to be installed. DF in open space/common area. Recommmend mowing twice a year min. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/27/2021 | 01:26 PM
09/16/2020 |  | Routine, Scheduled | 175-04-0420 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Delta Environmental Products, DF Series |  |  |  |  | None |  | ["Blower/Compressor/Aerator Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation"] |  | Good | Clear | [15 empty] | Spin filter cleaned. Pump Amps 11.95 ETM 6019 hrs Cycles 38217 Water Meter Reading 2302500 Septic Sludge 10" Scum 1" ATU Sludge 5" Scum 8" Pump Sludge 3" Scum 0 Delta ATU needs pumping. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 09/16/2020 | 09:47 AM
06/10/2020 |  | Routine, Scheduled | 061-16-408 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Biomicrobics Retrofast |  |  |  |  | None |  | ["Blower/Compressor/Aerator Operation"] | ["Blower/Compressor/Aerator Operation"] |  | Good | Clear | [15 empty] | Pump Amps 6.47 ETM 9254 Cycles 1257 Septic Sludge 12" Scum 4" ATU Sludge 13" Scum 0 Pump Sludge 0 Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 06/10/2020 | 12:13 PM
11/20/2020 |  | Reportable Incident | 043180106 | Clarke | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Lord Fairfax | POWELLS PLUMBING, INC. | 1942001036 | Kurt | Holthaus |  |  | Multiflo FTB | [6 empty] | ["Distribution Pump Operation","Sludge/Scum Accumulation"] | ["Distribution Pump Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | Replaced sewer pump under warranty, pumped septic tank and pump chamber. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12/31/2020 | 01:17 PM
09/01/2020 |  | RoutineScheduled | 177-STS-87158 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 |  | 04/09/2021 | 03:25 PM
10/22/2020 |  | RoutineScheduled | 145-97-0072 (LEGACY ALT. SYSTEM) | Highland | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 2.000000 | 2000 | SEPTIC TANK ONLY | SANDFILTER, RECIRCULATING | Pump | Pressure | Trenches | Not Applicable |  | ["Control Operation","Level Sensor Operation"] | ["None"] | NO | [7 empty] | 10/22/2020 |  | 8.000000 | [5 empty] | Attached to this report |  | SYSTEM DID NOT NEED TO BE PUMPED; DUE TO HIGH WINDS A TREE LIMB FELL ON THE PUMP CONTROL PANEL AND REQUIRES REPLACEMENT. THIS CAMP IS SEASONAL AND WILL BE SHUT DOWN DURING THE WINTER MONTHS; DUE TO LIMITED FUNDS CAUSED BY COVID-19, CAMP PLANS TO COMPLETE REPLACMENT OF PUMP PANEL IN THE SPRING PRIOR TO RE-OPENING. LIDS SECURE. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. |  |  | 07:50 PM
08/21/2020 | Alternative | Routine/Scheduled | 157-10-0140 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | Serviced system. Checked the pump, panel, & floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 08/21/2020 | 12:00 PM
08/14/2020 |  | Routine, Scheduled | 175-02-0079 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Orenco Advantex |  |  |  |  | None |  | ["Effluent Screens","Recirculation Pump"] | ["Effluent Screens","Recirculation Pump"] |  | Good | Good | [15 empty] | Pump Amps 11.88 ETM 356741 mins Cycles 842435 Pump Amps 8.90 ETM 13910 mins Cycles 6929 Septic Sludge 11" Scum 1" Pump Sludge 2" Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 08/14/2020 | 05:02 PM
06/05/2020 |  | Routine/Scheduled | 07-118-0039 | Charles City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chickahominy | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1500 | Orenco Advantex | None | Pump | Distribution Box | Aggregate Trench | None |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 06/29/2020 | Jan 1 1900 4:54PM
09/24/2020 | Alternative | Routine/Scheduled | 151-02-0120 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 2.000000 | 2250 | None |  | Pump | Distribution Box | Aggregate Bed |  |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump","Septic Tank Baffles","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 09/24/2020 | 05:00 PM
05/22/2020 | Alternative | RoutineScheduled | 115-12-0078 | Campbell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Taylor's Septic Service | 1942001028 | Penny | Taylor | 1.000000 | 1000 | Septic Tank | Advantex | Pump | Gravity | Trenches | Not Applicable | 350.000000 | ["Control Operation","Effluent Screens","SludgeScum Accumulation"] | ["Control Operation","Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [14 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 05/22/2020 | 09:00 AM
02/24/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Fairfax | Hott, Joshua D. | 1942001301 | Joshua | Hott |  | 1875 | Septic Tank Only | Septic Tank Only | None | None | None | None |  | ["Effluent Screens"] | ["Effluent Screens"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/02/2020 | Jan 1 1900 3:51PM
09/24/2020 |  | RoutineScheduled | 162-14-0062 | Nelson | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Taylor's Septic Service, Inc | 1942001028 | Penny | Taylor | 1.000000 | 1000 | septic | ecopod | Gravity | Gravity | Trenches | Not Applicable | 350.000000 | ["Effluent Screens"] | ["Effluent Screens","SludgeScum Accumulation"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 09/24/2020 | 01:00 PM
08/11/2020 |  | RoutineScheduled | 182-05-0053 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Central Shenandoah | Onsite Wastewater Services - May Supply | 1942001627 | Drew | Shull | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | INSPECTED ON 8/11/2020 BY DKS. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 06/09/2022 | 04:10 PM
08/12/2020 |  | RoutineScheduled | 175-14-0221 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Prince William | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  | ["Auxiliary Filter" ,"SludgeScum Accumulation"] | ["Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | Effluent level higher than last year so that recirc trough is always under water, even when blower is turned off. Media is plugged and needs to be cleaned. Tank will need pumped which will take care of 5-year pump-out requirement. Collected effluent sample for 5-year BOD test. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
06/01/2020 |  | RoutineScheduled | 033-STS-86800 | Caroline | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/09/2021 | 03:25 PM
02/26/2020 |  | Routine, Scheduled | {FIPSCode}-STS-2863 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesapeake | R & K Septic, Inc. |  | Craig | Van Holten |  |  | Clearstream ATU |  | Gravity | Distribution Box |  | None |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] |  |  |  | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/26/2020 | Jan 1 1900 11:30AM
12/15/2020 |  | Routine/Scheduled | 06-174-0022 | Prince George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Crater | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1500 | Norweco Singulair ATU |  | Pump | Drip | Drip Tubing | None | 450.000000 |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | Musty | Clear | [15 empty] | Routine Service Trash Tank - normal operating level Aeration Tank - normal level - aspirator serviced. Clarifier - normal level - effluent screen serviced. Pump Tank - Normal level - pump, float sensors & controls operating. Drip Headworks - drip field flushed - drip screen serviced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 12/16/2020 | Jan 1 1900 12:00PM
07/10/2020 |  | Routine/Scheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | POWELLS PLUMBING, INC. | 1942001036 | Kurt | Holthaus | 1.000000 | 1000 |  |  | Pump | Manifold | Aggregate Trench |  | 450.000000 | ["None"] | ["None"] | N/A | [17 empty] | Annual Inspection - No repairs or service needed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 07/17/2020 | 01:18 PM
10/06/2020 |  | RoutineScheduled | 175-02-0748 | Prince William | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["SludgeScum Accumulation"] |  | NA | [15 empty] | Will be sent separately | Inspected | We recommend pumping both sides of the Advantex Tank due to scum & sludge accumulation. We also recommend replacing two Orenco riser lids and the Advantex module vent cap. The pump line in the Pump Tank shows signs it has leaked where the pipe exits the tank. We recommend excavating by machine and resealing the outlet. The splitter & distribution boxes were inspected and roots removed from the top 2 boxes. We recommend excavating by hand and removing roots from the pipe feeding the lower distribution box. We also recommend rebuilding the concrete dams in the splitter box. | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 |  | 04/09/2021 | 03:25 PM
12/28/2020 |  | RoutineScheduled | SD-09-006 | Orange | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Distribution Pump Operation" ,"Level Sensor Operation" ,"Auxiliary Filter" ,"Control Operation" ,"Recirculation Pump"] | ["Auxiliary Filter" ,"Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"Recirculation Pump"] | NA | [15 empty] | Will be sent separately | Inspected | Routine inspection. In the past 30 days, the system averaged 10.3 drip cycles at 6.7 min/cycle (max cycles/day 12). | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
03/03/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green |  |  |  |  | Pump | Manifold | Aggregate Trench | None |  | ["Control Operation","Effluent Screens"] | ["Control Operation","Effluent Screens"] | [18 empty] | [Comments]: Pump Amps 20.55/13.34Septic Sludge 4" Scum 1"Pump Sludge 0 Scum 0Concrete lid needs replacement. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/03/2020 | Jan 1 1900 12:45PM
10/08/2020 | Alternative | RoutineScheduled | 124-STS-2379 | Richmond City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Three Rivers | Lyttle Service Co., LLC dba Stamie E. Lyttle Co | 1942001332 | Benjamin | Chapin | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
12/28/2020 |  | RoutineScheduled | 182-03-0360 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | Musty | Clear | 6.700000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 01/12/2021 | 11:50 AM
01/24/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Fairfax | BLEVINS, JOEL R, SR | 1934000415 | JOEL | BLEVINS |  |  | Microfast | Septic Tank Only | None | None | None | None |  | ["None"] | ["None"] | [18 empty] | [Comments]: Compressor is strong and the ditches are dry. Cleaned the air filter. There is 16" of sludge in the treatment tank. Recommend pumping it. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/03/2020 | Jan 1 1900 12:42PM
05/05/2020 |  | Follow-Up | 033-13-0022-SP | Caroline | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | EcoPod | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | ["Distribution Pump Operation" ,"Control Operation" ,"Level Sensor Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Both tanks pumped out today. Pumper said tanks were full to the lids. Found panel not completing cycles again. Also observed inputs showing for zone 2 and cycle start function. Discussed with tech support at American Mfg. Disconnected and capped off input wire for zone 2 (there is only 1 zone for this system). Replaced the reset/cycle start switch. Also replaced the bulbs for the high level alarm on drip panel and pressure alarm on the blower panel. Blower is making a raspy bearing noise, may not last long. Infiltration occurring at buried septic inlet lid - needs additional 12" riser. Infiltration also observed at broken atu vent pipe, outlet riser joint (septic), and screw holes in pump tank riser for float tree bracket and cool guide pipe. Replaced timer float switch that was stuck on. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
06/15/2020 |  | RoutineScheduled | 136-17-0340 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers |  |  | joel | pinnix | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
03/07/2020 |  | Routine, Scheduled |  | Page County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Lord Fairfax | DOVEL, JERRY A | 1942001116 | JERRY | DOVEL | 1.000000 |  | Biomicrobics MicroFAST | Septic Tank Only | None | Drip | None | None | [22 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/07/2020 | 07:25 PM
11/04/2020 |  | Routine/Scheduled | 136-93-0576 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | None | None | Pump | Manifold | Aggregate Trench | None | 450.000000 |  | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | [17 empty] | Routine service Primary septic tank - normal operating level Pump tank - normal operating level - pump, float sensors, controls operating properly. LPP Manifold located - valve exercised - no indications of surfacing. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 11/06/2020 | 10:30 AM
04/02/2020 |  | Follow-Up | 179-06-0107-SP | Stafford County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 2.000000 |  | Biomicrobics MicroFAST | None | Pump |  |  |  |  | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | [Comments]: Cleaned media, replaced air lift, extended inspection port above grade, and pumped out all tanks. Repaired drip breaks in tubing, added spring check valve to drip flush line, and replaced pressure gauge on supply line (in headworks) with backmount style for easier viewing. Installed proper float tree in pump tank. Flushed tubing, tested drip rate and adjusted run/rest times in control panel. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/27/2020 | 07:57 AM
05/29/2020 | Alternative | Routine/Scheduled | 103-STS-93075 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | Ecoflo | None | Pump | Distribution Box | Aggregate Trench | None |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | The outdated Filter in the Septic Tank was found 90% clogged (we recommend its replacement during your next scheduled pumping service), and the Riser had dirt/water leaking; the Pump and Floats in the Discharge Tank are near/past their expected life, the Cords for the Pump and Floats are not properly sealed, the Disconnect had dirt infiltration, and the Alarm Box was quiet (but still operational); | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 06/09/2020 | 04:09 PM
03/10/2020 |  | Routine, Scheduled |  | Albemarle County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Blue Ridge | CLARK, MICHAEL J | 1934000023 | MICHAEL | CLARK |  |  | Septic Tank Only | Septic Tank Only | None | None | None | None |  |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/17/2020 | 04:41 AM
02/06/2020 |  | Routine, Scheduled |  | Loudoun County | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Paid | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | None | Pump | Distribution Box | Aggregate Trench | [22 empty] | [Comments]: Pump tank needs pumped out | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 03/02/2020 | 04:43 AM
07/30/2020 | Alternative | RoutineScheduled | 128-08-070 | Essex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers |  |  | joel | pinnix | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
10/13/2020 |  | RoutineScheduled |  | Augusta | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Pressure | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | Recommended installation of riser on tank and also upgraded timer | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/26/2021 | 09:04 AM
11/03/2020 | Alternative | RoutineScheduled | 171-05-819 | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | None | Clear | 7.820000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 11/11/2020 | 02:30 PM
12/04/2020 | Alternative | Routine/Scheduled | 151-16-0016 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 2.000000 | 2500 | Microfast |  | Pump | Distribution Box | Aggregate Trench |  |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12/04/2020 | 05:00 PM
10/05/2020 |  | RoutineScheduled | SWP-03-45 | Stafford | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | ["Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Infiltration observed at septic tank wedge lid. Wet rust stains at inlet/ outlet pipe penetrations in pump tank suggest additional points of groundwater infiltration. Pump was not installed to allow for pump removal without entering tank. Pump disconnect (union) binds when loosened. Recommend replumb discharge piping in tank to correct for settling and allow for proper servicing. Cycle counter in control panel has seized, needs replaced. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
02/05/2020 |  | Reportable Incident | 234-16-307 | Chesapeake | This AOSS should now return to normal function after having provided the above stated routine maintenance. | Approved | EHD - Chesapeake | R & K Septic, Inc. |  | Craig | Van Holten |  |  | Clearstream ATU |  | Pump |  |  |  |  | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | [18 empty] | [Comments]: Replaced aerator | This AOSS should now return to normal function after having provided the above stated routine maintenance. |  | 02/05/2020 | Jan 1 1900 11:30AM
07/31/2020 |  | Routine/Scheduled | 11-137-0112 | Goochland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chickahominy | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. |  |  | Norweco Singulair ATU |  | Gravity |  |  |  |  | ["Blower/Compressor/Aerator Operation","Control Operation","Effluent Screens","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Effluent Screens","Sludge/Scum Accumulation"] | N/A | [17 empty] | Replaced norweco panel | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 07/31/2020 | Jan 1 1900 10:30AM
04/21/2020 |  | Routine/Scheduled | 147-06-0040 | James City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Peninsula | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1500 | Orenco Advantex | None | Pump | Drip | Drip Tubing | None |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | [17 empty] | Discharge Riser was leaking, there was root intrusion around the Inlet Tee as well as underneath the leaking Riser; the Gauge for the Return Line was not functioning, and there were signs of surfacing across the entire Drip Field | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/23/2020 | Jan 1 1900 4:52PM
02/05/2020 |  | Routine, Scheduled |  | Middlesex County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Three Rivers | LANGFORD, CHARLES T | 1934000143 | CHARLES | LANGFORD | 1.000000 | 1000 | Ecoflo | Septic Tank Only | Pump | None | Aggregate Bed | None |  | ["Effluent Screens"] | ["Effluent Screens"] | [18 empty] | [Comments]: UNSTOP TEE IN TANK MINOR CRACK STILL IN ECOFLO | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/02/2020 | 10:17 AM
11/13/2020 |  | RoutineScheduled | 05-197-A5 | Wise | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | Wise County Health Dept |  | Rodney | Neece | 1.000000 |  | Jet |  | Gravity | Gravity | Discharge | Chlorination |  | ["BlowerCompressorAerator Operation"] |  |  | None | Clear | 6.200000 | 1.000000 |  | 0.000000 | aerator is running but 1 DO | [11 empty] | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 11/13/2020 | 12:00 AM
12/30/2020 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Joe Blevins Equipment Rental, Inc | 2705013926 | Joel | Blevins | 2.000000 |  | Microfast |  | Pump | Gravity | Trenches | Not Applicable |  | ["None"] | ["None"] | NA | Musty | Cloudy | [15 empty] | Ditches were dry and cleaned the air filter. There was 8 inches of sludge in treatment tank. Good for another year. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12/31/2020 | 12:00 AM
11/16/2020 |  | RoutineScheduled |  | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001301 | Joshua | Hott | [9 empty] | [] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
01/20/2020 |  | Routine, Scheduled | 18-137-0255 | Goochland County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chickahominy | Old Dominion Onsite, Inc. |  | John | Ewing | 1.000000 | 1000 | Aerotech |  | Pump | Distribution Box | Elevated Sand Mound |  | 160.000000 | [12 empty] | 70.000000 | [7 empty] | [Comments]: Sample taken for BOD5 testingSystem is a Purasys with GeoMat dispersal. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/20/2020 | Jan 1 1900 2:44PM
04/14/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | SES MidAtlantic LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. Inlet tee on septic tank missing. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/15/2021 | 09:00 AM
03/10/2020 |  | Routine, Scheduled | 177-15-0123-SWP | Spotsylvania County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | None | Pump | Distribution Box | Aggregate Trench |  |  | ["Attached Growth Medium","None","Recirculation Pump"] | ["Attached Growth Medium","None","Recirculation Pump"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/06/2020 | 02:45 PM
07/08/2020 | Alternative | RoutineScheduled | 149-10-024 | King & Queen | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Church View Septic Service Inc. | 1942001302 | Charles | Langford | [9 empty] | ["Effluent Screens"] | ["Effluent Screens"] | YES | [16 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
03/12/2020 |  | Reportable Incident | 177-STS-92606 | Spotsylvania County | This AOSS should now return to normal function after having provided the above stated routine maintenance. | Approved | EHD - Rappahannock | SES Mid Atlantic | 1942001203 | Michael | Green | [9 empty] | ["Dispersal System Operation"] | ["Dispersal System Operation"] | [18 empty] | [Comments]: Repaired broken pipe in drainfield. | This AOSS should now return to normal function after having provided the above stated routine maintenance. |  | 03/12/2020 | 04:00 PM
03/04/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Fairfax | SEAMON, CHARLIE L | 1942001108 | CHARLIE | SEAMON |  |  | Septic Tank Only | Microfast | Pump | Manifold | Drip Tubing | UV Light |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | [8 empty] | 03/04/2020 |  | 58.000000 |  | 17.000000 |  |  |  | Attached to this report |  | [Comments]: Performance Inspection and Samples Microfast to American Drip. Septic-4"sludge 4"scum/ Microfast-0"sludge/Pump Tank-0"sludge. No pump out needed at this time.Z1 cnts-282 ff-10/Z2 cnts-279 ff-10/Pump Cnts-581 ETM-140h 32m/Peak cnts-8 ETM-56h 9m/High cnts-20 ETM-0/Watermeter-25946.78/ Drip rates 2.9 No breakout or spongy areas on the drip field. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/23/2020 | Jan 1 1900 6:51AM
08/31/2020 | Alternative | RoutineScheduled | 171-18-108 | Shenandoah | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Lord Fairfax | Onsite Wastewater Services - May Supply | 1942001022 | Sara | Tusing | 1.000000 |  | Orenco Advantex | none | Pump | Pressure | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Inspection DKS | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/28/2021 | 05:41 AM
02/14/2020 |  | Initial Visit | 234-19-115 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesapeake | Farmer's Septic Service, Inc. |  | Emily | Brady | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [10 empty] | 5.000000 |  | 2.000000 | [5 empty] | [Comments]: Serviced system. Checked the pump, panel, & floats (ok). Cleaned the filter in the Clearstream and cleaned the UV light bulb. Changed the diffuser in the Clearstream, changed the filter in the aerator, and installed an orifice in the return line. The septic tank needs additional risers on it so it can be properly inspected in the future. The timer is set to 2.75 minutes every 2 hours. Took initial BOD & Fecal samples. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/14/2020 | Jan 1 1900 12:00PM
09/04/2020 |  | Initial Visit | 136-07-0293 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | Clearstream | None | Pump | Distribution Box | Aggregate Trench | None | 450.000000 |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | Musty | Clear | [15 empty] | Initial Visit - ALARM event Primary septic tank at normal operating level - effluent screen serviced. Processing tank - normal operating level - compressor operational - NOTE original rotary - may be replaced when failed with HiBlow 60/80 Discharge tank - high level - float sensor failure - All float sensors replaced - discharge pump serviced - controls operating properly. Distribution box - Plastic - intact - all laterals accepting effluent. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 09/08/2020 | 07:45 AM
11/02/2020 |  |  | 11-183-190 | Russell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 11/02/2020 |  | 12.900000 |  |  | 4.600000 |  |  | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 11/02/2020 | 12:00 AM
12/17/2020 | Alternative | Routine/Scheduled | 151-04-043 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 2.000000 | 2500 | Microfast |  | Pump | Manifold | Aggregate Trench |  |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Septic Tank Baffles"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12/17/2020 | 05:00 PM
11/02/2020 |  | Routine/Scheduled |  | Richmond City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Richmond | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 2.000000 | 2000 | Puraflo |  | Pump | Manifold | Aggregate Bed |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 11/02/2020 | Jan 1 1900 1:00PM
07/07/2020 |  | RoutineScheduled | 109-05-0879 | Bedford | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Advantex AX20 |  | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | NA | [16 empty] | Inspected | System was pumped, Replaced Pump and 3 floats on June 10th, Returned 7-720 with new RSV to replace old one which had broken. System was pumped by foutz after initial repairs. System now operational. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 07/28/2020 | 12:30 PM
04/23/2020 |  | Routine/Scheduled | 228-05-0144 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Virginia Beach | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1500 | Orenco Advantex | None | Pump | Distribution Box | Aggregate Trench | None |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | [17 empty] | The Advantex Media Unit Lid did not have support Struts present; | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/27/2020 | Jan 1 1900 11:45AM
12/15/2020 |  | Initial Visit | 069-19-0122 | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Combs Wastewater Management LLC | 1942001353 | Amy | Combs | 2.000000 | 1000 |  |  | Pump | Gravity | Drip | Not Applicable | 600.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Effluent Screens","Septic Tank Baffles","SludgeScum Accumulation"] | YES | None | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12/18/2020 | 12:00 AM
10/16/2020 |  |  |  | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001301 | Joshua | Hott | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
11/02/2020 |  | Routine/Scheduled |  | Richmond City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Richmond | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 2.000000 | 2000 | Sandfilter, Recirculating |  | Pump | Distribution Box | Aggregate Trench |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 11/02/2020 | Jan 1 1900 1:00PM
07/11/2020 |  | RoutineScheduled | 109-04-0018 | Bedford | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1000 | Multiflo ATU |  | Pump | Pressure | Drip | Not Applicable |  | [] | [] | NA | [16 empty] | Inspected | On June 26th initial visit. Pump Tank sludge level 1-2" scum and 12" light sludge, Treatment unit- if fine, aspirator pump and sludge levels ok. Repaired Broken leaking valve body in headworks box, and multiple leaks in drainfield. Circuit board replaced 7-11-20, repaired 2 more leaks, replaced riser around air relief valves. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 07/28/2020 | 12:30 PM
06/25/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | SES MidAtlantic LLC | 1942001203 | James | Green | 1.000000 |  | Clearstream | none | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/15/2021 | 09:00 AM
04/28/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/14/2021 | 04:27 PM
02/25/2020 |  | Follow-Up |  | Loudoun County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | None | Pump | Distribution Box | [24 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/12/2020 | 02:21 PM
02/11/2020 |  | Routine, Scheduled |  | Loudoun County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | None | Pump | Distribution Box | Aggregate Trench | [22 empty] | [Comments]: Sale inspection on a alternative septic system. There are two exterior septic control panels one a time dose and the other a demand dose. There are 2 pvc cleanouts. The sewer line was camera snaked and all was clear. The septic tank has a plastic riser on the outlet side of the tank. There is also a filter that was cleaned when we pumped out the septic tank. Manufacture recommends the filter be cleaned every 6 months. The first pump tank has a concrete riser on the outlet side of the tank. The tank, pump, floats and force main were inspected. The 5 purflo pods were opened up and are in good condition. The second pump tank, pump, floats and force main were inspected. The 8 port concrete d-box was dug up it was 18" under the ground and the header lines were camera snaked. the drain field was probed and was dry. At time of inspection all components were in working condition. This is a Alternative septic system that by state law is required to be inspected every year and filed with the state and county. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/02/2020 | 04:43 AM
12/21/2020 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump | Drip | Elevated Sand Mound | UV Light |  | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  | 4.26 | 7.750000 | 8.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 12/21/2020 | Jan 1 1900 10:00AM
09/17/2020 |  | RoutineScheduled | 177-10-0019-SP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | EcoPod | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Attached Growth Medium" ,"Level Sensor Operation" ,"SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation" ,"Attached Growth Medium" ,"Level Sensor Operation"] | NA | [15 empty] | Will be sent separately | Inspected | We recommend pumping the Aerobic Treatment Unit due to solids accumulation. It may be advisable to pump the Septic Tank at the same time We also recommend mowing the dispersal area and maintaining in a mowed condition. | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 |  | 04/09/2021 | 03:25 PM
08/06/2020 |  | Routine/Scheduled | 234-18-082 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | Serviced system. Checked the pump, panel, & floats (ok). Cleaned the filter in the Clearstream and cleaned the UV light bulb. Changed the diffuser in the Clearstream, changed the filter in the aerator, and changed the disc filter. The septic tank needs additional risers on it so it can be properly inspected in the future. The timer was set at 8 minutes every 2 hours changed to 10 minutes every 2 hours. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 08/06/2020 | Jan 1 1900 12:00PM
01/21/2020 |  | Routine, Scheduled | S-175-14-0082 | Southampton County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Western Tidewater | R & K Septic, Inc. |  | John | Butt, Jr |  |  | Clearstream ATU |  | Pump | Distribution Box | Gravel-Less Trench | None |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] |  |  | 5.1 | 7.680000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/21/2020 | Jan 1 1900 12:30PM
06/18/2020 |  | RoutineScheduled | SP-03-253 | Caroline | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["SludgeScum Accumulation"] |  | NA | [15 empty] | Will be sent separately | Inspected | Roots are growing inthe Puraflo modules. There is a hole in one Puraflo module lid. We recommend replacing this lid. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/09/2021 | 03:25 PM
06/12/2020 |  | RoutineScheduled | 061-17-135 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | Ace Contracting Services Inc | 1942001120 | Lawrence | Fellenz Jr. |  |  | Puraflo | Puraflo | Gravity | Gravity |  | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 |  | 06/29/2021 | 10:39 PM
08/26/2020 |  | Reportable Incident | 175-17-0488 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green | [9 empty] | ["Level Sensor (Float) Operation"] | ["Level Sensor (Float) Operation"] | [18 empty] | Replaced low water float under warranty. | This AOSS should now return to normal function after having provided the above state routine maintenance |  | 08/26/2020 | 01:30 PM
07/28/2020 |  | RoutineScheduled | SP-03-40 | King George | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Attached Growth Medium"] | ["Effluent Screens" ,"Attached Growth Medium"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 |  | 04/09/2021 | 03:25 PM
06/14/2020 |  | RoutineScheduled | -STS-43154 | Alleghany | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Alleghany-Roanoke | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1500 | ORENCO ADVANTEX AX20 |  | Pump | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","Control Operation","Level Sensor Operation","Effluent Screens"] | ["Auxiliary Filter","Control Operation","Level Sensor Operation","Effluent Screens"] | YES | [17 empty] | SYSTEM DID NOT REQUIRE PUMPING, REMOVE AND INSTALL NEW WIRING TO RECIRCULATING TANK AND DISCHARGE TANK DUE TO BROKEN CONDUIT AND WIRE, NO VISIBLE LEAKS IN DRIP FIELD, UPON REPAIR SYSTEM FUNCTIONING AS DESIGNED, LIDS SECURED | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 06/14/2020 | Jan 1 1900 1:20PM
01/22/2020 |  | Routine, Scheduled | SD-04-190 | Culpeper County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | Brown, Jason W | 1942001049 | Jason | Brown | 1.000000 | 1000 | Septic Tank Only | Biomicrobics MicroFAST | Gravity | None | Alternative Discharge | Chlorine |  |  |  |  | Musty/earthy | Clean | [15 empty] | VENIS File Names: O&M Log Jan 2020.odt | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/26/2020 | 10:36 AM
08/05/2020 |  | RoutineScheduled | 133 08 0030 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | Western Virginia Water Authority | 1942001145 | Michael | Doss |  |  |  |  | Pump | Pressure | Drip | UV |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [5 empty] | 08/05/2020 | Sample Chamber | [6 empty] | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 09/14/2020 | 08:00 AM
06/12/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim |  |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/14/2021 | 04:27 PM
02/13/2020 |  | Routine, Scheduled |  | Frederick County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Lord Fairfax | POWELLS PLUMBING, INC. | 1942001036 | Kurt | Holthaus | 1.000000 | 1250 | Puraflo |  | Pump | Distribution Box | Aggregate Trench |  | 600.000000 | ["Effluent Screens","SludgeScum Accumulation"] | ["Effluent Screens","SludgeScum Accumulation"] | [18 empty] | [Comments]: Annual Inspection - Serviced effluent screen(s) and pumped septic tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/13/2020 | 12:40 PM
06/01/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | SES MidAtlantic LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Gravity | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/15/2021 | 09:00 AM
03/27/2020 |  | Routine, Scheduled | 234-14-275 | Chesapeake | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Chesapeake | Farmer's Septic Service, Inc. |  | Ross | Cole | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | [Comments]: Serviced system. Checked the pump, panel, & floats (ok). Cleaned the filter and the diffuser in the Clearstream. Changed the filter in the aerator and changed the mesh screen in the spinfilter. The Polylok UV is not working - power going through the switch but not to the light cord - either the ballast or the circuit board is bad - could be more. The timer is set to 8 minutes every 2 hours - it was set at 3 hours every 2 hours. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 03/27/2020 | Jan 1 1900 12:00PM
11/05/2020 |  | Routine/Scheduled | 17-142-0233 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Old Dominion Onsite, Inc. | 1942001549 | Russell | Revis | [9 empty] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump"] | N/A | [17 empty] | Cleaned effluent filter and manifold. System appears to be functioning well. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 11/05/2020 | Jan 1 1900 1:30PM
07/06/2020 |  | RoutineScheduled | n/a | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Wastemaster Inc |  | Timothy | Jenkins | 2.000000 |  | ATU | Recirculating Sand Filter | Pump | Gravity | Discharge |  |  | [] | ["Other"] | [18 empty] | Collected E Coli Sample | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 07/31/2020 | 01:35 PM
11/02/2020 |  | RoutineScheduled | SP-05-227 | Stafford | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Control Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | ["Control Operation" ,"Attached Growth Medium" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | YES | [15 empty] | Will be sent separately | Inspected | Re-circ overide bulb is burnt out on mother board but computer does recognize it. Pump out required, proposal to be sent to customer to meet pumper for pump out and to replace re circ lid on inlet riser. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
03/16/2020 |  | RoutineScheduled | 107-05-0353 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Onsite Wastewater Services - May Supply | 1942001022 | Sara | Tusing |  |  | none | none | Pump | Gravity |  | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 05/28/2021 | 05:41 AM
09/24/2020 |  | RoutineScheduled | 069040904 | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 2705110225 | Larry | Royston | [9 empty] | ["None"] | ["None"] | YES | [16 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 10/05/2020 | 12:00 AM
01/06/2020 |  | Follow-Up | 175-08-0058 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 | Approved | EHD - Prince William | Ace Contracting Services Inc | 1942001120 | Lawrence | Fellenz Jr. | 1.000000 |  | Puraflo | none | Pump | Gravity |  | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected | Replaced Puraflo System With A EZTREAT TL-3 System | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 |  | 06/29/2021 | 10:39 PM
08/14/2020 |  | RoutineScheduled |  | Warren | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Puraflo | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter" ,"Effluent Screens" ,"Level Sensor Operation"] | ["Control Operation" ,"Auxiliary Filter" ,"Effluent Screens" ,"Level Sensor Operation"] | YES | [7 empty] | 08/14/2020 |  | 12.000000 | [5 empty] | Will be sent separately | Inspected | Replaced timer in control panel Replaced floats in pump tank Septic tank pumped Lab Sample normal | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance |  | 04/26/2021 | 09:04 AM
03/27/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Paid | EHD - Fairfax | MCKIM, STEPHEN E | 1934000043 | STEPHEN | MCKIM |  |  | Septic Tank Only | Septic Tank Only | None | None | None | None |  | ["SludgeScum Accumulation"] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [18 empty] | [Comments]: Pump tank riser is cracked and needs parged and the pump tank needs pumped out | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 04/20/2020 | Jan 1 1900 10:48AM
06/02/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | SES MidAtlantic LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/15/2021 | 09:00 AM
05/04/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Onsite Wastewater Services - May Supply | 1942001022 | Sara | Tusing | 1.000000 |  | Orenco Advantex | Orenco Advantex | Pump | Gravity |  | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Inspection by ds | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/28/2021 | 05:41 AM
05/26/2020 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Pump | Distribution Box |  | None |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Recirculation Pump","Sludge/Scum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Recirculation Pump","Sludge/Scum Accumulation"] | N/A |  | 9.97 | 6.900000 | 7.500000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 05/26/2020 | Jan 1 1900 3:15PM
01/04/2020 |  | RoutineScheduled | 124-STS-2379 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Advantex | [6 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | ["Attached Growth Medium","Control Operation","Recirculation Pump","Distribution Pump Operation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 01/04/2020 | 12:00 AM
03/02/2020 |  | Routine, Scheduled | 05-197-A7 | Wise County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Lenowisco | DEEL, DENNY M | 1942001097 | DENNY | DEEL |  |  | Jet ATU | None | Gravity | None | Alternative Discharge | Chlorine | 200.000000 | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens","SludgeScum Accumulation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens"] |  | Musty | Clear | [15 empty] | [Comments]: Installs Own Tablets | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/03/2020 | Jan 1 1900 10:40AM
04/16/2020 |  | Routine, Scheduled |  | Page County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Lord Fairfax | Cubbage, Harrison Lee, II | 1942001021 | Harrison | Cubbage | 1.000000 | 1500 | Septic Tank Only | Orenco Advantex | Pump | Drip | Drip Tubing | None |  | ["Control Operation","Dispersal System Operation","Effluent Screens"] | ["Control Operation","Dispersal System Operation","Effluent Screens"] |  | Musty | Clear | [15 empty] | [Comments]: Jetted Drainfield that has a clog Recirc Pump- Off 19.7min On .5min ETM-2619.1HR Cycle COunt-11287 Discharge Pump- Off 2hrs On 10min ETM-1780.4Hr Cycle COunt-45034 Sludge/Scum Accumulations: Comp.1-12"/1" Comp.2-5"/0" Pump Tank-3"/0" | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/24/2020 | 01:46 PM
07/07/2020 |  | Routine, Scheduled | 175-14-0211 | Prince William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Clearstream |  |  |  |  | UV Light |  | ["Blower/Compressor/Aerator Operation","Disinfection","Dispersal System Operation"] | ["Blower/Compressor/Aerator Operation"] |  | Good | Clear | [15 empty] | ARV broken sewage coming to surface. UV Light burned out. Pump Amps 10.77 ETM 1518 Cycles 12638 Water Meter Reading 415970 Septic Sludge 8" Scum 12" ATU Sludge 3" Scum 2" Pump Sludge 1" Scum 0 | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 07/07/2020 | 09:29 AM
12/28/2020 |  | RoutineScheduled | 069-18-0400 | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax |  |  | Michael | Edmonson | 1.000000 | 1500 | Microfast | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Effluent Screens","SludgeScum Accumulation","Level Sensor Operation"] | ["BlowerCompressorAerator Operation","Effluent Screens","SludgeScum Accumulation","Level Sensor Operation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 01/01/2021 | 12:35 PM
11/03/2020 | Alternative | Routine/Scheduled | 166-10-133 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | PremierTech, EFX |  | Pump | Distribution Box | Aggregate Trench | None | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | Musty | Clear | [15 empty] | Septic tank pumped for peatmoss biofilter changeout. Peatmoss biofilter changeout | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 11/04/2020 | 08:00 AM
11/23/2020 | Alternative | Routine/Scheduled | 136-11-0105 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | Clearstream |  | Pump | Drip | Drip Tubing | UV Light | 450.000000 |  | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | Musty | Clear | [15 empty] | Routine Service Primary Septic Tank - normal operating level - effluent screen serviced. Aeration Tank - normal level - compressor serviced. UV Light - serviced. Pump Tank - normal level - pump, float sensors & controls operating. Drip Headworks - serviced, field flushed, drip screen serviced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 11/24/2020 | 08:00 AM
03/24/2020 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump | Drip | Elevated Sand Mound | UV Light |  | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  | 1.3 | 7.530000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/24/2020 | Jan 1 1900 11:45AM
04/06/2020 |  | RoutineScheduled | 107-02-0647 (LEGACY ALT. SYSTEM) | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Onsite Wastewater Services - May Supply | 1942001022 | Sara | Tusing | 1.000000 |  | Orenco Advantex | none | Pump | Gravity |  | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 05/28/2021 | 05:41 AM
09/22/2020 | Alternative | RoutineScheduled | 171-06-0790 | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | [6 empty] | PuraFlo |  | Pump | Pressure | Drip |  |  | ["Auxiliary Filter","Septic Tank Baffles"] | ["Auxiliary Filter","Septic Tank Baffles"] | [18 empty] | leak in valve box to be addressed | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 09/22/2020 | 12:00 AM
08/13/2020 | Alternative | Routine/Scheduled | 157-06-0041 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | Serviced system. Checked the pump, panel, & floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. The septic tank needs additional risers on it so it can be properly inspected in the future. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 08/13/2020 | 12:00 PM
01/03/2020 |  | Routine, Scheduled | 228-14-0447 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Virginia Beach | [8 empty] | Pump | Drip | Elevated Sand Mound | UV Light |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] |  |  |  | 6.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/03/2020 | Jan 1 1900 11:50AM
05/07/2020 |  | RoutineScheduled | 181-02-0445 (LEGACY ALT. SYSTEM) | Rockbridge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter | [9 empty] | [] | [] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 06/02/2021 | 12:00 AM
11/17/2020 |  | RoutineScheduled | 175-15-0300 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 1.000000 |  | Septic/ Aquarobic |  | Pump | Pressure | Mound | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [17 empty] | Aquarobic tank-1"sludge/ No pump out needed/ Pump @ 63gpm/ No counts on the control panel/ Blower air filter cleaned/ Mound site: no breakout or spongy areas, plants and trees in good shape. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
02/27/2020 |  | Routine, Scheduled | 234-18-390 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesapeake | VANHOLTEN, CRAIG S | 1934000053 | CRAIG | VANHOLTEN |  |  | Clearstream ATU | Septic Tank Only | None | None | None | None | [11 empty] | 02/27/2020 |  | 3.000000 |  | 1.000000 |  |  |  | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/27/2020 | Jan 1 1900 8:30AM
05/11/2020 |  | RoutineScheduled |  | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Soils, Inc. | 1940001392 | Markham | Smith | 2.000000 | 1500 | Mirofast 0.75 in a Hanover 1500 top seam tank |  | Pump | Gravity | Trenches | Not Applicable | 54.000000 | [] | ["Attached Growth Medium","BlowerCompressorAerator Operation","SludgeScum Accumulation","Dispersal System Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 07/31/2020 | Jan 1 1900 12:00AM
07/07/2020 |  | Initial Visit | S 800-15-0138 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Western Tidewater | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 500 | Clearstream |  | Pump | Drip | Drip Tubing | None | 450.000000 |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | Musty | Clear | [15 empty] | Initial visit - System reported in alarm - Owner reports 20+ guests over weekend with many staying overnight - Technician believes system hydraulically overloaded due to excessive water usage. Trash Tank - normal level ATU - functioning - Normal level on arrival - evidence of high level present. Discharge Tank - High Level - drip screen serviced - operating properly - Hydraulic overload - requires time to return to normal level. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 07/08/2020 | Jan 1 1900 7:30AM
06/16/2020 |  | Initial Visit | 97017302 | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | [6 empty] | tank only |  | Gravity | Pressure | Trenches | Not Applicable |  | ["Distribution Pump Operation"] | ["Distribution Pump Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 06/16/2020 | 12:00 AM
07/28/2020 |  | Routine/Scheduled | 13-120-0345AR | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesterfield | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | PremierTech, EFX | None | Pump | Distribution Box | Aggregate Trench | None | 600.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | Musty | Clear | [15 empty] | Routine service. Primary Septic Tank - normal level - effluent screen serviced. PeatMoss Biofilter - Fiberglass unit - visual of the tank appears to be intact - peatmoss biofilter raked out and turned - reported to be in bad condition Pump Basin - plastic - appears to be intact - pump and float sensors operating properly. Surge Box & Distribution Box - normal level - all laterals accepting effluent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 07/29/2020 | Jan 1 1900 7:30AM
05/02/2020 |  | RoutineScheduled | 133 07 0974 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1500 | Advantex |  | Pump | Gravity | Trenches |  |  | ["None"] | ["None"] | [18 empty] | 12" of solids in septic tank. Cleaned recirculation basket filter. Flushed treatment unit basket filter. Tested floats, pumps and alarm. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 09/21/2020 | 07:03 PM
04/06/2020 |  |  | 08-113-254 | Buchanan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 04/06/2020 | 12:00 AM
06/03/2020 |  | RoutineScheduled | {FIPSCode}-STS-30001 | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 2705110225 | Larry | Royston | [9 empty] | ["None"] | ["None"] | YES | [16 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 08/17/2020 | 12:00 AM
02/27/2020 |  | Initial Visit | C 800-18-0271 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Western Tidewater | Farmer’s Septic Service, Inc. |  | Ross | Cole | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | [Comments]: Serviced system. Checked the pump, panel, & floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. The timer is set to 1.5 minutes every 2 hours. Took initial BOD sample. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/27/2020 | Jan 1 1900 12:00PM
04/28/2020 | Alternative | Initial Visit | 157-18-0129 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [9 empty] | 3.000000 | [7 empty] | Serviced system. Checked the pump, panel, & floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. The timer is set to 2 minutes every 2 hours. Took initial BOD sample. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 04/28/2020 | 12:00 PM
01/06/2020 |  | Routine, Scheduled | 179-16-0229-SP | Stafford County | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Orenco Advantex | None | Pump | Distribution Box | Aggregate Trench |  |  | ["Attached Growth Medium","Effluent Screens","Recirculation Pump"] | ["Attached Growth Medium","Effluent Screens","Recirculation Pump"] | [18 empty] | [Comments]: Property Sale Inspection.The gate valve for the recirculation pump is leaking. We recommend installing a ball valve in its place. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 02/04/2020 | 07:46 AM
08/13/2020 |  | Initial Visit | 05-190-148 | Surry | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Crater | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | Clearstream | None | Pump | Distribution Box | Aggregate Trench | None | 600.000000 |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | Pungent | Discolored | [15 empty] | System pumped by Goodman's septic service. Initial Visit - Real Estate Transfer Inspection - Minor Repair. Septic tank at normal level on arrival - pumped empty for inspection. Aeration unit not operating due to failed compressor - replaced compressor with HiBlow 60/80 and placed back into operation. Pump Tank at normal operating level on arrival - pumped empty for inspection Distribution Box not located - walkover of area indicated to be absorption field had no indications of surfacing. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 08/14/2020 | Jan 1 1900 8:00AM
03/23/2020 |  | Routine, Scheduled | SWT-02-1168 | Spotsylvania County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Biomicrobics MicroFAST | None | Pump | Drip | Drip Tubing |  |  | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/06/2020 | 02:46 PM
08/26/2020 |  | RoutineScheduled | 093-16-0061 | Isle of Wight | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Western Tidewater | Environmental Services of Virginia | 1942001182 | Steve | Haley | 2.000000 | 1000 | 1000 Gal S/T | Clearstream NC600 ATU | Pump | Pressure | Discharge | UV | 150.000000 | ["None"] | ["None","Dispersal System Operation"] | YES | Musty | Clear | 7.200000 | 5.400000 |  |  |  | 08/26/2020 | Sample Tap | 2.000000 |  | 1.000000 | 3.900000 |  |  | Attached to this report |  |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 09/15/2020 | Jan 1 1900 3:00PM
11/18/2020 |  | Routine/Scheduled |  | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump | Distribution Box |  | None |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  | 7 | 4.000000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 11/18/2020 | Jan 1 1900 4:15PM
05/13/2020 |  | RoutineScheduled | 13-197-048 | Wise | This AOSS is functioning as designed and in accord | Approved | EHD - Lenowisco | Septic Inc |  | Denny | Deel |  |  |  |  | Gravity | None | Alternative Discharge | UV | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens"] | true | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accord |  |  | 12:00 AM
11/20/2020 |  | Routine/Scheduled | 196-06-144 | Westmoreland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 3.000000 | 3500 | Microfast |  | Pump | Drip | Drip Tubing |  |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 11/20/2020 | 05:00 PM
01/20/2020 |  | Routine, Scheduled | {FIPSCode}-STS-3819 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesapeake | R & K Septic, Inc. |  | John | Butt, Jr |  |  | Clearstream ATU |  | Pump | Distribution Box |  | None |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] |  |  |  | 7.980000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/20/2020 | Jan 1 1900 11:00AM
10/22/2020 |  | RoutineScheduled |  | Pulaski | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - New River | MSS INC |  | Tim | Conner | 1.000000 | 1000 | MICROFAST |  | Gravity | Gravity | Trenches | Not Applicable |  | ["on"] | ["on"] | NA | Septic | Cloudy | [5 empty] | 11/13/2020 | Sample Tap | [6 empty] | Attached to this report | Inspected | EVERYTHING FUNCTIONING | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 11/13/2020 | 12:00 PM
06/15/2020 |  | RoutineScheduled | S-12-111-0081 | Botetourt | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | Hunter E. Ayres, General Contractor | 1942001166 | Hunter | Ayres | 3.000000 | 6,000 | Ecopod |  | Pump | Pressure | Trenches | Not Applicable |  | ["Auxiliary Filter","Effluent Screens"] | ["Auxiliary Filter","Dispersal System Operation"] | YES | [17 empty] | Filters checked and cleaned. All pumps and control panels functioning properly. System did not need to be pumped. No apparent leaks in system or drain field area. All child safety nets in place and in good condition. All lids properly secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 07/11/2020 | Jan 1 1900 3:30PM
03/25/2020 |  | Routine, Scheduled |  | Loudoun County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | EcoPod | None | Pump | Drip | Drip Tubing | [23 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/12/2020 | 02:21 PM
05/07/2020 |  | RoutineScheduled | 181-16-0108 | Rockbridge | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Central Shenandoah | Onsite Wastewater Services - May Supply | 1942001627 | Drew | Shull | 1.000000 |  | Orenco Advantex | none | Pump | Gravity |  | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/28/2021 | 05:41 AM
01/11/2020 |  | Routine, Scheduled |  | Prince William County | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Paid | EHD - Prince William | KLEINDL, JAMES LEE | 1942001380 | JAMES LEE | KLEINDL | 1.000000 | 1500 | Biomicrobics MicroFAST | Septic Tank Only | Pump | Distribution Box | Aggregate Trench | None | [21 empty] | [Comments]: need to replace computer in panel box | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 02/03/2020 | 06:45 PM
05/18/2020 |  | Follow-Up | 154-13-0195 | Louisa | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Blue Ridge | Dominion Septic, Inc | 1942001125 | Tom | Jackson |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [9 empty] | 11.000000 | [5 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
01/13/2020 |  | Routine, Scheduled | 179-15-0127-SWP | Stafford County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | None | Pump | Distribution Box | Aggregate Trench |  |  | ["Attached Growth Medium","Effluent Screens","Recirculation Pump"] | ["Attached Growth Medium","Effluent Screens","Recirculation Pump"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/04/2020 | 07:46 AM
03/14/2020 |  | Routine, Scheduled |  | Albemarle County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Blue Ridge | BASORE, WESLEY LEE | 1942001047 | Wesley | Basore | 1.000000 | 1000 | Sandfilter, Recirculating | None | Pump | Drip | Drip Tubing | None | 150.000000 | ["Auxiliary Filter","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Auxiliary Filter","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/26/2020 | 10:17 AM
10/14/2020 |  | RoutineScheduled | 133 01 1092 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1000 | BioMicrobics MicroFast |  | Pump | Pressure | Drip |  |  | ["None"] | ["None"] | [17 empty] | Pumped Out | 24" of solids in septic tank. Repaired drip field tubing leak. 36" of solids in treatment unit. Cleaned blower filter. Cleaned drip field spin filter. Tested floats, pump and alarm. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 11/09/2020 | 07:03 PM
07/06/2020 |  | RoutineScheduled | 43717 | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | ["None"] | ["None"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 07/28/2020 | 12:15 PM
02/13/2020 |  | RoutineScheduled | {FIPSCode}-STS-18980 | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Combs Wastewater Management LLC | 1942001353 | Amy | Combs | 2.000000 | 1000 |  |  | Pump | Gravity | Drip | Not Applicable | 450.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12/28/2020 | 12:00 AM
08/19/2020 |  | RoutineScheduled | 05-125-081 | Dickenson | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
05/28/2020 | Alternative | Routine/Scheduled | {FIPSCode}-STS-63347 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001063 | K.R. Trapper | Davis | [11 empty] | N/A | [17 empty] | At the time of maintenance, the service expert found that all tanks were at normal level. He did note that there was some minor buldging in the pump tank. All pumps and floats were tested and functioning at this time. The peat moss was also in good condition at this time. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 05/29/2020 | 12:44 PM
06/25/2020 |  | RoutineScheduled | SWP-05-15 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Distribution Pump Operation" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter" ,"SludgeScum Accumulation"] | ["Distribution Pump Operation" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | We recommend pumping the septic tank, the ATU and the pump tank due to scum and sludge accumulation. | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 |  | 04/09/2021 | 03:25 PM
04/29/2020 |  | RoutineScheduled |  | Shenandoah | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [7 empty] | 04/29/2020 |  | 2.000000 | [5 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/26/2021 | 09:04 AM
10/01/2020 |  | RoutineScheduled | R15-180-0021 | Roanoke | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 750 | BIOMICROBICS MICROFAST |  | Pump | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","Effluent Screens"] | ["Auxiliary Filter","Effluent Screens"] | YES | [17 empty] | CLEANED BLOWER AND SPIN FILTER, SYSTEM DID NOT NEED TO BE PUMPED, PULLED PUMP FROM SYSTEM AND CLEANED EFFLUENT SCREENS, REMOVED AND CLEANED LARGE FILTER LOCATED IN PUMP TANK, ADJUSTED DRIP FIELD PRESSURE, NO VISIBLE LEAKS IN DRIP FIELD, SYSTEM CONTROLS OPERATING AS DESIGNED, LIDS SECURED | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 10/07/2020 | 12:00 AM
04/14/2020 |  | Routine, Scheduled | 175-18-0298 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Biomicrobics MicroFAST |  |  |  |  | UV Light |  | ["Blower/Compressor/Aerator Operation","Control Operation"] | ["Blower/Compressor/Aerator Operation","Control Operation"] |  | Good | Clear | [15 empty] | Spin filter cleaned. Pump Amps 10.44 ETM 126 h Cycles 1182 Water Meter Reading 55540 Septic Sludge 8" Scum 4" ATU Sludge 10" Scum 0 Pump Sludge 1" Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/14/2020 | 10:33 AM
09/24/2020 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump | Distribution Box |  | None |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  |  | 8.200000 | 5.810000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 09/24/2020 | Jan 1 1900 2:30PM
02/24/2020 |  | Routine, Scheduled | SD-10-109 | Culpeper County | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | EcoPod | None | Pump |  |  | Chlorine |  | ["Attached Growth Medium","BlowerCompressorAerator Operation","None"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","None"] | [10 empty] | 2.000000 |  | 1.000000 | 8.330000 |  |  |  |  | [Comments]: DO 11.01The sand filter is holding water. We recommend contacting an AOSE for assistance with sand replacement or other repairs. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 04/06/2020 | 02:45 PM
08/06/2020 |  | RoutineScheduled | SWP-02-463 | Stafford | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  | ["Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Attached Growth Medium" ,"Control Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Level Sensor Operation"] | ["Attached Growth Medium" ,"Control Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | YES | [15 empty] | Will be sent separately | Inspected | Roots in last pod (pad site) so it can not be controlled. Peat is degraded but still OK. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
07/28/2020 |  | Initial Visit | 15-163-0004 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chickahominy | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | Clearstream |  | Pump | Drip | Drip Tubing | None | 450.000000 |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | Musty | Clear | [15 empty] | Initial visit for service and service agreement. Processing Tank - 3 Compartment single tank. Trash tank normal level Aeration tank - normal operating level - weir pulled and serviced. Compressor serviced. Pump tank - normal operating level - discharge pump serviced, float sensors and control panel operating properly. Drip Dispersal - manual headworks - system flushed - drip screen serviced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 07/29/2020 | Jan 1 1900 8:15AM
09/16/2020 | Alternative | Routine/Scheduled | 151-02-317 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 500 | Biomicrobics MicroFAST | None | Pump | Distribution Box | Aggregate Trench | None | 450.000000 |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | Musty | Clear | [15 empty] | Routine service conducted. Trash Tank - normal operating level Aeration - normal operating level - compressor serviced. Pump Tank - normal operating level - pump, float sensors & controls operating properly | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 09/17/2020 | 07:45 AM
10/13/2020 | Alternative | Routine/Scheduled | 166-07-573 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 2.000000 | 2500 | Microfast |  | Pump | Drip | Drip Tubing |  |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 10/13/2020 | 02:30 PM
02/28/2020 |  | Routine, Scheduled | 09-120-0193A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesterfield | Madison Environmental LLC |  | Larry | Madison, Jr. |  |  | Biomicrobics MicroFAST |  | Pump | Distribution Box |  |  |  | ["BlowerCompressorAerator Operation","Control Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Lab results not reported by Operator, EHS chose "No" in order to allow saving updated entry. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/28/2020 | Jan 1 1900 2:00AM
07/23/2020 |  | RoutineScheduled | 175-13-0175 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Wastemaster Inc |  | Timothy | Jenkins | 2.000000 |  | ATU | EZ Treat | Pump | Gravity | Discharge | UV |  | [] | [] |  | Musty | Clear | 7.200000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 10:35 AM
07/11/2020 |  | Routine, Scheduled | 175-05-0628 | Prince William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Biomicrobics MicroFAST |  |  |  |  | None |  | ["Blower/Compressor/Aerator Operation"] |  |  | Bad | Brown | [15 empty] | Compressor is bad. Pump Amps 12.42 Water Meter Reading 644590 Septic Sludge 4" Scum 12" ATU Sludge 6" Scum 0 Pump Sludge 3" Scum 0 | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 06/25/2020 | 11:24 AM
09/11/2020 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintanence requirements | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Gravity | Gravity |  | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Septic inspection of a conventional pump system. The state requires that all conventional septic tanks must be pumped out EVERY 5 years and filed with the state and county. The septic control panel is a demand dose. There is 1 pvc clean out near the house. The pvc sewer line was camera snaked and was clear. The septic tank has a riser and a filter that was cleaned. The filter manufacture recommends the filter be cleaned every 6 months. The septic tank was pumped out. The pump tank, pump, floats and force main were inspected. The 4 port splitter was in good condition. The two 9 port plastic d-boxes were broken and not holding effluent. They will need replaced. Health dept will need to issue a permit. All 8 header lines were camera snaked and were clear. The drain field was probed and dry. AT this time the septic system is not in working condition | This AOSS is not functioning as designed or in accordance with the performance/maintanence requirements |  | 04/14/2021 | 04:27 PM
07/15/2020 |  | Routine, Scheduled | 175-03-0523 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Orenco Advantex |  |  |  |  | None |  | ["Effluent Screens"] | ["Effluent Screens"] |  | Good | Clear | [15 empty] | Pump Amps 11.42/5.98 Septic Sludge 5" Scum 0.50 ATU Sludge 12" Scum 0 Pump Sludge 7" Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 07/15/2020 | 03:30 PM
08/10/2020 |  |  | 69120106 | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 2705110225 | Larry | Royston | [9 empty] | ["None"] | ["None"] | YES | [16 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 09/02/2020 | 12:00 AM
07/16/2020 | Alternative | Initial Visit | 136-08-0230 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | PremierTech, EFX | None | Pump | Distribution Box | Aggregate Bed | None | 450.000000 | ["Attached Growth Medium"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | Pungent | Discolored | [15 empty] | Pumped septic tank empty in preparation of peatmoss biofilter changeout. Initial visit - Septic tank in normal operating level - effluent screen serviced. Peatmoss biofilter - Concrete EcoFlo with integral pump station - peatmoss biofilter is severely degraded and requires replacement. Ponding present on media - raked and turned as best as possible. Pump Station - pump, float sensors and Orenco controls operating properly. System marked as GOOD as there is no evidence of back-up into residence and no sewage discharged to the ground surface. 08/24/2020 - Peatmoss Biofilter changeout conducted. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 08/27/2020 | 10:00 AM
04/06/2020 |  | RoutineScheduled | 18-142-0387 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | [11 empty] | NA | [17 empty] | At the time of maintenance, the service expert reported that all components were functioning properly and the system was operational. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 04/06/2020 | Jan 1 1900 11:40AM
04/16/2020 |  | RoutineScheduled | 107-04-0673 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Onsite Wastewater Services - May Supply | 1942001022 | Sara | Tusing | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 05/28/2021 | 05:41 AM
08/17/2020 |  | Routine, Scheduled | 175-12-0049 | Prince William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Biomicrobics MicroFAST |  |  |  |  | None |  | ["Level Sensor (Float) Operation"] |  |  | Good | Clear | [15 empty] | Spin filter cleaned. Pump 1 Amps 9.30 ETM 548 hrs Cycles 6193 Water Meter Reading 0249.970 Septic sludge 4" Scum 1" ATU Sludge 4" Scum 0 Pump Sludge 1" Scum 0 Needs OFF float | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 08/17/2020 | 11:15 AM
12/01/2020 |  | RoutineScheduled | 181-00-0093 (LEGACY ALT. SYSTEM) | Rockbridge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1000 | No Treatment |  | Pump | Pressure | Trenches | Not Applicable |  | ["None"] | ["None"] | NA | [17 empty] | The system did not need to be pumped. The controls were operating as designed. There were no visible leaks in the leech field. The lids were secured. This system is a LPD system. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12/28/2020 | 10:45 PM
08/10/2020 |  | Routine/Scheduled |  | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump | Distribution Box | Aggregate Bed | None |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  |  | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 08/10/2020 | Jan 1 1900 11:15AM
08/27/2020 |  | Routine, Scheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Clearstream ATU |  |  |  |  | None |  | ["Blower/Compressor/Aerator Operation"] | ["Blower/Compressor/Aerator Operation"] |  | Acceptable | Clear | [15 empty] | Pump Amps 10.40/9.98 Septic Sludge 8" Scum 0.50 ATU Sludge 1" Scum 1" Pump Sludge 1" Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 08/27/2020 | Jan 1 1900 3:20PM
06/25/2020 |  | RoutineScheduled | 177-11-0013-SP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | EcoPod | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 |  | 04/09/2021 | 03:25 PM
06/15/2020 |  |  | 181-11-0020 | Rockbridge | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central Shenandoah | Hunter E. Ayres, General Contractor | 1942001166 | Hunter | Ayres | 1.000000 | 1000 | Biomicrobics MicroFAST |  | Pump | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","Effluent Screens","SludgeScum Accumulation"] | ["Auxiliary Filter","Effluent Screens"] | YES | [16 empty] | Pumped Out | Pump tank and treatment unit pumped and cleaned. Filters checked and cleaned. No apparent leaks in system or drain field area. Control panels operating properly. Lids properly secured. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 07/17/2020 | 07:15 AM
10/06/2020 |  | Routine/Scheduled | C-11-111-0042 | Botetourt | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Alleghany-Roanoke | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Delta Environmental Products, DF Series |  | Pump | Drip | Drip Tubing | None |  | ["None"] | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 10/06/2020 | Jan 1 1900 12:15PM
08/14/2020 |  | Routine, Scheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Puraflo |  |  |  |  | None |  | ["Effluent Screens"] | ["Effluent Screens"] | [18 empty] | Pump 1 Amps 11.87 ETM 320.63 Cycles 12238 Pump 2 Amps 11.78 ETM 0 Cycles 12267 Septic Sludge 9" Scum 1" Pump Sludge 2" Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 08/14/2020 | Jan 1 1900 9:20AM
01/02/2020 |  | Routine, Scheduled |  | Lancaster County | This AOSS should now return to normal function after having provided the above stated routine maintenance. | Paid | EHD - Three Rivers | PINNIX, JOEL S | 1934000193 | JOEL | PINNIX |  |  | Septic Tank Only | Septic Tank Only | None | None | None | None | [21 empty] | [Comments]: Replaced Timer and Pump relay in control panel. | This AOSS should now return to normal function after having provided the above stated routine maintenance. |  | 01/23/2020 | 10:13 AM
10/01/2020 |  | Routine/Scheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | POWELLS PLUMBING, INC. | 1942001036 | Kurt | Holthaus | 1.000000 | 1250 | Microfast |  | Pump | Drip | Drip Tubing |  | 600.000000 | ["Blower/Compressor/Aerator Operation"] | ["Blower/Compressor/Aerator Operation"] | N/A | [17 empty] | Annual Inspection - Serviced spin filter and blower. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 10/16/2020 | 01:00 PM
02/03/2020 |  | Routine, Scheduled | 179-18-0257-SP | Stafford County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Orenco Advantex | None | Pump | Distribution Box | Aggregate Trench |  |  | ["Attached Growth Medium","Distribution Pump Operation","Effluent Screens","Recirculation Pump"] | ["Attached Growth Medium","Distribution Pump Operation","Effluent Screens","Recirculation Pump"] | [18 empty] | [Comments]: The sewer line has settled entering & exiting the septic tank. We have contacted the installer to ask him to look at this and restore pipes to proper elevation. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/02/2020 | 11:52 AM
10/28/2020 |  | RoutineScheduled | 154-05-1079 | Louisa | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 | Approved | EHD - Blue Ridge | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Attached Growth Medium" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | ["Control Operation" ,"Dispersal System Operation" ,"Attached Growth Medium" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | NA | [15 empty] | Will be sent separately | Inspected | FAST tank requires a pump out, homeowner will arrange for pump out of FAST and pump tank. FAST unit hard wired, panel needs to be replaced. Both check valves must be replaced. Small tree near tank needs to be removed. Proposal for repairs to be sent to homeowner. | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
01/09/2020 |  | RoutineScheduled | 12-195-224-DIS | Washington | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Mount Rogers | Septic Inc |  | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
02/18/2020 |  | Routine, Scheduled | 15-142-0057 | Hanover County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chickahominy | Old Dominion Onsite, Inc. |  | Jason | Hackler | 1.000000 | 1250 | Orenco Advantex |  | Pump | Distribution Box | Aggregate Trench | None |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | [18 empty] | [Comments]: Cleaned filter and pump screen. Flushed manifold. System appears to be operating normally. Septic tank will need to be pumped out in six months. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/18/2020 | Jan 1 1900 1:28PM
11/06/2020 |  | Reportable Incident | 175-11-0545 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green | [9 empty] | ["Level Sensor (Float) Operation"] | ["Level Sensor (Float) Operation"] | [18 empty] | Replaced 3 control floats. | This AOSS should now return to normal function after having provided the above state routine maintenance |  | 11/06/2020 | 04:00 PM
11/16/2020 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | None |  | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | Replaced alarm float | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 11/16/2020 | Jan 1 1900 8:00AM
05/18/2020 |  | RoutineScheduled | 027-STS-15314 | Buchanan | This AOSS is functioning as designed and in accord | Approved | EHD - Cumberland Plateau | Septic Inc |  | Denny | Deel |  |  |  |  | Gravity | None | Alternative Discharge | Chlorine | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens"] | true | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accord |  |  | 12:00 AM
09/19/2020 |  | RoutineScheduled | 154-06-0761 | Louisa | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 | Approved | EHD - Blue Ridge | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Attached Growth Medium"] | ["Control Operation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter" ,"Attached Growth Medium" ,"Level Sensor Operation" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | NA | [15 empty] | Will be sent separately | Inspected | Blower is wired on pump control breaker. Needs new panel, pumping when no floats are attached. Need new drip check valves and to clean/repair zoner. Proposal for repairs to be sent to homeowner. | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
02/26/2020 |  | Follow-Up | 179-13-0210-SR | Stafford County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001350 | Mike | Cook | 1.000000 |  | Orenco Advantex | None | Pump | Distribution Box | [15 empty] | 5.000000 | [8 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/06/2020 | 08:57 AM
08/03/2020 | Alternative | Routine/Scheduled | 157-08-0030 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | PremierTech, EFX |  | Pump | None | Aggregate Bed | None | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | Musty | Clear | [15 empty] | Routine service conducted. Primary septic tank at normal operating level - effluent screen serviced. Pump Basin - normal operating level - pump, float sensors and controls operating properly - minor bulging noted at bottom of pump basin. EcoFlow Fiberglass unit - intact - peatmoss biofilter in good condition - raked and turned - minor roots in biofilter noted. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 08/03/2020 | 09:10 AM
12/31/2020 | Alternative | RoutineScheduled | 171-13-0280 | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | None | Clear | 7.300000 |  |  |  |  | 12/31/2020 |  | 3.000000 |  |  | 2.400000 | [5 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 01/13/2021 | 10:30 AM
11/10/2020 |  | Initial Visit | 069-19-0121 | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Combs Wastewater Management LLC | 1942001353 | Amy | Combs | 2.000000 | 1500 |  |  | Pump | Gravity | Drip | Not Applicable | 600.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12/23/2020 | 12:00 PM
09/25/2020 |  | RoutineScheduled | 061-16-250 | Fauquier | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 5.000000 |  | Bio Barrier | Bio Barrier | Pump | Gravity | Drip | Not Applicable |  | ["Distribution Pump Operation" ,"Auxiliary Filter"] | ["Distribution Pump Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | Biweekly inspection. Grass in dripfield has been cut (hooray), but grass around tanks is still terrible. Replaced surge dosing pump #1 with same model, Zoeller E161. New pump running at 7.06 amps. Blower panel #2 alarms constantly and can't be silenced. Needs to be replaced. In the past 11 days, an average of 1,191.3 gals/day at 182.01 gals/dose was pumped to the dripfield. | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
12/29/2020 |  | RoutineScheduled | 177-07-0254-SWP | Spotsylvania | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Effluent Screens"] | ["Attached Growth Medium" ,"Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/09/2021 | 03:25 PM
11/06/2020 |  | RoutineScheduled | 99-184-5002 | Scott |  |  | EHD - Lenowisco |  |  | John | Hyder |  |  | Jet ATU |  | Gravity |  |  | Chlorination |  |  |  |  | None | Clear | 7.500000 | 6.000000 |  |  | chlorine residual 0 | [10 empty] | No laboratory testing performed. Field inspection only. |  |  |  | 12:00 AM
12/11/2020 |  | Follow-Up | 02-197-A2 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | Wise County Health Dept |  | Rodney | Neece | 1.000000 |  | ATU |  | Gravity | Gravity | Discharge | Chlorination |  |  |  |  | Musty | Cloudy | 7.500000 | 6.000000 |  | 0.000000 | Tablets are located in the chamber | [11 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12/14/2020 | 12:00 AM
05/19/2020 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Gravity | Gravity |  | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Sale inspection on a conventional pump septic system. The control panel is a interior demand dose. There is 1 pvc cleanout near the house. The pvc sewer line was camera snaked and was clear. The septic tank has a concrete riser and a filter that was cleaned when the tank was pumped out. The pump tank, pump, floats and force main were inspected. The d-box was dug up and the header lines were camera snaked. The drain field was probed. At time of inspection all components were in working condition | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 |  | 04/14/2021 | 04:27 PM
04/28/2020 |  | Follow-Up | 177-18-0278-SWP | Spotsylvania | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [9 empty] | 38.000000 | [5 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
10/27/2020 |  | RoutineScheduled | 182-01-0232 (LEGACY ALT. SYSTEM) | Rockingham | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Central Shenandoah | Onsite Wastewater Services - May Supply | 1942001627 | Drew | Shull | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Pressure | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/28/2021 | 05:41 AM
07/10/2020 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Sale inspection on a conventional gravity septic system. The sewer line was camera snaked and was clear. Septic tank was pumped out by other. Septic tank was dug up it was 6 inches under the ground. The effluent in tank was at proper level. The inlet and outlet T's are PVC. The conveyance line was camera snaked and was clear. The concrete d-box was dug up it was 28" under the ground. Header lines were camera snaked and were clear. Drain field was probed. At time of inspection all components were in working condition | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 |  | 04/14/2021 | 04:27 PM
06/25/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | SES MidAtlantic LLC | 1942001203 | James | Green | 1.000000 |  | Orenco Advantex | Orenco Advantex | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Effluent Screens"] | ["Auxiliary Filter" ,"Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/15/2021 | 09:00 AM
01/15/2020 |  | Routine, Scheduled |  | Prince William County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Prince William | Aquarobic Services | 1934000142 | Michael | Blake |  |  | None | None | Pump |  |  |  |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","SludgeScum Accumulation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","SludgeScum Accumulation"] |  | YES | YES | [15 empty] | [Comments]: Aeration was not uniform. Tank pumped by SeptiClean. A couple of diffusers were found to be torn. Tank pressure washed and all sludge and debris removed. New manifold/diffuser assembly installed, leveled and secured with marine nylon rope. Flush valve added for future maintenance and additional ballast added to prevent manifold from floating. Added enough water back to tank to verify excellent aeration and to flush discharge piping. Air filter replaced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/16/2020 | 08:55 AM
07/14/2020 |  | RoutineScheduled | 182-12-0234 | Rockingham | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Central Shenandoah | Onsite Wastewater Services - May Supply | 1942001022 | Sara | Tusing |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | INSPECTION BY DS | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/28/2021 | 05:41 AM
01/23/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Paid | EHD - Fairfax | GOINS, AARON M | 1942001248 | AARON | GOINS |  |  | Septic Tank Only | Septic Tank Only | None | None | None | None | [22 empty] | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 01/24/2020 | Jan 1 1900 3:08PM
10/01/2020 |  | Reportable Incident | S 800-17-0116 | Suffolk | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | Owner called due to the red light being on. Serviced system. Checked the pump, panel, & floats (ok). Cleaned the filter in the Clearstream and cleaned the disc filter. Changed the diffuser in the Clearstream and changed the filter in the aerator. Replaced the buzzer. The UV is not working - bulb and cord are bad - still blowing fuses - probably ballast or circuit board. The septic tank needs additional risers on it so it can be properly inspected in the future. There is visible wetness on the drainfield - most likely due from rain - need to keep an eye on it. The timer is set to 8 minutes every 2 hours. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. |  | 10/01/2020 | Jan 1 1900 12:00PM
01/17/2020 |  | Routine, Scheduled |  | Middlesex County | This AOSS should now return to normal function after having provided the above stated routine maintenance. | Paid | EHD - Three Rivers | LANGFORD, CHARLES T | 1934000143 | CHARLES | LANGFORD | 1.000000 | 1000 | Clearstream | Septic Tank Only | None | None | None | None |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | [19 empty] | This AOSS should now return to normal function after having provided the above stated routine maintenance. |  | 02/19/2020 | 09:12 AM
05/11/2020 |  | Follow-Up | 17-120-0081AR | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Stamie E. Lyttle Co. | 1942001470 | Eric | Tambourine | [9 empty] | [] | [] | [19 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. |  |  | 12:00 AM
06/02/2020 |  | RoutineScheduled | 187070128 | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Greenway Engineering | 1942001008 | Jeremy | Ferguson | 1.000000 | 1000 | Puraflo | none | Pump | Pressure | Drip | Not Applicable |  | ["Attached Growth Medium","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Level Sensor Operation","SludgeScum Accumulation"] | NA | [17 empty] | System is operational | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 09/28/2020 | 02:30 PM
09/05/2020 |  | RoutineScheduled | 2115-06-153 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Wastemaster Inc |  | Timothy | Jenkins | 2.000000 |  | PuraFlo | Effluent Filter | Pump | Gravity | Discharge | Chlorination |  | [] | [] | YES | Musty | Clear | 7.900000 |  |  | 2.200000 | [12 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 09/11/2020 | 12:15 PM
05/14/2020 |  | RoutineScheduled | 107-06-0608 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Onsite Wastewater Services - May Supply | 1942001022 | Sara | Tusing | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | INSPECTION DS | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 05/28/2021 | 05:41 AM
08/31/2020 | Alternative | Reportable Incident | 159-10-185 | Middlesex | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | Owner called due to the alarm going off. Serviced system. Checked the pump, panel, & floats (ok). Cleaned the filter in the Clearstream and cleaned the UV light bulb. Changed the diffuser in the Clearstream, installed a re-build kit on the aerator, changed the filter in the aerator, and changed the mesh screen in the spinfilter. The septic tank needs additional risers on it so it can be properly inspected in the future. Still needs a new top for the Clearstream tank (old style black risers). The timer is set to 7 minutes every 1 hour. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 08/31/2020 | 12:00 PM
08/26/2020 |  | Routine/Scheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | POWELLS PLUMBING, INC. | 1942001036 | Kurt | Holthaus | 1.000000 | 1250 | Microfast |  | Pump | Distribution Box | Aggregate Trench |  |  | ["Blower/Compressor/Aerator Operation"] | ["Blower/Compressor/Aerator Operation"] | N/A | [17 empty] | Annual Inspection - Serviced blower. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 09/04/2020 | 12:44 PM
06/03/2020 |  | RoutineScheduled | 01-184-5001 | Scott | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. |  | Denny | Deel |  |  | FAST |  | Gravity | Gravity | Discharge | Chlorination |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
05/13/2020 |  | Follow-Up |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Pad | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Air release valve was repaired. System should return to functioning as designed. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/27/2021 | 01:26 PM
09/18/2020 |  | RoutineScheduled | 2009-126-058 | Dinwiddie | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Crater | Stamie E. Lyttle Co. | 1942001470 | Eric | Tambourine | [9 empty] | [] | [] | [19 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. |  |  | 12:00 AM
07/07/2020 |  | Routine, Scheduled | 175-14-0051 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Biomicrobics MicroFAST |  |  |  |  | None |  | ["Blower/Compressor/Aerator Operation"] | ["Blower/Compressor/Aerator Operation"] |  | Good | Clear | [15 empty] | Pump Amps 8.77 ETM 207.21 Cycles 1696 Septic Sludge 7" Scum 0.50 ATU Sludge 8" Scum 0 Pump Sludge 1" Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 07/07/2020 | 02:20 PM
11/13/2020 |  |  | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | McKim Construction | 1942001330 | Michelle | McKim | 2.000000 |  |  |  | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 11/13/2020 | 12:00 AM
01/14/2020 |  | Routine, Scheduled | 2018-143-0158 | Henrico County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Henrico | [7 empty] | None | Pump | Drip | None | None |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles"] | [18 empty] | [Comments]: The filters and aerator shaft were cleaned. The system is operating as designed in the automatic mode. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/10/2020 | 08:56 AM
08/12/2020 |  | Reportable Incident | 05-137-0189 | Goochland | This AOSS should now return to normal function after having provided the above state routine maintenance | Approved | EHD - Chickahominy | Miller's Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1500 | Orenco Advantex | None | Pump | Distribution Box | Aggregate Trench | None | 600.000000 | ["Control Operation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | [17 empty] | Alarm Event - motherboard for control panel has failed - allowing recirc and discharge pumps to run continuously - probable lightning strike as owner reports other "household appliances" are "fried". New motherboard / control panel ordered. 08/14/2020 - new motherboard installed - timer settings adjusted to permit requirements. | This AOSS should now return to normal function after having provided the above state routine maintenance |  | 08/17/2020 | Jan 1 1900 7:15AM
06/09/2020 |  | Follow-Up |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | SES MidAtlantic LLC | 1942001203 | James | Green | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Pressure | Drip | Not Applicable |  | ["Dispersal System Operation"] | ["Dispersal System Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Repaired break Zone 1. Lime applied to affected area. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/15/2021 | 09:00 AM
05/19/2020 |  | RoutineScheduled | 154-04-1010 | Louisa | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Blue Ridge | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Auxiliary Filter" ,"Attached Growth Medium" ,"BlowerCompressorAerator Operation" ,"Control Operation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | ["SludgeScum Accumulation" ,"Auxiliary Filter" ,"Attached Growth Medium" ,"BlowerCompressorAerator Operation" ,"Control Operation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"Septic Tank Baffles"] | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
08/18/2020 |  | RoutineScheduled |  | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 2705051738 | Joshua | Hott |  |  | Septic | Puraflo | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
05/01/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | Hydro-Action ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/14/2021 | 04:27 PM
05/12/2020 |  | Routine, Scheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Biomicrobics MicroFAST |  |  |  |  | None |  | ["Blower/Compressor/Aerator Operation"] | ["Blower/Compressor/Aerator Operation"] |  | Good | Clear | [15 empty] | Pump 1 Amps 11.46 ETM 36 hrs Cycles 670 Pump 2 Amps 11.75 ETM 35 hrs Cycles 644 Septic Sludge 8" Scum 3" ATU Sludge 1" Scum 0 Pump Sludge 1" Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 05/12/2020 | Jan 1 1900 2:16PM
04/07/2020 |  | Routine, Scheduled |  | Prince William County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Prince William | Aquarobic Services | 1934000142 | Michael | Blake |  |  | None | None | Pump |  |  |  |  | ["Auxiliary Filter","Control Operation"] | ["Auxiliary Filter","Control Operation"] |  | YES | YES | [15 empty] | [Comments]: Replaced worn out/ noisy blower contactor. Also replaced blower starter with proper size. Control panel lights were burnt out, 1 lens cover was missing, and weather seals dry-rotted and worn. All light assemblies replaced with LED assemblies, seals treated, and panel door cleaned. Replaced air filter.Note: Returned on 4/9/20 and replaced failed start capacitor for blower. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/14/2020 | 09:06 AM
10/26/2020 |  | RoutineScheduled | SWT-05-533 | Stafford | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Attached Growth Medium" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Attached Growth Medium" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | Installed EZ Set lid on Septic Tank. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/09/2021 | 03:25 PM
06/22/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/27/2021 | 01:26 PM
11/10/2020 |  | RoutineScheduled | 11-197-A1 | Wise | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
03/26/2020 |  | Reportable Incident |  | Fairfax County | This AOSS should now return to normal function after having provided the above stated routine maintenance. | Paid | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green | [9 empty] | ["Disinfection"] | ["Disinfection"] | [18 empty] | [Comments]: Replaced UV Bulb. | This AOSS should now return to normal function after having provided the above stated routine maintenance. |  | 03/26/2020 | Jan 1 1900 11:59AM
03/19/2020 |  | Routine, Scheduled |  | Loudoun County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | None | None | Pump | Drip | Drip Tubing | [22 empty] | [Comments]: The pump chamber lid will likely need to be replaced next year. Recommend replacement of the drip hydraulic unit filters. The disks are sticking and not functioning to the best of their ability. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/19/2020 | 08:35 AM
09/04/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 2.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/14/2021 | 04:27 PM
06/23/2020 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Eco Virginia | 1942001235 | William | Poindexter | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 |  | 06/03/2021 | 05:53 AM
01/25/2020 |  | Routine, Scheduled |  | Northumberland County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Three Rivers | BEASLEY, THOMAS W | 1934000450 | THOMAS | BEASLEY | 2.000000 | 2500 | Ecoflo | Septic Tank Only | Pump | None | Aggregate Bed | None |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [5 empty] | 40.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/25/2020 | 03:00 PM
03/04/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Paid | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Puraflo |  |  |  |  | None |  | ["Effluent Screens"] | ["Effluent Screens"] |  | Good | [16 empty] | [Comments]: Pump in Puraflo tank is bad.Pump 1 Amps 38.62/12.98 ETM 13342/13348 Cycles 7705/7680Pump 2 Amps 12.03/12.80 ETM 105590/20 Cycles 800/2560Septic Sludge 6" Scum 1"Pump Sludge 3"/2" Scum 0/0 | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 03/04/2020 | Jan 1 1900 9:50AM
04/25/2020 |  | RoutineScheduled | 196-00-457 | Westmoreland | This AOSS is functioning as designed and in accord | Approved | EHD - Three Rivers | Wastemaster |  | Tim | Jenkins | 2.000000 |  |  |  | Pump |  | Subsurface |  |  | [] | [] | [8 empty] | 04/25/2020 | [10 empty] | This AOSS is functioning as designed and in accord |  |  | 12:00 AM
09/08/2020 |  | Reportable Incident | 153-STS-19014 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Prince William | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Clearstream | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Atu alarm, chirping sound but no light. Replaced ruptured diaphragms in compressor. Replaced alarm horn and bulb in atu control panel. Replaced diffuser block at bottom of airline. Owner has appointment to have atu tank pumped out. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
07/06/2020 |  | Routine/Scheduled | 03-120-0414 | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesterfield | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | PremierTech, EFX |  | Pump | Distribution Box | Aggregate Trench | None | 600.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | [17 empty] | Routine service conducted. Septic tank at normal operating level - effluent screen serviced. EcoFlo unit has minor fractures developing - Peatmoss Biofilter Media raked out - in fair condition. Discharge pump basin intact - pump, float sensors and controls operating properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 07/07/2020 | Jan 1 1900 11:30AM
09/26/2020 |  | RoutineScheduled |  | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Wastemaster Inc |  | Timothy | Jenkins | 2.000000 |  | Recirculating Sand Filter |  | Pump | Gravity | Discharge | Chlorination |  | [] | [] |  | Musty | Clear | 6.600000 | 7.900000 |  | 2.200000 |  | 09/26/2020 |  | 1.800000 |  |  | 37.800000 |  |  | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 10/15/2020 | Jan 1 1900 1:35PM
10/02/2020 |  | Routine/Scheduled | 075-STS-31581 | Goochland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chickahominy | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. |  |  | Clearstream ATU |  | Pump |  |  |  |  | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 10/02/2020 | Jan 1 1900 12:30PM
10/06/2020 |  | Routine/Scheduled |  | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump | Drip | Elevated Sand Mound | UV Light |  | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  | 8.28 | 6.680000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 10/06/2020 | Jan 1 1900 12:05PM
03/02/2020 |  | Follow-Up | 179-08-0193-SWT | Stafford County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Puraflo | None | Pump | Distribution Box | [23 empty] | [Comments]: Reseal septic tank and pump tank risers. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/03/2020 | 05:36 AM
10/24/2020 |  | RoutineScheduled | SD-87-458 | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Wastemaster Inc |  | Timothy | Jenkins | 2.000000 | [5 empty] | Mound | Chlorination |  | [] | [] |  | Musty | Clear | 6.200000 |  |  | 2.200000 | [11 empty] | Trash Tank and Mound Located below grade | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 11/06/2020 | 11:05 AM
01/21/2020 |  | Routine, Scheduled |  | Prince William County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Prince William | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Biomicrobics MicroFAST | None | Pump | Distribution Box | Aggregate Trench |  |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/04/2020 | 07:46 AM
03/16/2020 |  | Routine, Scheduled |  | Loudoun County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | None | None | Gravity | Distribution Box | Aggregate Trench | [23 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/16/2020 | 11:28 AM
12/23/2020 | Alternative | Pump-Out Only | 171-04-0148 | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | POWELLS PLUMBING, INC. | 1942001036 | Kurt | Holthaus |  |  | Puraflo | [6 empty] | ["Effluent Screens","Sludge/Scum Accumulation"] | ["Effluent Screens","Sludge/Scum Accumulation"] | YES | [16 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 01/15/2021 | 01:45 PM
06/12/2020 | Alternative | Initial Visit | 119-STS-94258 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 750 | None | None | Gravity | Distribution Box | Aggregate Trench | None | 450.000000 |  | ["Dispersal System Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | [17 empty] | Asked for Second Opinion - primary septic tank reported by owner to have been pumped empty by another company - Septic tank has root intrusion present - requires "parging" of intrusions. Distribution Box intact, minor root intrusion present - removed. Balanced as necessary. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 06/15/2020 | 09:30 AM
09/18/2020 |  | Reportable Incident | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance | Approved | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green | [9 empty] | ["Level Sensor (Float) Operation"] | ["Level Sensor (Float) Operation"] | [18 empty] | Replaced alarm float. | This AOSS should now return to normal function after having provided the above state routine maintenance |  | 09/18/2020 | Jan 1 1900 8:30AM
01/02/2020 |  | Routine, Scheduled | SD-03-151 | Madison County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Biomicrobics MicroFAST | None | Pump | Drip | Drip Tubing |  |  | ["SludgeScum Accumulation"] | [19 empty] | [Comments]: We recommend pumping the Septic tank due to sludge accumulation. Pumping has been scheduled for Tuesday, January 21, 2020. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/04/2020 | 07:46 AM
05/27/2020 |  | RoutineScheduled | 133 08 0250 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Norweco |  | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | NA |  | Clear | 7.090000 | 10.560000 |  |  | 16.7 c | 05/27/2020 | Pump Chamber | 2.600000 |  |  | 6.800000 |  |  | Will be sent separately | Inspected | 6 Month Initial Laboratory sampling of a Norweco Unit-DO 10.56, Ph 7.09 , Temp 16.7, TSS 6.8 , BOD 2.6 - PACE LAB. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 05/28/2020 | 09:30 AM
03/30/2020 |  | Routine, Scheduled |  | Lancaster County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Three Rivers | LANGFORD, CHARLES T | 1934000143 | CHARLES | LANGFORD | 2.000000 | 1000 | Clearstream | Clearstream | Pump | Distribution Box | None | None |  | ["Effluent Screens"] | [20 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/14/2020 | 02:50 PM
06/15/2020 |  | RoutineScheduled | 179-10-0175-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Effluent Screens" ,"SludgeScum Accumulation"] | ["Attached Growth Medium" ,"Effluent Screens" ,"SludgeScum Accumulation"] | YES | [15 empty] | Will be sent separately | Inspected | Cleared out slime build-up in D-Box. | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 |  | 04/09/2021 | 03:25 PM
08/27/2020 |  | RoutineScheduled | 171-07-0295 | Pittsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Pittsylvania-Danville | Virginia Septic Service LLC | 1942001512 | iain | Waugh | 1.000000 | 1500 | Advantex AX20 |  | Gravity | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 08/30/2020 | 12:00 AM
07/11/2020 |  | RoutineScheduled | 109-11-0358 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1500 | Advantex |  | Pump | Gravity | Trenches |  |  | ["None"] | ["None"] | [18 empty] | 4" of solids in septic tank. Flushed recirculation basket filter. Removed and cleaned recirculation pump screen and replaced. Tested floats, pumps and alarm. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 10/02/2020 | 07:03 PM
09/16/2020 |  | RoutineScheduled | 069-18-0473 | Frederick | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage |  |  | none | none | Pump | Gravity |  | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation"] | ["BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [7 empty] | 09/16/2020 |  | 57.000000 | [5 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/26/2021 | 09:04 AM
05/18/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | SES MidAtlantic LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/15/2021 | 09:00 AM
04/25/2020 | Alternative | RoutineScheduled | 166-99-726 | Northumberland | This AOSS is functioning as designed and in accord | Approved | EHD - Three Rivers | Wastemaster |  | Tim | Jenkins | 1.000000 |  |  |  | Gravity |  | Subsurface |  |  | [] | [] | [5 empty] | 35.000000 |  |  | 04/25/2020 | [9 empty] | Some foaming more than normal | This AOSS is functioning as designed and in accord |  |  | 12:00 AM
06/02/2020 |  | RoutineScheduled |  | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | [9 empty] | ["Attached Growth Medium"] | ["Attached Growth Medium"] | [18 empty] | Septic tank had 6" sludge and 2" scum pump tank had 0" sludge/scum. Puraflo peat was fluffed. CC1-13452 ETM1-209.61 CC2-13580 ETM2-208.43 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
11/18/2020 |  | RoutineScheduled | SWP-05-883 | Spotsylvania | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"Auxiliary Filter" ,"Attached Growth Medium" ,"BlowerCompressorAerator Operation" ,"Control Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | ["Distribution Pump Operation" ,"Level Sensor Operation" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Auxiliary Filter" ,"Attached Growth Medium" ,"BlowerCompressorAerator Operation" ,"Control Operation" ,"Dispersal System Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
08/28/2020 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump | Drip | Elevated Sand Mound | UV Light |  | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  | 10.24 | 6.680000 | 4.900000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 08/28/2020 | Jan 1 1900 1:00PM
06/10/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/14/2021 | 04:27 PM
07/28/2020 |  | RoutineScheduled | 179-06-0422-SP | Stafford | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  | ["Distribution Pump Operation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Attached Growth Medium" ,"Control Operation" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | ["Control Operation" ,"Distribution Pump Operation" ,"Attached Growth Medium" ,"Effluent Screens" ,"Level Sensor Operation" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | YES | [15 empty] | Will be sent separately | Inspected | Roots @ inlet wedge lid on septic tank. Stains on outlet pipe in pump tank. Force main has settled; no alarms OK for now. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
04/07/2020 |  | RoutineScheduled | 165-STS-336087 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | [6 empty] | Sandfilter |  | Pump | Pressure | Discharge | Chlorination |  | ["None"] | [] |  |  |  | 6.800000 |  |  | 2.200000 |  | 04/15/2020 | Sample Tap | [9 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 08/31/2020 | 12:00 AM
01/02/2020 |  | Routine, Scheduled | 179-08-0145-SWP | Stafford County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Puraflo | None | Pump | Distribution Box | Aggregate Bed |  |  | ["Attached Growth Medium","Effluent Screens"] | ["Attached Growth Medium","Effluent Screens"] | [18 empty] | [Comments]: Panel Control inside locked fence. Not inspected. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/04/2020 | 07:46 AM
08/18/2020 |  | RoutineScheduled | 107-04-0052 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Onsite Wastewater Services - May Supply | 1942001022 | Sara | Tusing | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 05/28/2021 | 05:41 AM
12/30/2020 |  | RoutineScheduled | 069-03-0006 | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax |  |  | Michael | Edmonson | 1.000000 | 1000 | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","Level Sensor Operation","SludgeScum Accumulation","Effluent Screens"] | ["Attached Growth Medium","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 01/01/2021 | 11:50 AM
01/24/2020 |  | Routine, Scheduled |  | Prince William County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Prince William | MCKIM, STEPHEN E | 1934000043 | STEPHEN | MCKIM |  |  | Septic Tank Only | Septic Tank Only | None | None | None | None |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/07/2020 | 10:49 AM
06/05/2020 | Alternative | Reportable Incident | 136-14-0165 | Gloucester | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | Changed the diffuser in the Clearstream and changed the filter in the aerator. Installed a new light bulb for the alarm light and new relay in the panel. Un-Stopped line from house and dug up line from the house to the tank - backgrading - fixed. Needs pumping. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 06/05/2020 | 12:00 PM
10/27/2020 |  | RoutineScheduled |  | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001301 | Joshua | Hott | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
01/10/2020 |  | Routine, Scheduled | 061-16-250 | Fauquier County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 5.000000 |  | Bio Barrier | Bio Barrier | Pump | Drip | Drip Tubing |  |  | ["Auxiliary Filter","Distribution Pump Operation"] | ["Auxiliary Filter","Distribution Pump Operation"] | [18 empty] | [Comments]: (Note: broken pvc male adapter for pump #1 was replaced on Jan 2nd.) All tanks in high level again. Tested drip rates/pressures for all zones. Zone 2 had highest drip rate and lowest pressure reading on return line gauge. Spent extra time walking over zone 2 and discovered effluent to surface. Will return in a day or two to repair. In the past 10 days, an average of 7540.5 gals/day at 223.75 gals/cycle (avg.) was pumped for a total of 75,405 gals. Called airport office and asked to have both septic tanks pumped out. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/03/2020 | 05:52 AM
02/17/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Paid | EHD - Fairfax | MCKIM, STEPHEN E | 1934000043 | STEPHEN | MCKIM |  |  | Septic Tank Only | Septic Tank Only | None | None | None | None |  | ["SludgeScum Accumulation"] | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [18 empty] | [Comments]: Septic and atu tank need pumped out | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 02/29/2020 | Jan 1 1900 4:16PM
08/24/2020 |  | Reportable Incident | 234-15-433 | Chesapeake | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Chesapeake | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | Owner called due to the alarm going off. Serviced system. Checked the pump, panel, & floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream, changed the filter in the aerator, and changed the mesh screen in the spinfilter. The UV is not working - circuit board, tube, cord, and bulb. Re-attached weir filter. Raised the return line in the septic tank. Filled pump tank with enough water to run the pump. Pumping company came out and pumped out 1500 gals. Needs a 1 1/4" check valve on pump assembly. No splice box in pump tank. The timer is set to 9 minutes every 1.5 hour. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. |  | 08/24/2020 | Jan 1 1900 12:00PM
10/08/2020 |  | RoutineScheduled | 182-06-0062 | Rockingham | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Central Shenandoah | Onsite Wastewater Services - May Supply | 1942001022 | Sara | Tusing | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Pressure | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Inspected DKS | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/28/2021 | 05:41 AM
05/05/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | EcoPod | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/14/2021 | 04:27 PM
04/07/2020 |  | RoutineScheduled | 107-11-0104 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Onsite Wastewater Services - May Supply | 1942001022 | Sara | Tusing | 1.000000 |  | Orenco Advantex | none | Pump | Gravity |  | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 05/28/2021 | 05:41 AM
06/24/2020 |  | Initial Visit |  | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Western Tidewater | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | Advanced Septic |  | Pump | Distribution Box | Aggregate Trench | None | 450.000000 | ["Blower/Compressor/Aerator Operation","Dispersal System Operation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | Pungent | Discolored | [15 empty] | Initial visit - maintenance repairs necessary Septic tank in normal operating level - no riser access present ATU - Compressor operating intermittently and requires pumpout - Repair/replacement authorized - pumpout authorized. Discharge - pump and float sensors operating properly - minor fracture noted in forcemain - repair authorized. Distribution box - plastic tufftite fractured - replacement with concrete distribution box authorized. NOTE - HD Permit indicates system permitted and installed is supposed to be a Cajun-Aire ATU - System IS NOT a Cajun-Aire unit as this unit is Fiberglass in construction. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 06/25/2020 | Jan 1 1900 11:30AM
07/30/2020 |  | Routine/Scheduled | 03-103-0185 | Amelia | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Piedmont | Miller's Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | PremierTech, EFX | None | Pump | Distribution Box | Aggregate Trench | None | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | Musty | Clear | [15 empty] | Annual service conducted. Primary Septic Tank in normal operating level - effluent screen serviced. Peatmoss Biofilter has excessive ponding present and peatmoss changeout is recommended. Biofilter raked and turned Pump Basin - found at normal operating level - discharge pump, float sensors and controls operating properly. Distribution box - intact - at normal operating level - one header line is root bound, unable to clear, will require excavation. All other laterals accepting effluent. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 07/31/2020 | Jan 1 1900 7:15AM
01/02/2020 |  | Routine, Scheduled | {FIPSCode}-STS-61521 | Spotsylvania County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Michael Smith | 1942001080 | michael | smith | 1.000000 |  | Puraflo | None | Gravity | Distribution Box | Aggregate Bed | [22 empty] | [Comments]: Area around pods needs to be maintained by keep saplings cut down | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/11/2020 | 11:20 AM
07/20/2020 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Onsite Wastewater Services - May Supply | 1942001022 | Sara | Tusing | 1.000000 |  | Orenco Advantex | Orenco Advantex | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | INSPECTION BY DS | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 05/28/2021 | Jan 1 1900 5:41AM
03/24/2020 |  | Initial Visit | 2017-143-0051 | Henrico County | This AOSS should now return to normal function after having provided the above stated routine maintenance. | Approved | EHD - Henrico |  |  |  |  | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | [Comments]: Serviced system. Checked the pump, panel, & floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream (it was broken) and changed the filter in the aerator. Replaced the UV light bulb and replaced the UV light cord. The timer is set to 4.75 minutes every 3.5 hours. Could not take sample due to the diffuser being broken. | This AOSS should now return to normal function after having provided the above stated routine maintenance. |  | 03/24/2020 | 12:00 PM
11/05/2020 |  | Reportable Incident | 175-05-0891 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green | [9 empty] | ["Level Sensor (Float) Operation"] | ["Level Sensor (Float) Operation"] | [18 empty] | Replaced 3 control floats. | This AOSS should now return to normal function after having provided the above state routine maintenance |  | 11/05/2020 | 04:00 PM
06/02/2020 |  | RoutineScheduled |  | Rockingham | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"BlowerCompressorAerator Operation"] | ["Control Operation" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced blower with rebuilt blower | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance |  | 04/26/2021 | 09:04 AM
08/11/2020 |  | Reportable Incident |  | Frederick | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Lord Fairfax | POWELLS PLUMBING, INC. | 1942001036 | Kurt | Holthaus |  |  | Orenco Advantex | [6 empty] | ["Distribution Pump Operation","Sludge/Scum Accumulation"] | ["Distribution Pump Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | Sealed pump chamber due to roots, pumped septic tank and pump chamber. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 11/25/2020 | 12:48 PM
09/12/2020 |  | Initial Visit | 067-STS-37097 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1000 | Advantex RT |  | Pump | Gravity | Trenches |  |  | ["None"] | ["None"] | [18 empty] | Initial start-up inspection. Tested floats, pumps and alarm. Utilizing factory settings for timers. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 10/28/2020 | 07:03 PM
10/28/2020 |  | RoutineScheduled |  | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [9 empty] | 18.000000 | [5 empty] | Attached to this report |  | Septic-10"sludge 4"scum/ Microfast-6"sludge/ Pump tank-1"sludge. No pump out needed/ Counts: Pump1-1257 ETM-47h 57m/ Pump2-1249 ETM-41h 33m Peak-20/ High-11/ Blower air filter cleaned/ No breakout or spongy areas on the drainfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
10/02/2020 |  | RoutineScheduled | {FIPSCode}-STS-9621 | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Greenway Engineering | 1942001008 | Jeremy | Ferguson | 1.000000 | 1000 | Microfast | none | Pump | Pressure | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 10/02/2020 | 03:55 PM
08/20/2020 |  | RoutineScheduled |  | Buckingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Piedmont | Taylor's Septic Service, Inc | 1942001028 | Penny | Taylor | 3.000000 | 6000 | septic | EZ treat Sandfilter | Pump | Gravity | Trenches | Not Applicable | 1400.000000 | ["Effluent Screens","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Recirculation Pump","SludgeScum Accumulation"] | YES | Musty | Clear | [15 empty] | recommend that tanks be pumped and cleaned on the next visit | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 08/20/2020 | 12:00 AM
10/01/2020 |  | Routine/Scheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | POWELLS PLUMBING, INC. | 1942001036 | Kurt | Holthaus | 1.000000 | 1500 | Microfast |  | Pump | Drip | Drip Tubing |  | 600.000000 | ["Blower/Compressor/Aerator Operation"] | ["Blower/Compressor/Aerator Operation"] | N/A | [17 empty] | Annual Inspection - Serviced spin filter and blower. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 10/07/2020 | 02:36 PM
10/06/2020 |  | Routine/Scheduled | 06-131-4118 | Floyd | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Delta Environmental Products, DF Series | Delta Environmental Products, DF Series | Pump | Distribution Box | Aggregate Trench | None |  | ["None"] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 10/06/2020 | 03:30 PM
05/27/2020 |  | RoutineScheduled | 109-19-0241 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1000 | Multiflo |  | Gravity | Gravity | Trenches | Not Applicable |  | [] | [] | NA |  | Clear | 4.170000 | 12.960000 |  |  | 25.4 c | 05/27/2020 | Pump Chamber | 0.000000 |  |  | 5.900000 |  |  | Will be sent separately | Inspected | 6 Month Initial Laboratory sampling of a MultiFlo -DO 12.96, Ph 4.17 , Temp 25.4c, TSS 5.9 , BOD 0(ND) ESS LAB | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 05/12/2020 | 09:30 AM
03/02/2020 |  | Routine, Scheduled | 234850128 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesapeake | R & K Septic, Inc. |  | Robbie | Van Holten |  |  | Clearstream ATU |  | Pump | Drip | Elevated Sand Mound | UV Light |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] |  |  |  | 6.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/02/2020 | Jan 1 1900 9:45AM
03/09/2020 |  | Routine, Scheduled |  | Loudoun County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | None | Pump | Distribution Box | Aggregate Trench | [22 empty] | [Comments]: D-box is cracked and will need to be parge. There are roots getting in that will need to be pulled out. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/12/2020 | 02:21 PM
11/24/2020 |  | RoutineScheduled | 154-09-0067 | Louisa | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Blue Ridge | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"Attached Growth Medium" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Distribution Pump Operation" ,"Level Sensor Operation" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Attached Growth Medium" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation" ,"Dispersal System Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Drainfield is overgrown (saplings) and needs to be cleared. Pressure was 60 PSI, installed new pressure regulator, supply now 39 return 37 PSI. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
11/06/2020 | Alternative | RoutineScheduled | 171-05-692 | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | [6 empty] | Advantex | [6 empty] | ["Attached Growth Medium","Auxiliary Filter","Septic Tank Baffles"] | ["Attached Growth Medium","Auxiliary Filter","Septic Tank Baffles"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 11/06/2020 | 12:00 AM
03/11/2020 |  | RoutineScheduled | 182-12-0139 | Rockingham | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Central Shenandoah | Onsite Wastewater Services - May Supply | 1942001022 | Sara | Tusing |  |  | none | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/28/2021 | 05:41 AM
08/14/2020 |  | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Greenway Engineering | 1942001008 | Jeremy | Ferguson | 1.000000 | 1500 | Microfast | none | Pump | Pressure | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","SludgeScum Accumulation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 09/03/2020 | 01:45 PM
02/09/2020 |  | Reportable Incident | 05-137-0294 | Goochland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Old Dominion Onsite, Inc. | 1942001549 | Russell | Revis | [11 empty] | N/A | [17 empty] | Responded to alarm call. System had caught up from high levels by the time I got there. System was functioning normally. One post for motherboard was loose. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 10/08/2020 | Jan 1 1900 8:20AM
07/01/2020 |  | RoutineScheduled | 40388 | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | [6 empty] | tank only | PuraFlo | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","Septic Tank Baffles"] | ["Attached Growth Medium","Septic Tank Baffles"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 07/01/2020 | 12:00 AM
11/03/2020 | Alternative |  | {FIPSCode}-STS-61643 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Church View Septic Service Inc. | 1942001302 | Charles | Langford | 1.000000 | 1000 | Puraflo |  | Pump |  |  |  |  | ["None"] | ["None"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 11/18/2020 | 12:00 AM
12/03/2020 |  | RoutineScheduled | 033-09-0175-SP | Caroline | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Effluent Screens"] | ["BlowerCompressorAerator Operation" ,"Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected | Installer notified of leaking tanks and resealed/completed repairs. | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 |  | 04/09/2021 | 03:25 PM
05/20/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | For background see Laserfiche file and HD correspondence. On May 20, 2020 the AOSS appeared to be functioning. There were no signs of surfacing effluent and probe around headers were not saturated. There is a fence running in between the distribution box/headers/lines. Without uncovering the distribution box and cameraing the headers and the start of the lines there is no way to definitively say there is or is not an issue at this time. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/27/2021 | 01:26 PM
07/10/2020 |  | RoutineScheduled | 05-163-0185 | New Kent | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chickahominy | Onsite Maintenance Team | 1942001039 | Corey | Braxton | 2.000000 | 600 | Clear stream n600 |  | Gravity | Gravity | Trenches |  | 500.000000 | ["BlowerCompressorAerator Operation","Control Operation","Effluent Screens"] | ["BlowerCompressorAerator Operation","Control Operation","Effluent Screens"] | YES | Musty | Clear | 7.200000 | 3.000000 | [14 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 07/10/2020 | 12:00 AM
08/07/2020 | Alternative | RoutineScheduled | 171-08-0578 | Shenandoah | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Lord Fairfax | Greenway Engineering | 1942001008 | Jeremy | Ferguson | 1.000000 | 1000 | Microfast | none | Pump | Pressure | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Level Sensor Operation","SludgeScum Accumulation"] | NA | [17 empty] | System needs pumped out and unit needs flushed out. Approved once pumpout and flushing is completed | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. |  | 08/13/2020 | 01:40 PM
11/06/2020 |  | Routine/Scheduled | 05-160-0224 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Delta Environmental Products, DF Series |  | Pump | Distribution Box | Aggregate Trench | None |  | ["None"] | ["Blower/Compressor/Aerator Operation","Distribution Pump Operation","Sludge/Scum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 11/06/2020 | 10:30 AM
04/17/2020 | Alternative | Routine/Scheduled | 151-06-0423 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | Ecoflo | None | Pump | Distribution Box | Aggregate Trench | None |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | Filter in Septic Tank is outdated (we recommend its replacement during next scheduled pumping service); Pump and Floats are near/past their expected life; Ecoflo Biofilter (peat moss) was found with root intrusion causing water to pond and not properly filter in the center of the Module. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/20/2020 | 12:43 PM
11/25/2020 |  | RoutineScheduled | 09-113-057 | Buchanan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | WHITEWATER |  | Gravity | Gravity | Discharge | UV | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
05/20/2020 |  | RoutineScheduled | 10-100-0291 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Bundick Well & Pump | 1942001051 | Peter | Duer | 1.000000 | 750 | Septic Tank | Purflo | Pump | Pressure | Pad | Not Applicable | 300.000000 | ["None"] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 07/01/2020 | 12:10 PM
05/21/2020 |  | RoutineScheduled |  | Shenandoah | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Puraflo | none | Pump | Gravity |  | Not Applicable |  | ["Recirculation Pump" ,"SludgeScum Accumulation" ,"Control Operation"] | ["Recirculation Pump" ,"SludgeScum Accumulation" ,"Control Operation"] | NA | [7 empty] | 05/21/2020 |  | 121.000000 | [5 empty] | Will be sent separately | Inspected | Respliced pump connection Homeowner replacing visual alarm Will be returning to site and pumping all tanks | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance |  | 04/26/2021 | 09:04 AM
11/04/2020 |  | RoutineScheduled |  | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Lord Fairfax | dovel enterprises |  | jerry | dovel | 2.000000 | 1000 |  |  | Pump | Pressure | Drip |  |  | [] | [] | YES | None | [15 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 11/12/2020 | 12:00 AM
09/04/2020 |  | RoutineScheduled | 177-STS-86809 | Spotsylvania | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | EZ Treat Sandfilter | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NO | [15 empty] | Will be sent separately | Inspected | 90-Day Inspection | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/09/2021 | 03:25 PM
10/28/2020 |  | RoutineScheduled | 019-STS-24354 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Advantex AX25 RT |  | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | NA | [16 empty] | Inspected | New advantex Installed, Original install inspection, RTU143125, Set in setting for recirculation currently in start up mode. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 10/29/2020 | 09:30 AM
07/20/2020 |  | RoutineScheduled | 181-06-0011 | Rockbridge | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Central Shenandoah | Onsite Wastewater Services - May Supply | 1942001022 | Sara | Tusing | 1.000000 |  | Orenco Advantex | Orenco Advantex | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/28/2021 | 05:41 AM
09/22/2020 |  |  | {FIPSCode}-STS-11947 | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 2705110225 | Larry | Royston | [9 empty] | ["None"] | ["None"] | YES | [16 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
12/02/2020 |  | Routine/Scheduled |  | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump | Drip | Elevated Sand Mound | UV Light |  | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  | 4.09 | 7.270000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 12/02/2020 | Jan 1 1900 4:00PM
03/24/2020 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump | Drip | Elevated Sand Mound | UV Light |  | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  |  | 7.790000 | 3.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/24/2020 | Jan 1 1900 1:30PM
04/02/2020 |  | Routine, Scheduled | 02-113-304 | Buchanan County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Cumberland Plateau | DEEL, DENNY M | 1942001097 | DENNY | DEEL |  |  | Norweco Singulair ATU | None | Gravity | Distribution Box | Aggregate Bed | None | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","Effluent Screens","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Effluent Screens"] |  | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/08/2020 | Jan 1 1900 11:01AM
12/17/2020 |  | RoutineScheduled | 179-07-0105-SWP | Stafford | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Recirculation Pump" ,"Attached Growth Medium" ,"Auxiliary Filter" ,"Control Operation"] | ["Attached Growth Medium" ,"Auxiliary Filter" ,"Control Operation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Recirculation Pump"] | NA | [15 empty] | Will be sent separately | Inspected | Solenoids are not working property due to a bad transformer. Replacement has been ordered. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/09/2021 | 03:25 PM
12/18/2020 |  | RoutineScheduled | 177-18-0399-SP | Spotsylvania | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Attached Growth Medium" ,"Effluent Screens" ,"Recirculation Pump"] | ["Auxiliary Filter" ,"Attached Growth Medium" ,"Effluent Screens" ,"Recirculation Pump"] | YES | [15 empty] | Will be sent separately | Inspected | Pump tank riser is leaking. Installer has been notified and will repair in the near future. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/09/2021 | 03:25 PM
10/13/2020 |  | RoutineScheduled | 08-197-A12 | Wise | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | Wise Health Dept |  | Rodney | Neece | 1.000000 |  | ATU |  | Gravity | Gravity | Discharge | Chlorination |  | ["BlowerCompressorAerator Operation"] |  |  | Septic | Dark Brown | 4.800000 | 0.000000 | [14 empty] | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 10/14/2020 | Jan 1 1900 12:15PM
10/30/2020 |  | Routine/Scheduled | 04-142-0002 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Old Dominion Onsite, Inc. | 1942001549 | Russell | Revis | [9 empty] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump"] | N/A | [17 empty] | Cleaned effluent filter, RSV and manifold. Checked float and pump operation, walked drain field. System appears to be working well. The drain field trenches have settled significantly, soil should be brought in to bring it back to grade. Water collects in the low spots over the trenches, ultimately causing water to flood the field. This can cause the field to fail prematurely. 0 overrides | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 10/30/2020 | Jan 1 1900 11:30AM
03/13/2020 |  | Routine, Scheduled | 2002-143-0266 | Henrico County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Henrico |  |  |  |  | 1.000000 |  |  | None | Pump | None | None | None | 150.000000 |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump"] |  | None | 20.1 | 6.100000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/21/2020 | 10:11 AM
04/02/2020 |  | Initial Visit | 19-177-1048 | Pulaski County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - New River | KING, WILLIAM M, II | 1942001112 | WILLIAM | KING | 1.000000 | 1000 | Aqua Safe ATU | Septic Tank Only | Gravity | Distribution Box | Aggregate Trench | None | 300.000000 | ["None"] | ["None"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/03/2020 | 05:47 PM
05/06/2020 |  | Follow-Up |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | SES MidAtlantic LLC | 1942001203 | James | Green | 1.000000 |  | EcoPod | none | Gravity | Gravity | Trenches | UV |  | ["Disinfection"] | ["Disinfection"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced UV Bulb & test tube. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/15/2021 | 09:00 AM
03/11/2020 |  | Routine, Scheduled | 099-18-0085 SP | King George County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Ware, Michele P | 1942001165 | Michele | Ware |  |  | Septic Tank Only | Septic Tank Only | None | None | None | None |  |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/12/2020 | 12:12 PM
12/08/2020 |  | RoutineScheduled | 109-14-0120 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1000 | Aqua Klear |  | Pump | Pressure | Drip | Not Applicable |  | [] | [] | NA | Musty | [15 empty] | Inspected | Sludge level-4-6" Sludge in Septic tank.10-12" Sludge in treatment, Clear Effluent on top. Pump tank clear on top 6" fine sludge. Cleaned Effluent filterand spin filter(not very dirty), sprayed B.W. spiders. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12/28/2020 | 05:30 PM
05/28/2020 |  | Follow-Up |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | SES MidAtlantic LLC | 1942001203 | James | Green | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation"] | ["Dispersal System Operation"] | NA | [15 empty] | Will be sent separately | Inspected | 05/12/2020 Drip lines flushed with cleaner. 05/28/2020 Recheck : Good | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/15/2021 | 09:00 AM
12/05/2020 |  | RoutineScheduled | 2086-04-153 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Wastemaster Inc |  | Timothy | Jenkins | 2.000000 |  | PuraFlo | Effluent Filter | Pump | Gravity | Discharge | Chlorination |  | [] | [] |  | Musty | Clear | 76.000000 |  |  | 2.200000 | [12 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12/10/2020 | 02:00 PM
03/31/2020 |  | Routine, Scheduled | 177-06-0594-SWP | Spotsylvania County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Orenco Advantex | None | Pump | Distribution Box | Aggregate Trench |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | [18 empty] | [Comments]: Both Advantex risers are not sealed. Inlet tee is jacked up if blockage occurs will need to be repaired. Pump tank needs pump out. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/27/2020 | 04:14 AM
09/29/2020 |  | RoutineScheduled | SWP-05-62 | King George | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Attached Growth Medium" ,"Control Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Level Sensor Operation"] | ["Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Attached Growth Medium" ,"Effluent Screens" ,"Level Sensor Operation" ,"Control Operation" ,"Distribution Pump Operation"] | YES | [15 empty] | Will be sent separately | Inspected | Few grass roots and septic tank and pump tank wedge lids. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
10/06/2020 |  | Routine/Scheduled | R03-111-0114 | Botetourt | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Alleghany-Roanoke | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Delta Environmental Products, DF Series |  | Gravity | Distribution Box |  | None |  | ["None"] | ["Blower/Compressor/Aerator Operation","Effluent Screens","Sludge/Scum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 10/06/2020 | Jan 1 1900 1:30PM
08/28/2020 |  | RoutineScheduled |  | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - New River | MONTGOMERY SANITATION SERVICES, INC. | 1942001003 | Tim | Conner | 2.000000 | APPROX 2500 GALLONS | WHITEWATER |  | Gravity | Gravity | Trenches | Not Applicable |  | ["on"] | ["on"] | YES | Septic | Discolored | [5 empty] | 08/28/2020 | Sample Chamber | [6 empty] | Attached to this report | Exempt | REPLACED BLOWER | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 09/14/2020 | 12:00 PM
03/24/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | EZ Treat Sandfilter |  |  |  |  | UV Light |  | ["BlowerCompressorAerator Operation","Effluent Screens"] | ["BlowerCompressorAerator Operation","Effluent Screens"] |  | Good | Clear | [15 empty] | [Comments]: Pump Amps 9.30Pump Amps 11.7 ETM 5.95h Cycles 22260Septic Sludge 3" Scum 1"ATU Sludge 3" Scum 0Pump Sludge 1" Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/24/2020 | Jan 1 1900 12:11PM
02/25/2020 |  | Routine, Scheduled |  | Page County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Lord Fairfax | Cubbage, Harrison Lee, II | 1942001021 | Harrison | Cubbage | 1.000000 | 1500 | Septic Tank Only | Biomicrobics MicroFAST | Pump | Drip | Drip Tubing | None |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation"] |  | Musty | Clear | [15 empty] | [Comments]: Pump Settings: Off 2.5Hr On 12.5min ETM-218.64Hr Cycle COunt-2481 Sludge/Scum Accumulations: Comp.1-13"/2" Comp.2-13"/0" Pump Tank-5"/0" | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/01/2020 | 01:05 PM
06/30/2020 |  | Reportable Incident | 2015-143-0147 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Wastemaster Inc |  | Timothy | Jenkins | 2.000000 |  | ATU |  | Pump | Pressure | Drip |  |  | ["Other"] | ["Other"] | [18 empty] | In for alarm. Found water in pump tank junction box. Remade connection and drained water from box. Pump and aerator now running in auto. Found water coming up in yard when pump is on indicative of a broken pipe which owner will repair. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 08/27/2020 | 12:30 PM
08/05/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/27/2021 | 01:26 PM
10/28/2020 |  | Routine/Scheduled | 136-10-0219 | Gloucester | This AOSS should now return to normal function after having provided the above state routine maintenance | Approved | EHD - Three Rivers | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | Clearstream |  | Pump | Drip | Drip Tubing | UV Light | 450.000000 |  | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | Pungent | Discolored | [15 empty] | Routine Service Trash Tank - normal operating level Aeration Tank - Air compressor failed - requires replacement - Pump Tank - normal operating level - pump serviced, float sensors & controls operating properly. Drip Field - headworks and spinfilter serviced. 11/24/2020 - Air compressor and diffuser replaced. | This AOSS should now return to normal function after having provided the above state routine maintenance |  | 11/25/2020 | 08:00 AM
05/22/2020 | Alternative | RoutineScheduled | 115-98-0121 | Campbell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Taylor's Septic Service | 1942001028 | Penny | Taylor | 1.000000 | 1000 | Septic Tank | Clearstream | Pump | Gravity | Trenches | Not Applicable | 450.000000 | ["BlowerCompressorAerator Operation","Auxiliary Filter"] | ["BlowerCompressorAerator Operation","Auxiliary Filter","SludgeScum Accumulation"] |  | Musty | Clear | [5 empty] | 05/22/2020 | [8 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 05/22/2020 | 10:00 AM
02/28/2020 |  | Follow-Up |  | Fairfax County | This AOSS should now return to normal function after having provided the above stated routine maintenance. | Paid | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green | [9 empty] | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | [18 empty] | [Comments]: Installed new compressor. | This AOSS should now return to normal function after having provided the above stated routine maintenance. |  | 02/28/2020 | Jan 1 1900 4:00PM
12/21/2020 |  | Follow-Up | 98-197-A2 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | Wise Health Dept |  | Rodney | Neece | 1.000000 |  | ATU |  | Gravity | Gravity | Drip | Chlorination |  |  |  |  | Musty | Clear | 6.500000 | 5.000000 | [14 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  |  | 12:00 AM
06/01/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/27/2021 | 01:26 PM
05/04/2020 | Alternative | RoutineScheduled | 175-05-0011 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Prince William | McKim Construction | 1942001330 | Michelle | McKim | 1.000000 |  | 2000 |  | Pump | Pressure | Mound | Not Applicable |  | [] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Dispersal System Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NA | [18 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 10/24/2020 | 04:40 PM
09/04/2020 |  | RoutineScheduled |  | Shenandoah | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation"] | ["BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/26/2021 | 09:04 AM
09/02/2020 |  | RoutineScheduled | 153-STS-20160 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Wastemaster Inc |  | Timothy | Jenkins | 2.000000 |  | Polishing Sand Filter | Dosing Siphon | Pump | Gravity | Discharge | Chlorination |  | [] | [] | [18 empty] | No Discharge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 09/11/2020 | 12:20 PM
02/07/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS should now return to normal function after having provided the above stated routine maintenance. | Paid | EHD - Fairfax | SEAMON, CHARLIE L | 1942001108 | CHARLIE | SEAMON |  |  | Septic Tank Only | Microfast | Pump | Manifold | Drip Tubing | None |  | ["BlowerCompressorAerator Operation","Dispersal System Operation"] | ["BlowerCompressorAerator Operation","Dispersal System Operation"] | [12 empty] | 350.000000 | [5 empty] | [Comments]: Performance Inspection and Fecal Sample: Microfast to American Drip. Septic-6"sludge 4"scum/ Microfast-4"sludge/ Pump Tank-0"sludge. Z1 cnt-206 ff-31/ Z2 cnt-198 ff-31/ Z3 cnt-194 ff-31.Pump cnt-691 ETM-151h 25m/Peak-14 ETM-0/ High-18 ETM-0 Watermeter-66,811.88 Blower air filter cleaned. | This AOSS should now return to normal function after having provided the above stated routine maintenance. |  | 02/25/2020 | Jan 1 1900 3:31PM
10/22/2020 |  |  |  | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Pressure | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation","Attached Growth Medium","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation"] | NA | [17 empty] | Septic-12"sludge 4"scum/ Microfast-20"sludge (Requires cleaning and pump out) Pump tank-0"sludge/ Blower air filter cleaned/ No breakout or spongy areas on the drip field/ Counts: Z1-1495 ff-62/ Z2-1495 ff-61/ Pump-3111 ETM-828h 8m/ Peak-11 ETM-65h 9m/ High-26 ETM-0/ Water meter-194934.29 | This AOSS should now return to normal function after having provided the above state routine maintenance. |  |  | 12:00 AM
03/17/2020 |  | Routine, Scheduled |  | Prince William County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Biomicrobics MicroFAST |  | Pump | Drip | Drip Tubing | None |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] |  | Good | Good | [15 empty] | [Comments]: Spin filter cleaned.Pump Amps 9.70 ETM 1336 Cycles 8614Water Meter Reading 279950Septic Sludge 4" Scum 2"ATU Sludge 14" Scum 0Pump Sludge 4" Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/17/2020 | 12:30 PM
10/06/2020 |  | RoutineScheduled | 107-18-0244 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter | [9 empty] | ["None"] | ["None"] |  | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 06/02/2021 | 12:00 AM
04/22/2020 |  | Reportable Incident |  | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU | [6 empty] | ["Blower/Compressor/Aerator Operation","Control Operation"] | ["Blower/Compressor/Aerator Operation","Control Operation"] | N/A | [17 empty] | Replaced aerator | This AOSS should now return to normal function after having provided the above state routine maintenance |  | 04/22/2020 | Jan 1 1900 12:30PM
04/07/2020 |  | Routine, Scheduled | 07-184-5004 | Scott County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Lenowisco | DEEL, DENNY M | 1942001097 | DENNY | DEEL |  |  | Norweco Singulair ATU | None | Gravity | None | Alternative Discharge | Chlorine | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens"] |  | Musty | Clear | [5 empty] | 04/07/2020 | [9 empty] | [Comments]: 5 Blue crystals, loaner, new control panel, brush filter | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/08/2020 | Jan 1 1900 8:50AM
03/31/2020 |  | Routine, Scheduled |  | Warren County | This AOSS should now return to normal function after having provided the above stated routine maintenance. | Paid | EHD - Lord Fairfax | Cubbage, Harrison Lee, II | 1942001021 | Harrison | Cubbage | 1.000000 | 1500 | Septic Tank Only | Biomicrobics MicroFAST | Pump | Drip | Drip Tubing | None |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation"] |  | Musty | Clear | [15 empty] | [Comments]: Replaced pressure gauge Pump Settings: Off 2.5Hr On 12.5min ETM-533.64Hr Cycle COunt-2135 Sludge/Scum Accumulations: COmp.1-15"/2" Comp.2-13"/0" Pump Tank-3"/0" | This AOSS should now return to normal function after having provided the above stated routine maintenance. |  | 04/06/2020 | 03:12 PM
10/05/2020 |  | Routine/Scheduled | 11-163-0026 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chickahominy | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. |  |  | Clearstream ATU |  | Pump |  |  |  |  | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 10/05/2020 | Jan 1 1900 3:00AM
01/14/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green | [9 empty] | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] |  | Good | Good | [15 empty] | [Comments]: Pump 1 Amps 12.30 ETM 8h 50m Cycles 262Pump 2 Amps 12.15 ETM 8h 33m Cycles 253Septic Sludge 9" Scum 10"ATU Sludge 12" Scum 0Pump Sludge 0 Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/14/2020 | Jan 1 1900 2:11PM
08/31/2020 |  | Reportable Incident |  | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU | [6 empty] | ["Blower/Compressor/Aerator Operation","Control Operation"] | ["Blower/Compressor/Aerator Operation","Control Operation"] | N/A | [17 empty] | Replaced aerator | This AOSS should now return to normal function after having provided the above state routine maintenance |  | 08/31/2020 | Jan 1 1900 7:30PM
05/01/2020 |  | RoutineScheduled | 101-11-0031 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark | [9 empty] | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 07:10 AM
11/24/2020 |  | RoutineScheduled | 08-113-162 | Buchanan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
07/20/2020 |  | RoutineScheduled | 09-142-0240 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Drainfield Solutions | 2705163102 | Michele | Ware | [9 empty] | [] | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Effluent Screens","Distribution Pump Operation","Recirculation Pump","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
02/18/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Paid | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Puraflo |  |  |  |  | None |  | ["Effluent Screens"] | ["Effluent Screens"] | [18 empty] | [Comments]: #2 Pump Z140 is bad. Strongly recommend BOD sampling on Puraflo modules.Pump 1 Amps 12.43 ETM 49738h Cycles 25847Pump 2 Amps 0.00 ETM 49527h Cycles 25748Septic Sludge 9" Scum 6"Pump Sludge 2" Scum 0 | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 02/18/2020 | Jan 1 1900 2:55PM
10/21/2020 |  | RoutineScheduled |  | Shenandoah | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Bio Barrier | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/26/2021 | 09:04 AM
03/31/2020 |  | Routine, Scheduled | 12-184-060 | Scott County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Lenowisco | DEEL, DENNY M | 1942001097 | DENNY | DEEL |  |  | None | None | Gravity | None | Alternative Discharge | None | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation"] |  | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/08/2020 | Jan 1 1900 11:16AM
06/11/2020 |  | Follow-Up | -STS-86641 | Spotsylvania | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [9 empty] | 320.000000 | [5 empty] | Will be sent separately | Inspected | BOD collected; effluent 320 mg/L, influent 366 mg/L | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
05/07/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | SES MidAtlantic LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/15/2021 | 09:00 AM
09/30/2020 |  | RoutineScheduled | VAG401044 | Rockingham | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Central Shenandoah | Onsite Wastewater Services - May Supply | 1942001022 | Sara | Tusing |  |  | Multiflo FTB | none | Gravity | Gravity |  | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | inspected DKS | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/28/2021 | 05:41 AM
07/06/2020 | Alternative | Reportable Incident | -STS-15916 | Suffolk | This AOSS should now return to normal function after having provided the above state routine maintenance | Approved | EHD - Western Tidewater | Miller's Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | None | None | Gravity | Distribution Box | Aggregate Trench | None | 450.000000 | ["Dispersal System Operation"] | ["Dispersal System Operation"] | N/A | [17 empty] | Replaced failed / damaged distribution box - spliced header and conveyance lines - confirmed six (6) absorption laterals accepting effluent. | This AOSS should now return to normal function after having provided the above state routine maintenance |  | 07/07/2020 | Dec 30 1899 12:00PM
09/16/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | SES MidAtlantic LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/15/2021 | 09:00 AM
03/11/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS should now return to normal function after having provided the above stated routine maintenance. | Paid | EHD - Fairfax | MCKIM, STEPHEN E | 1934000043 | STEPHEN | MCKIM |  |  | Septic Tank Only | Septic Tank Only | None | None | None | None | [21 empty] | [Pumpout Comments]: Microfast tank septic and atu sides pumped out | This AOSS should now return to normal function after having provided the above stated routine maintenance. |  | 03/12/2020 | Jan 1 1900 9:56AM
02/20/2020 |  | Routine, Scheduled |  | Prince George County | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Paid | EHD - Crater | Madison Environmental LLC | 1934 000061 | Larry | Madison, Jr. |  |  | Ecoflo |  | Pump |  |  |  |  | ["Attached Growth Medium","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | [Comments]: Peat moss needs replacement. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 02/20/2020 | Jan 1 1900 10:30AM
04/15/2020 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Pump |  |  |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Recirculation Pump","Sludge/Scum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Recirculation Pump","Sludge/Scum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/15/2020 | Jan 1 1900 2:30PM
08/14/2020 |  | RoutineScheduled | 099-12-0042-SR | King George | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | ["Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Puraflo tank in high level due to failed pump. Replaced pump and check valve. New pump running at 11.88 amps, 62.5 gpm. Infiltration observed in discharge pump tank at inlet and outlet pipe penetrations, wedge lid, and riser joint. Roots in tank appear to be coming in through the wall. Need to excavate end wall, cut off roots and seal from outside. Other tanks have evidence of infiltration, but could not be confirmed today. Removed roots from d-box as best as possible and added a root killer. Cut roots growing into end Puraflo pod and removed as best as possible. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
09/01/2020 |  | RoutineScheduled | 177-19-0100-SP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NO | [15 empty] | Will be sent separately | Inspected | The base of both risers on the pump tank are leaking. It is also possible the top seam on this tank is leaking. Additionally settling has occurred around the tanks. We recommend contacting your builder and asking the to have the installer (New Day Construction) make repairs. | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 |  | 04/09/2021 | 03:25 PM
05/12/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Gravity | Gravity | Pad | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/14/2021 | 04:27 PM
03/11/2020 |  | Routine, Scheduled | 11-197-092 | Wise County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Lenowisco | DEEL, DENNY M | 1942001097 | DENNY | DEEL |  |  | Aqua Klear | None | Gravity | Distribution Box | Aggregate Bed | None | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation"] |  | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/20/2020 | Jan 1 1900 1:41PM
06/24/2020 |  | Reportable Incident | SD-02-51 | Fauquier | This AOSS should now return to normal function after having provided the above state routine maintenance | Approved | EHD - Rappahannock-Rapidan | SES Mid Atlantic | 1942001203 | Michael | Green | [9 empty] | ["Attached Growth Medium","Dispersal System Operation"] | ["Attached Growth Medium","Dispersal System Operation"] | [18 empty] | Replaced peat in (5) Puraflo modules. | This AOSS should now return to normal function after having provided the above state routine maintenance |  | 06/24/2020 | 04:00 PM
03/04/2020 |  | Follow-Up |  | Fairfax County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Fairfax | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Orenco Advantex | Orenco Advantex | Pump | Distribution Box | [15 empty] | 13.000000 | [8 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/12/2020 | Jan 1 1900 6:05AM
09/18/2020 |  |  |  | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | McKim Construction | 1942001330 | Michelle | McKim | 3.000000 |  |  |  | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 11/13/2020 | Jan 1 1900 10:30AM
03/12/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Fairfax | BLEVINS, JOEL R, SR | 1934000415 | JOEL | BLEVINS |  |  | Microfast | Septic Tank Only | None | None | None | None |  | ["None"] | ["None"] | [8 empty] | 03/12/2020 | pump tank | 10.000000 | [5 empty] | Attached to this report |  | [Comments]: The compressor is strong and the pad is dry. No build up in the tank. Cleaned the air filter and took water sample | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/23/2020 | Jan 1 1900 10:16AM
02/10/2020 |  | Initial Visit |  | Page County | This AOSS should now return to normal function after having provided the above stated routine maintenance. | Paid | EHD - Lord Fairfax | SEAL, CHARLES K | 1934000144 | CHARLES | SEAL | 1.000000 |  | Septic Tank Only | Microfast | Pump | Manifold | Drip Tubing | None |  | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | [18 empty] | [Comments]: replaced blower | This AOSS should now return to normal function after having provided the above stated routine maintenance. |  | 03/11/2020 | 05:14 PM
05/12/2020 |  | RoutineScheduled | 109-12-0098 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 2.000000 | 2500 | Advantex AX25RT |  | Pump | Gravity | Trenches | Not Applicable |  | ["Dispersal System Operation","Recirculation Pump"] | ["Attached Growth Medium","Recirculation Pump"] | NA | Musty | [15 empty] | Inspected | System was recently pump out, sludge level not checked. Weak Spray pattern upon arrival, Pulled recirc pump and cleaned, flushed sprayers and manifold, Ran in test mode, sprayed off media, flushed recirc pump till clean, All good no alarms, Spray pattern normal after cleaning. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 05/15/2020 | 09:30 AM
04/14/2020 |  | RoutineScheduled | 15-192-042 | Tazewell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. |  | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Effluent Screens"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
02/05/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Fairfax | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Puraflo | None | Pump | Distribution Box | Aggregate Trench |  |  | ["Attached Growth Medium","Effluent Screens"] | ["Attached Growth Medium","Effluent Screens"] | [10 empty] | 58.000000 | [7 empty] | [Comments]: BOD: 58We recommend replacing the concrete lid on the pump tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/02/2020 | Jan 1 1900 11:52AM
02/24/2020 |  | Routine, Scheduled | SD-04-111 | Culpeper County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | None | None | Pump |  |  | Chlorine |  | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","None"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection","None"] | [10 empty] | 14.000000 |  | 158.500000 | 3.000000 |  |  |  |  | [Comments]: DO: 9.08The sand in the sand filter was dark and clumpy on top. We recommend reminding users not to put chemicals in the septic system. We also recommend raking the sand to break this up.Two sample chambers are broken and the chlorine chamber lid is missing. We recommend replacing the lid and one sample chamber and installing 4" PVC in place of the other damaged sample chamber. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/06/2020 | 02:45 PM
04/23/2020 |  | RoutineScheduled | 179-13-0188-SP | Stafford | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Disinfection" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Distribution Pump Operation" ,"Recirculation Pump"] | NA | [15 empty] | Will be sent separately | Inspected | The pump line is broken on the outside of the Advantex RT tank. We recommend excavating by machine & repairing the pump line. | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 |  | 04/09/2021 | 03:25 PM
04/15/2020 |  | Pump-Out Only |  | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex | [8 empty] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/15/2020 | Jan 1 1900 8:00AM
11/03/2020 |  | Follow-Up |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Eco Virginia | 1942001235 | William | Poindexter | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium"] | ["Attached Growth Medium"] | NA | [15 empty] | Will be sent separately | Inspected | Peat was replaced in the Puraflo (not Glendon) modules | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 |  | 06/03/2021 | 05:53 AM
02/04/2020 |  | Routine, Scheduled |  | Greene County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Blue Ridge | ARNOLD, ARCHIE G | 1942001291 | ARCHIE | ARNOLD |  |  | Septic Tank Only | Septic Tank Only | None | None | None | None | 200.000000 | ["Auxiliary Filter","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] |  | Earthy | Clear | [15 empty] | [Comments]: O&M: Flushed drip lines. Cleaned effluent filter. 8" Sludge in septic tank, 16" in other tank. Performed typical maintenance. System working as intended. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/12/2020 | 03:27 PM
02/24/2020 |  | Follow-Up | {FIPSCode}-STS-28233 | Frederick County | This AOSS should now return to normal function after having provided the above stated routine maintenance. | Approved | EHD - Lord Fairfax | Ferguson, Jeremy | 1942001008 | Jeremy | Ferguson | 1.000000 | 1500 | Puraflo | None | Pump | Distribution Box | Aggregate Trench | None |  | ["Dispersal System Operation"] | ["Attached Growth Medium","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | [Comments]: On 2/4/20 the initial comprehensive inspection was completed. During the inspection the drainfield lines were inspected by use of an underground camera and found to be 2 lines collapsed. On 2/24/20 the sections were dug up and repaired the system is now operating as intended. Photos are attached from repair. VENIS File Names: 6853A - Septic System Repairs - Photo Report.pdf, ATTUOKVU.pdf | This AOSS should now return to normal function after having provided the above stated routine maintenance. |  | 02/26/2020 | 02:48 PM
10/05/2020 |  | Routine/Scheduled | 2016-143-0137 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Old Dominion Onsite, Inc. | 1942001549 | Russell | Revis | [9 empty] | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump"] | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump"] | N/A | [17 empty] | Flushed drip field, cleaned spin filter, RSV and effluent filter. Flushed manifold. UV bulb inspected and working well. System appears to be functioning properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 10/05/2020 | 10:10 AM
10/26/2020 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintanence requirements | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Gravity | Gravity |  | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | A inspection on a conventional gravity septic system.. The state requires that all conventional septic tanks must be pumped out EVERY 5 years and filed with the state and county. There is no clean outs. The pvc sewer line was camera snaked and was clear. The septic tank lid was dug it was 10" under the ground was pumped out there was no cracks or leaks seen at that time. The pvc conveyance line was not able to be camera snaked about 2 feet out side of tank the pipe looks like it has broken and settled. This will need to be fixed. The The concrete splitter and both 8 port concrete d-boxes appear to be holding the effluent at the proper level but all 3 boxes are soft and were full of grease and sludge. No way of determining how long boxes will last. Tried to camera snake the header lines they were full of sludge and water. Probed drain field it was dry. T this time the septic system is not in working condition. The header lines need to be jetted out to get the sludge out of them. All 3 d-boxes need to be cleaned out of the grease and sludge. the conveyance line needs dug up and fixed. | This AOSS is not functioning as designed or in accordance with the performance/maintanence requirements |  | 04/14/2021 | 04:27 PM
11/06/2020 |  | Routine/Scheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | POWELLS PLUMBING, INC. | 1942001036 | Kurt | Holthaus | 1.000000 | 1000 |  |  | Pump | Manifold | Aggregate Trench |  | 375.000000 | ["Effluent Screens"] | ["Effluent Screens"] | N/A | [17 empty] | Annual Inspection - Serviced effluent screen(s). | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 11/17/2020 | 10:04 AM
05/01/2020 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Eco Virginia | 1942001235 | William | Poindexter | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 |  | 06/03/2021 | 05:53 AM
05/08/2020 |  | RoutineScheduled | 175-14-0302 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | [9 empty] | ["SludgeScum Accumulation"] | ["SludgeScum Accumulation"] | [18 empty] | Septic/ATU had 12" sludge and 0" scum ATU had 14" sludge and required pump out and cleaning of media which occurred May 11, 2020. Cleaned air filter for blower. Registers in control panel were Hand-88 H/L-183 Override-163 Pump starts-8751 Pump run-974 W/M-0351,759 | This AOSS should now return to normal function after having provided the above state routine maintenance. |  |  | 12:00 AM
11/06/2020 |  | Reportable Incident | 175-15-0036 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green | [9 empty] | ["Blower/Compressor/Aerator Operation"] | ["Blower/Compressor/Aerator Operation"] | [18 empty] | Installed new MicroFast compressor. | This AOSS should now return to normal function after having provided the above state routine maintenance |  | 11/06/2020 | 04:00 PM
07/13/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Payment | EHD - Loudoun | Great Falls Septic Service, Inc | 1942001301 | Josh | Hott | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/27/2021 | 11:51 AM
04/15/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | SES MidAtlantic LLC | 1942001203 | James | Green | 2.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/15/2021 | 09:00 AM
08/12/2020 |  | RoutineScheduled | 175-14-0130 | Prince William | This AOSS is not functioning as designed or in accordance with the performance/Maintenance requirements | Approved | EHD - Prince William | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter" ,"Distribution Pump Operation"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter" ,"Distribution Pump Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Property Sale/Annual Inspection. The normally closed solenoid for zone 1 is not working, and the meter is not working. These should be replaced to confirm the system is dosing property. | This AOSS is not functioning as designed or in accordance with the performance/Maintenance requirements |  | 04/09/2021 | 03:25 PM
04/09/2020 |  | Routine, Scheduled |  | Prince William County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Prince William | SEAMON, CHARLIE L | 1942001108 | CHARLIE | SEAMON |  |  | Septic Tank Only | Microfast | Pump | Distribution Box | Aggregate Trench | None |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | [18 empty] | [Comments]: Performance Inspection: Microfast to Drainfield. Septic-6"sludge 2"scum/ Microfast-8"sludge/ Pump tank-0"sludge. No pump out required at this time. Blower air filter cleaned. Counts:Peak-0 (n/a) / High-22/ Pump-1346 ETM-139h 4m No breakout or spongy areas on the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/16/2020 | 06:24 AM
10/07/2020 |  | RoutineScheduled | SD-11-263 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Soils, Inc. | 1942001004 | Markham | Smith | 2.000000 | 1500 | PuroFlo |  | Pump | Gravity | Pad |  | 52.200000 | [] | ["Attached Growth Medium","Control Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 10/09/2020 | 12:00 AM
06/11/2020 |  | Routine/Scheduled |  | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump | Distribution Box |  | UV Light |  | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  | 3.4 | 6.430000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 06/11/2020 | Jan 1 1900 4:30PM
04/23/2020 |  | RoutineScheduled | 179-15-0216-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Effluent Screens" ,"Recirculation Pump" ,"Distribution Pump Operation"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 |  | 04/09/2021 | 03:25 PM
07/10/2020 |  | RoutineScheduled |  | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 2705051738 | Joshua | Hott |  |  | Septic | Puraflo | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
05/12/2020 |  | RoutineScheduled | 06-142-0552 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1500 | Orenco Advantex | Orenco Advantex | Pump | Gravity | Trenches | Not Applicable |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump","Septic Tank Baffles","Sludge/Scum Accumulation"] | NA | [17 empty] | Septic Tank was not found; Recirculation Floats have exceeded their life expectancy, and there was evidence of ground water leaking into the Tank; Discharge Pump and Floats have exceeded their life expectancy; the Motherboard in the Control Panel was not functioning properly | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 05/26/2020 | Jan 1 1900 3:18PM
05/06/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim |  |  | Norweco Singulair ATU | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | NORWECO TANK NEEDS PUMPED OUT | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 |  | 04/14/2021 | 04:27 PM
03/06/2020 |  | Routine, Scheduled |  | Loudoun County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | None | Pump | Distribution Box | Aggregate Trench | [23 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/16/2020 | 11:28 AM
02/26/2020 |  | Routine, Scheduled | {FIPSCode}-STS-1948 | Dickenson County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Cumberland Plateau | DEEL, DENNY M | 1942001097 | DENNY | DEEL |  |  | Norweco Singulair ATU | None | Gravity | None | Alternative Discharge | Chlorine |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens"] |  | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/16/2020 | Jan 1 1900 11:08AM
02/12/2020 | Alternative | Reportable Incident | 115-14-0300 | Campbell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | WAUGH, IAIN C | 1942001512 | IAIN | WAUGH | 1.000000 | 1500 | Septic Tank | Orenco Advantex | Gravity | Gravity | Trenches | Not Applicable |  | ["Dispersal System Operation","Recirculation Pump"] | ["Dispersal System Operation","Recirculation Pump"] | [18 empty] | [Pumpout Comments]: Not needed at this time [Comments]: Recirculation pump outlet pipe had broken off from the connection leaving the pump tank. It was leaking raw septic onto the ground. Owner smelled septic & reported it to us. We found the broken pipe upon testing the system and repaired it, it sits above grade & may have been bumped into because it is covered in mulch & invisible. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 02/13/2020 | 03:54 PM
09/11/2020 |  |  |  | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | McKim Construction | 1942001330 | Michelle | McKim | 2.000000 |  |  |  | Pump | Pressure | Drip | UV |  | [] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Auxiliary Filter","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","Recirculation Pump","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 11/13/2020 | 12:00 AM
06/29/2020 |  | RoutineScheduled | 099-06-0253-SWP | King George | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | none | none | Pump | Gravity | Pad | Not Applicable |  | ["Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Attached Growth Medium"] | ["Effluent Screens" ,"Attached Growth Medium" ,"Distribution Pump Operation" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | YES | [15 empty] | Will be sent separately | Inspected | Septic tank needs to be pumped out. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
10/22/2020 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Gravity | Gravity |  | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 |  | 04/14/2021 | 04:27 PM
09/23/2020 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Gravity | Gravity |  | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Septc inspection on a conventional pump system. The state requires that all conventional septic tanks be pumped out EVERY 5 years and filed with the state and county . The exterior control panel is a time dose. There are 2 pvc clean outs near the house. The septic tank was pumped out and the filter was cleaned. There is a plastic riser on the outlet side. The pump tank, pump, floats and force main were inspected. The drain field was probed and dry. At time of inspection what was visually inspected was in working condition | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 |  | 04/14/2021 | 04:27 PM
04/02/2020 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump | Distribution Box |  | UV Light |  | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  | 8.13 | 8.300000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/02/2020 | Jan 1 1900 12:30PM
09/16/2020 |  | RoutineScheduled |  | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Ashleys Septic Service | 1930332 | Shane | Majewski | 1.000000 | 1500 |  |  |  | Gravity | Drip | Not Applicable |  | ["None"] | ["None"] | NA | Septic | Clear | 657.000000 | 7.100000 | [13 empty] | Micro fast pressure driip system | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 10/21/2020 | Jan 1 1900 12:00AM
03/04/2020 |  | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | 1000.000000 | 1000 | [7 empty] | ["None"] | ["None"] | YES | [16 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 07/28/2020 | 12:25 PM
05/26/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/14/2021 | 04:27 PM
07/28/2020 |  | RoutineScheduled | 10-173-049 | Prince Edward | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Piedmont | Taylor's Septic Service, Inc | 1942001028 | Penny | Taylor | 1.000000 | 1000 | Norweco |  | Pump | Gravity | Trenches | Not Applicable | 350.000000 | ["Effluent Screens","SludgeScum Accumulation"] | ["Effluent Screens","Control Operation","BlowerCompressorAerator Operation","SludgeScum Accumulation","Level Sensor Operation"] | YES | Musty | Clear | [14 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
09/21/2020 |  | RoutineScheduled | 069-18-0375 | Frederick | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage |  |  | none | none | Gravity | Gravity |  | Not Applicable |  | ["Attached Growth Medium"] | ["Attached Growth Medium"] | NA | [15 empty] | Will be sent separately | Inspected | Comp.1 Sludge/Scum- 12"/0" Comp.2- 15"/6" | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/26/2021 | 09:04 AM
08/27/2020 |  | RoutineScheduled | SWT-01-352 | Spotsylvania | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Attached Growth Medium" ,"Auxiliary Filter" ,"Effluent Screens" ,"Dispersal System Operation"] | ["Attached Growth Medium" ,"Auxiliary Filter" ,"Dispersal System Operation" ,"Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/09/2021 | 03:25 PM
02/19/2020 |  | Routine, Scheduled |  | Loudoun County | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Paid | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim |  |  | Delta Environmental Products, DF Series | None | Gravity | Distribution Box | Gravel-Less Trench | [22 empty] | [Comments]: Atu tank needs pumped | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 04/12/2020 | 02:21 PM
03/26/2020 |  | RoutineScheduled | 171-05-1013 | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Greenway Engineering | 1942001008 | Jeremy | Ferguson | 1.000000 | 1500 | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 09:15 AM
05/07/2020 |  | Follow-Up | 179-12-0057-SWP | Stafford | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Clearstream | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [9 empty] | 7.000000 | [5 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
05/01/2020 |  | RoutineScheduled |  | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Rappahannock-Rapidan | Soils, Inc. | 1940001392 | Markham | Smith | 2.000000 | 1500 | MicroFAST 0.75 |  | Gravity | Gravity | Pad | Not Applicable |  | [] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Effluent Screens","SludgeScum Accumulation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 07/13/2020 | 12:00 AM
09/18/2020 |  | Routine, Scheduled | 175-12-0508 | Prince William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | EcoPod |  | Pump | Drip | Drip Tubing | None |  | ["Blower/Compressor/Aerator Operation","Level Sensor (Float) Operation"] | ["Blower/Compressor/Aerator Operation"] |  | Acceptable | Clear | [15 empty] | Spin filter cleaned. Pump Amps 6.34 ETM 1193 hrs Cycles 11740 Water Meter Reading 360720 Septic Sludge 12" Scum 2" ATU Sludge 11" Scum 0 Pump Sludge 3" Scum 0 Needs timer enable float. Yard box lid damaged from lawn mower. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 09/18/2020 | 06:45 PM
10/05/2020 |  | Routine/Scheduled |  | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump | Manifold | Elevated Sand Mound | UV Light |  | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  |  | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 10/05/2020 | Jan 1 1900 2:30PM
07/20/2020 |  | RoutineScheduled | 124-STS-2379 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Lord Fairfax | [6 empty] | tank only | FAST | Gravity | Pressure | Trenches | Not Applicable |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 07/20/2020 | 12:00 AM
02/06/2020 |  | Routine, Scheduled | 179-14-0018-SP | Stafford County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Orenco Advantex | None | Pump | Distribution Box | Aggregate Trench |  |  | ["Attached Growth Medium","Distribution Pump Operation","Effluent Screens","Recirculation Pump"] | ["Attached Growth Medium","Distribution Pump Operation","Effluent Screens","Recirculation Pump"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/02/2020 | 11:52 AM
01/06/2020 |  | Routine, Scheduled | SD-14-98 | Fauquier County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | EcoPod | None | Pump | Drip | Drip Tubing |  |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Distribution Pump Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Distribution Pump Operation"] | [18 empty] | [Comments]: We recommend pumping the Pump Tank due to solids accumulation. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/04/2020 | 07:46 AM
01/09/2020 |  | Routine, Scheduled | 03-100-0003 | Accomack County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Eastern Shore | DUER, PETE C | 1942001051 | PETE | DUER | 2.000000 | 2000 | Septic Tank Only | Microfast | Pump | None | None | None |  | ["None"] | ["None"] | [18 empty] | [Comments]: Aoss Inspection | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/10/2020 | 02:54 PM
03/03/2020 |  | Routine, Scheduled |  | Prince William County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Biomicrobics MicroFAST |  | Pump | Drip | Drip Tubing | UV Light |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] |  | Good | Clear | [15 empty] | [Comments]: Spin filter cleaned.Pump Amps 10.70 ETM 134h Cycles 1474Water Meter Reading 87500Septic Sludge 6" Scum 5"ATU Sludge 9" Scum 0Pump Sludge 0 Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/03/2020 | 12:40 PM
08/13/2020 |  | RoutineScheduled | 017-STS-333411 | Bath | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1500 | EZ Treat |  | Pump | Pressure | Trenches | Not Applicable |  | ["None"] | ["None"] | NA | [7 empty] | 08/13/2020 | Pump Chamber | 13.000000 |  |  | 10.500000 |  |  |  |  | Following discussion with EZ Treat representitive, it was determined that the elevated results were due to the recirculating pump operating more often than necessary for the amount of usage. Upon next visit, the timers will be set accordingly. Lids secured | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
07/01/2020 |  | RoutineScheduled | 175-13-0031 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Prince William | Dominion Septic, Inc | 1942001125 | Tom | Jackson |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Level Sensor Operation" ,"Recirculation Pump"] | ["Level Sensor Operation" ,"Recirculation Pump"] | NA | [15 empty] | Will be sent separately | Inspected | Annual inspection. In the past 30 days, the discharge pump averaged 2.2 cycles per day at 2.1 minutes per cycle. Cleaned intake on recirc pump. Recirc tank may need pumping by next year. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
06/05/2020 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Ace Contracting Services Inc | 1942001120 | Lawrence | Fellenz Jr. | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected | Septic Tank Lid Cracked Is Being Replaced. | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 |  | 06/29/2021 | 10:39 PM
11/18/2020 |  | Follow-Up | SD-97-240 | Culpeper | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Rappahannock-Rapidan | Wastemaster Inc |  | Timothy | Jenkins | 2.000000 |  | Recirculating Sand Filter |  | Pump | Gravity | Discharge |  |  | [] | [] | [18 empty] | In to replace conduit from tank to control panel. Cannot pull wired through conduit. Installed new conduit and tested. Found 1 bad float. Replaced. Tested all okay. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12/18/2020 | 11:30 AM
09/08/2020 | Alternative | RoutineScheduled | 40534 | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | [13 empty] | ["Attached Growth Medium"] | ["Attached Growth Medium"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 09/08/2020 | 12:00 AM
11/20/2020 |  | RoutineScheduled | 108-17-0013 | Bath | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1000 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [17 empty] | The System didn't need to be pumped. Cleaned septic tank filter. sprayed off textile sheets. Pulled both recirculating and discharge pumps and cleaned effluent screens. Controls were functioning as designed. There were no visible leaks in leech field. The lids were secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12/28/2020 | 09:36 PM
06/10/2020 |  | RoutineScheduled | 09-125-142 | Dickenson | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Effluent Screens","Control Operation"] | ["BlowerCompressorAerator Operation","Disinfection","Effluent Screens","Control Operation"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
06/05/2020 |  |  | 139-05-0227 | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | SEAL’S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | tank only | FAST | Pump | Pressure | Drip |  |  | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 06/05/2020 | 12:00 AM
02/14/2020 |  | Routine, Scheduled |  | Prince William County | This AOSS should now return to normal function after having provided the above stated routine maintenance. | Paid | EHD - Prince William | SEAMON, CHARLIE L | 1942001108 | CHARLIE | SEAMON |  |  | Septic Tank Only | Microfast | Pump | Distribution Box | Aggregate Trench | None |  | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | [18 empty] | [Comments]: Performance Inspection: Microfast to Drainfield. Septic-4"sludge 0"scum/Microfast-2"sludge. No pump out needed at this time. Replaced faulty blower (Fuji VFC200P-5T) and faulty alarm buzzer. Blower air filter cleaned. Pump counts-3029 ETM-262.10 Pump @ 51.4gpm. No break out or spongy areas on the drainfield. | This AOSS should now return to normal function after having provided the above stated routine maintenance. |  | 03/06/2020 | 03:55 PM
09/16/2020 |  | Reportable Incident | 177-08-0240-SWP | Spotsylvania | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation" ,"Distribution Pump Operation"] | ["Auxiliary Filter" ,"Control Operation" ,"Distribution Pump Operation" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | On site for high level alarm. Discovered blower not running and atu panel non-responsive. Power was going in, but not through the motherboard. Panel was obsolete. Replaced with latest panel from Biomicrobics. Blower started running again, but recirc trough was not visible unless blower was turned off. Used camera inside atu to determine that airlift was broken and media plugged. Drip rate was slow due to damaged solenoid tubing in headworks. Drip rate back to normal after replacing vent tubing and cleaning disc filters. Repair proposal will be sent to replace airlift and clean media. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
01/09/2020 |  | Routine, Scheduled | 177-07-0214-ST | Spotsylvania County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 2.000000 |  | Enviro-Flo | Orenco Advantex | Pump | Distribution Box | Aggregate Trench |  |  | ["Attached Growth Medium","BlowerCompressorAerator Operation","Effluent Screens","None"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Effluent Screens","None"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/04/2020 | 07:46 AM
12/16/2020 | Alternative | Initial Visit | 136-16-0288 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | Owner called due to water being out by the tanks. Serviced system. Checked the panel & floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. Replaced the P-20 pump, replaced the buzzer, and replaced the alarm light bulb. Pumped out the pump tank and trash out of the Clearstream. There is wetness on the drainfield - have had alot of rain - once it dries up need to keep an eye on the drainfield. The timer is set to 2 minutes every 1 hour. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12/16/2020 | 12:00 PM
06/24/2020 |  | Follow-Up |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Replaced septic tank plastic lid, the pump tank concrete lid and installed new shocks on the advantex lid | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/14/2021 | 04:27 PM
08/19/2020 |  | RoutineScheduled |  | Augusta | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | none | none | Pump | Gravity |  | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation"] | ["BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [7 empty] | 08/19/2020 |  | 69.000000 | [5 empty] | Will be sent separately | Inspected | Repaired air supplu line will return in october and pump tank | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/26/2021 | 09:04 AM
04/30/2020 |  | RoutineScheduled | 17-192-006 | Tazewell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | Septic Inc |  | Denny | Deel |  |  | Clearstream |  | Gravity |  | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens","Level Sensor Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens","Level Sensor Operation"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
09/17/2020 |  | RoutineScheduled | 124-STS-2379 | Augusta | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Rejected | EHD - Central Shenandoah | Onsite Wastewater Services - May Supply | 1942001022 | Sara | Tusing | 2.000000 |  | none | none | Gravity | Gravity |  | Chlorination |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Inspected by DKS | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/28/2021 | 05:41 AM
11/11/2020 |  | RoutineScheduled | SD-12-05 | Culpeper | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC |  | Jason | Brown | 1.000000 | 1000 | Best 1 |  | Gravity | Gravity | Discharge | Chlorination |  | [] | [] | YES | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12/28/2020 | 03:10 PM
07/17/2020 |  | Reportable Incident | SD-13-443 | Fauquier | This AOSS should now return to normal function after having provided the above state routine maintenance | Approved | EHD - Rappahannock-Rapidan | SES Mid Atlantic | 1942001203 | Michael | Green | [9 empty] | ["Distribution Pump Operation"] | ["Distribution Pump Operation"] | [18 empty] | Installed N140 pump. | This AOSS should now return to normal function after having provided the above state routine maintenance |  | 07/17/2020 | 04:00 PM
08/28/2020 |  | Reportable Incident | 2006-143-0141 | Henrico | This AOSS should now return to normal function after having provided the above state routine maintenance | Approved | EHD - Henrico | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1500 | Orenco Advantex | None | Pump | Distribution Box | Aggregate Trench | None | 450.000000 | ["Control Operation"] | ["Control Operation"] | N/A | Musty | Clear | [15 empty] | Alarm event - found recirc / processing tank in high level condition due to failed electrical contactor. - Contactor in control panel replaced, system pumped out of high level alarm condition. | This AOSS should now return to normal function after having provided the above state routine maintenance |  | 08/31/2020 | 08:15 AM
09/23/2020 |  | RoutineScheduled | 175-17-0351 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Prince William | Dominion Septic, Inc | 1942001125 | Tom | Jackson |  |  | EZ Treat Sandfilter | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation" ,"Level Sensor Operation" ,"Control Operation"] | ["Level Sensor Operation" ,"Control Operation" ,"Distribution Pump Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
11/16/2020 |  | Follow-Up | 179-11-0142-SWP | Stafford | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | EZ Treat Sandfilter | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [7 empty] | 11/16/2020 |  | 2.000000 | [5 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
05/01/2020 |  | Follow-Up | 196-10-183 | Westmoreland | This AOSS should now return to normal function aft | Approved | EHD - Three Rivers | [13 empty] | ["Dispersal Sytem Operation"] | ["Dispersal Sytem Operation"] | [19 empty] | This AOSS should now return to normal function aft |  |  | 12:00 AM
08/21/2020 |  | RoutineScheduled | 171-09-0307 | Pittsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Pittsylvania-Danville | Virginia Septic Service LLC | 1942001512 | iain | Waugh | 1.000000 | 1500 | Ecoflo |  | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens","Attached Growth Medium"] | ["Effluent Screens","Attached Growth Medium"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 08/21/2020 | 12:00 AM
07/07/2020 |  | RoutineScheduled | SWP-04-349 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Distribution Pump Operation" ,"Dispersal System Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | We recommend replacing the metal alarm horn and the water meter on your system. | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 |  | 04/09/2021 | 03:25 PM
10/06/2020 |  | RoutineScheduled |  | Shenandoah | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Control Operation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens"] | ["Auxiliary Filter" ,"Control Operation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens"] | YES | [7 empty] | 10/06/2020 |  | 58.000000 | [5 empty] | Will be sent separately | Inspected | Repaired Discharge assembly Replaced zone valve Replaced multiple cracked lids and air vents System now operating as designed | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance |  | 04/26/2021 | 09:04 AM
04/07/2020 |  | Reportable Incident | 234-17-444 | Chesapeake | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Chesapeake | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] |  | N/A | [17 empty] | Owner called due to the red light being on. Serviced system on 3/27/2020 - Replaced UV light bulb. Back on 4/7/2020 - Found UV had water in the control panel. Water running in thru the flex tube into the electrical assembly. Need to fix properly. This is not warranty related and needs to be fixed. System is bad because UV is not working. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. |  | 04/07/2020 | Jan 1 1900 12:00PM
10/28/2020 | Alternative | RoutineScheduled | 171-05-0971 | Shenandoah | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Lord Fairfax | Onsite Wastewater Services - May Supply | 1942001627 | Drew | Shull | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Pressure | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/28/2021 | 05:41 AM
05/05/2020 |  | RoutineScheduled |  | Fairfax | This AOSS is functioning as designed and in accord | Approved | EHD - Fairfax | Great Falls Septic Service | 1942001301 | Joshua | Hott | 1.000000 | 1875 |  | Puraflo | Pump | Distribution Box | Aggregate Trench | None | 500.000000 | ["None"] | ["Effluent Screens"] |  | Low | [17 empty] | This AOSS is functioning as designed and in accord |  |  | 12:00 AM
04/13/2020 |  | Routine/Scheduled |  | Frederick | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Review | EHD - Lord Fairfax | POWELLS PLUMBING, INC. | 1942001036 | Kurt | Holthaus | 1.000000 | 1000 | None |  | Gravity | None | Alternative Discharge |  | 750.000000 | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Disinfection","Sludge/Scum Accumulation"] | N/A | [17 empty] | Annual Inspection - Add high level alarm to system. Patch hole in fiberglass lid. Air filter needs to be replaced for blower. Need 13" lid for dechlorinator. Softener needs to be open to daylight or repair continous discharge. Serviced blower and disinfection. Pumped all 3 tanks. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. |  | 05/22/2020 | 03:15 PM
09/10/2020 |  | RoutineScheduled |  | Augusta | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation" ,"Level Sensor Operation" ,"SludgeScum Accumulation" ,"BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | ["Dispersal System Operation" ,"Level Sensor Operation" ,"BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced Alarm float at time of service Recommended to pump all tanks. Homeowner has contacted us about this service to schedule | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 |  | 04/26/2021 | 09:04 AM
12/08/2020 |  | RoutineScheduled | 175-15-0247 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Wastemaster Inc |  | Timothy | Jenkins | 2.000000 |  | ATU | EZ Flow | Pump | Gravity | Discharge | UV |  | [] | [] |  | Musty | Clear | 7.300000 |  | 8.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12/16/2020 | 12:55 PM
11/16/2020 |  | RoutineScheduled | 069160043 | Frederick | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | Adjusted pressure gauge to proper psi after jetting drainfield | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/26/2021 | 09:04 AM
05/01/2020 |  | RoutineScheduled | {FIPSCode}-STS-8044 | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | ["None"] | ["None"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 07/28/2020 | 12:00 AM
04/06/2020 |  | Routine, Scheduled | SWT-05-430 | King George County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 2.000000 |  | Clearstream | None | Pump | Distribution Box | Aggregate Trench |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation"] |  | YES | NO | [15 empty] | [Comments]: Routine inspection. Found timer enabler float switch stuck on, replaced it. Replaced air filter in air compressor. Excessive sludge measured in atu tank and pump tank. Owner to make arrangements for pump-out. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/27/2020 | 04:14 AM
12/18/2020 |  | Routine, Scheduled | 175-18-0488 | Prince William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | EZ Treat Sandfilter |  |  |  |  | UV Light |  | ["Blower/Compressor/Aerator Operation","Disinfection"] | ["Blower/Compressor/Aerator Operation"] |  | Acceptable | Clear | 7.900000 | 14.300000 | [13 empty] | Needs new Salcor UV Bulb. Pump 1 Amps 10.86 ETM 240 hrs Cycles 28622 Pump 2 Amps 6.02 ETM 14 hrs Cycles 1605 Septic Sludge 3" Scum 1" ATU Sludge 1" Scum 0 Pump Sludge 0 Scum 0 On 30 secs Off 1 hr | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 12/18/2020 | 12:03 PM
12/11/2020 |  | RoutineScheduled | 061-18-206 | Fauquier | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Rappahannock-Rapidan | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 1.000000 |  | Septic/ Microfast |  | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [17 empty] | Septic-7"sludge 0"scum/ Microfast-8"sludge/ Blower air filter cleaned/ Water color in Microfast is a little dark. Added a 4" tee on the inlet pipe of the monster box and adjusted the dial-a-flows to help with equal distribution of the box. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  |  | 12:00 AM
01/17/2020 |  | Routine, Scheduled | 179-09-0009-SWP | Stafford County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001350 | Mike | Cook | 1.000000 |  | EZ Treat Sandfilter | None | Pump | Distribution Box | Aggregate Trench |  |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/28/2020 | 01:39 PM
10/08/2020 |  | RoutineScheduled | SD-13-480 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Greenway Engineering | 1942001008 | Jeremy | Ferguson | 1.000000 | 1500 | Presby | none | Pump | Pressure | Mound | Not Applicable |  | ["Effluent Screens","SludgeScum Accumulation","Control Operation"] | ["Effluent Screens","SludgeScum Accumulation","Control Operation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 10/08/2020 | 02:30 PM
01/09/2020 | Alternative | Routine, Scheduled | 234-16-209 | Chesapeake | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Chesapeake | Farmer's Septic Service, Inc. |  | Ross | Cole | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | [Comments]: Serviced system. Checked the pump, panel, & floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. The aerator should be raised 6-8". The Salcor UV cord, tube, bulb, circuity board, box, and wires from splice box are bad and need to be replaced. The septic tank has 16" of sludge in the bottom of the tank - no crust. The timer is set to 2 minutes every 2 hours. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 01/09/2020 | Dec 30 1899 12:00PM
08/05/2020 |  | Follow-Up | 069150349 | Frederick | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["SludgeScum Accumulation"] | ["SludgeScum Accumulation"] | NA | [15 empty] | Will be sent separately | Inspected | Septic tank pumped however still 12in of sludge in tank. System is operating as designed | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/26/2021 | 09:04 AM
03/17/2020 |  | Routine, Scheduled |  | Loudoun County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | Delta Environmental Products, DF Series | None | Pump | Distribution Box | Aggregate Trench | [23 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/12/2020 | 02:21 PM
07/29/2020 |  | RoutineScheduled | 195-Discharge-21118 Grassy Ridge Road | Washington | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Mount Rogers | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","Effluent Screens","Disinfection"] | ["Disinfection","BlowerCompressorAerator Operation","Control Operation","Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
04/09/2020 |  | RoutineScheduled | 44826 | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Greenway Engineering | 1942001008 | Jeremy | Ferguson | 1.000000 | 1000 | Puraflo | none | Pump | Gravity | Trenches | Not Applicable | 125.000000 | ["Attached Growth Medium","Control Operation","Distribution Pump Operation"] | ["Distribution Pump Operation","Control Operation","Attached Growth Medium"] | NA | [17 empty] | The control panel has been fixed and is now mounted on the post and secured. Timers have been adjusted for proper flow to the units. The peat moss has been replaced. The dbox was rebalanced and camera. System is operational. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 07/22/2020 | 09:00 AM
08/13/2020 |  | RoutineScheduled | 03-125-095 | Dickenson | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Effluent Screens"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
07/22/2020 |  | RoutineScheduled | 137-STS-25544 | Orange | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Wastemaster Inc |  | Timothy | Jenkins | 2.000000 |  | Advantex | UV | Pump | Gravity | Discharge | UV |  | [] | [] |  | Musty | Clear | 7.600000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 02:35 PM
10/30/2020 |  | Initial Visit |  | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - New River | MSS INC |  | Tim | Conner | 2.000000 | 2500 | MICROFAST |  | Gravity | Pressure | Trenches | Not Applicable |  | ["on"] | ["on"] | YES | Septic | Discolored | [5 empty] | 11/13/2020 | Sample Chamber | [6 empty] | Attached to this report | Inspected | REFER TO JOB REPORT FOR NOTES | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 10/30/2020 | 12:00 PM
09/04/2020 |  | Initial Visit | 177-08-0245-SWP | Spotsylvania | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Start-Up Inspection | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/09/2021 | 03:25 PM
03/30/2020 |  | Routine, Scheduled | 061-19-034 | Fauquier County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Biomicrobics MicroFAST | None | Pump | Distribution Box | Gravel-Less Trench |  |  | ["Auxiliary Filter","Control Operation"] | ["Auxiliary Filter","Control Operation"] | [18 empty] | [Comments]: 6-month inspection. Collected first BOD sample. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/01/2020 | 06:33 AM
11/25/2020 |  | RoutineScheduled | 153-STS-20378 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 3.000000 |  | Septic Tank | Delta ATU | Pump | Pressure | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | [18 empty] | Septic tank-6"sludge 0"scum/ ATU-6"sludge 0"scum/ Pump tank-0"sludge/ Drip rates: Zone1-5.9/ Zone2-5.8/ Zone3-5.5/ Water meter-0600551/ Blower air filter cleaned/ Broken fitting replaced at time of inspection in the drip field. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  |  | 12:00 AM
12/23/2020 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump | Distribution Box | Aggregate Bed | None |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  |  | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 12/23/2020 | Jan 1 1900 1:00PM
06/23/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | SES MidAtlantic LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. Strongly recommend septic tank be replaced. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/15/2021 | 09:00 AM
01/06/2020 | Alternative | Routine, Scheduled | 234-15-30 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesapeake | R & K Septic, Inc. |  | John | Butt, Jr |  |  | Clearstream ATU |  | Pump | Distribution Box |  | None |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] |  |  |  | 7.800000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/06/2020 | Dec 30 1899 2:15PM
07/08/2020 |  | Routine/Scheduled |  | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Hoot |  | Pump | Drip | Drip Tubing | UV Light |  | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  |  | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 07/08/2020 | Jan 1 1900 11:15AM
12/05/2020 |  | RoutineScheduled | 2061-99-153 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Wastemaster Inc |  | Timothy | Jenkins | 2.000000 |  | Recirculating Sand Filter | Effluent Filter | Pump | Gravity | Discharge | Chlorination |  | [] | [] |  | Musty | Clear | 6.900000 |  |  | 2.200000 | [12 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12/10/2020 | 01:25 PM
07/16/2020 |  | Routine/Scheduled | 128-15-0049 | Essex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | PremierTech, EFX | None | Gravity | None | Aggregate Bed | None | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | Musty | Clear | [15 empty] | Routine service conducted. Primary septic tank in normal operating level - effluent screen serviced. Pump Basin in normal level - pump, float sensors operating properly. EcoFlo processing tank - peatmoss biofilter in good condition, raked / turned. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 07/18/2019 | 07:30 AM
09/14/2020 |  | Routine/Scheduled | 17-120-0419AR | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. |  |  | Ecoflo | [6 empty] | ["Attached Growth Medium","Dispersal System Operation","Effluent Screens","Sludge/Scum Accumulation"] | ["Attached Growth Medium","Dispersal System Operation","Effluent Screens","Sludge/Scum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 09/14/2020 | Jan 1 1900 12:00PM
12/16/2020 |  | Initial Visit | 179-STS-87782 | Stafford | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation"] | ["Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Recirc high level count at 11, low level 22. Discharge high level count at 4. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
11/03/2020 |  | Routine/Scheduled |  | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Gravity | Distribution Box |  | None |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Level Sensor (Float) Operation","Recirculation Pump","Sludge/Scum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Level Sensor (Float) Operation","Recirculation Pump","Sludge/Scum Accumulation"] | N/A |  | 5.58 | 7.660000 | 6.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 11/03/2020 | Jan 1 1900 7:30AM
10/01/2020 |  | RoutineScheduled | S-12-111-0081 | Botetourt | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | Hunter E. Ayres, General Contractor | 1942001166 | Hunter | Ayres | 3.000000 | 6000 | Ecopod |  | Pump | Pressure | Trenches | Not Applicable |  | ["Auxiliary Filter","Effluent Screens"] | ["Auxiliary Filter","Effluent Screens"] | YES | [7 empty] | 10/01/2020 | Pump Chamber | 5.000000 | [5 empty] | Attached to this report |  | Filters checked and cleaned. Pumps and control panels functioning properly. No apparent leaks in system or drain field area. System did not need to be pumped. Sample draw within acceptable limits. All child safety nets in place and in good condition. All lids properly secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 10/16/2020 | Jan 1 1900 7:45AM
08/20/2020 |  | RoutineScheduled | SD-10-167 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Soils, Inc. | 1940001392 | Markham | Smith | 2.000000 | 1500 | PuroFlo |  | Pump | Gravity | Pad | Not Applicable | 62.500000 | [] | ["Septic Tank Baffles","SludgeScum Accumulation","Level Sensor Operation","Attached Growth Medium","Control Operation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 09/03/2020 | 09:35 AM
01/07/2020 |  | Pump-Out Only | {FIPSCode}-STS-19163 | Frederick County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Lord Fairfax | POWELLS PLUMBING, INC. | 1942001036 | Kurt | Holthaus |  |  | Orenco Advantex | [6 empty] | ["SludgeScum Accumulation"] | ["SludgeScum Accumulation"] | [18 empty] | [Comments]: Pumped Advantex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/07/2020 | 03:24 PM
06/09/2020 |  | RoutineScheduled |  | Rockingham | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["Control Operation" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | [7 empty] | 06/09/2020 |  | 34.000000 | [5 empty] | Will be sent separately | Inspected | Lab Sample Normal Will send quote next year along with inspection for pumping as we discussed | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/26/2021 | 09:04 AM
09/10/2020 |  | Routine/Scheduled | 154-05-0628 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Old Dominion Onsite, Inc. | 1942001134 | John | Ewing | 1.000000 | 1500 | Orenco Advantex |  | Pump | Distribution Box | Aggregate Trench | None | 250.000000 | ["Dispersal System Operation","Effluent Screens","Recirculation Pump"] | ["Dispersal System Operation","Recirculation Pump"] | N/A | [17 empty] | Recirculation pump vault filter cannot be accessed with fence so close to access lids. Fence must be removed in order to perform necessary maintenance or possible repair/replacement work. The Advantex manifold was flushed and the recirculating splitter valve was removed and checked for proper functioning. There were no pump timing overrides recorded in the past 30 days. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 09/10/2020 | 10:53 AM
03/27/2020 |  | Routine, Scheduled |  | Loudoun County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | None | None | Gravity | [24 empty] | [Comments]: Sale inspection was done on a conventional gravity septic system. There are 2 pvc cleanouts. The sewer line was camera snaked and was clear. The concrete septic tank was 12" under the ground and pumped out and inspected for any leaks or cracks none were found. The conveyance line was camera snaked and was clear. The 9 port plastic splitter box was 2" under the ground and was in good condition. The two 9 port plastic d-boxes were 4" under the ground and all 10 header lines were camera snaked and the drain field was probed and was dry. At this time all components are in working condition. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/12/2020 | 02:21 PM
07/13/2020 |  | RoutineScheduled |  | Fauquier | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation"] | ["Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Observed small wet area below drainfield trenches. Possibly from lateral groundwater movement. Will go back for further investigation. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
09/01/2020 |  | Follow-Up | SD-08-147 | Fauquier | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001068 | David | Stewart |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Installed new post and backer board for control panel. Added special spring check valve on drip and filter flush. Found infiltration at the septic tank riser and pump tank drip grommets, proposal for repairs to be sent to homeowner. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
05/08/2020 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Eco Virginia | 1942001235 | William | Poindexter | 2.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 |  | 06/03/2021 | 05:53 AM
10/14/2020 |  | RoutineScheduled | 179-12-0334-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | EcoPod | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Distribution Pump Operation"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter" ,"Distribution Pump Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Installed replacement air filter. | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 |  | 04/09/2021 | 03:25 PM
05/28/2020 |  | Routine/Scheduled | 18-163-0066 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chickahominy | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. |  |  | Aqua Klear |  | Pump |  |  |  |  | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 05/28/2020 | Jan 1 1900 9:00AM
07/24/2020 | Alternative | Reportable Incident | 150-07-0271 | King William | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Atlee Sewage Disposal, LLC | 1942001144 | Francis | Frere | 3.000000 | 2850 | Septic Tank | Delta White Water | Pump | Gravity | Trenches | Not Applicable | 600.000000 | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | NA | None | Clear |  |  | 20.000000 | [11 empty] | Pumped Out |  | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 07/29/2020 | 09:25 PM
01/29/2020 |  | Routine, Scheduled |  | Mathews County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Three Rivers | MEAGHER, WILLIAM J | 1942001190 | WILLIAM | MEAGHER | 1.000000 | 1000 | Septic Tank Only | Clearstream | Pump | Distribution Box | Gravel-Less Trench | None | [22 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/06/2020 | 09:50 AM
01/10/2020 |  | Routine, Scheduled | {FIPSCode}-STS-28679 | Goochland County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chickahominy | SHAW, WILLIAM A, JR. | 1934000449 | WILLIAM | SHAW |  |  | Septic Tank Only | Septic Tank Only | None | None | None | None |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/27/2020 | Jan 1 1900 10:53AM
11/24/2020 |  | Pump-Out Only | 175-03-0964 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | POWELLS PLUMBING, INC. | 1942001036 | Kurt | Holthaus |  |  | Aquarobic Mini Plant | [6 empty] | ["Sludge/Scum Accumulation"] | ["Sludge/Scum Accumulation"] | N/A | [17 empty] | Pumped Aquarobic. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12/31/2020 | 12:30 PM
11/03/2020 |  | Routine/Scheduled | 2003-143-0292 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Henrico | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1500 | Orenco Advantex |  | Pump | Distribution Box | Aggregate Trench | None | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | None | Clear | [15 empty] | Routine Service Processing Tank - normal operating level - RSV, recirc pump & effluent screen serviced. Treatment module - media drapes & spray grid serviced. Pump Tank - normal operating level - pump, float sensors & controls operating properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 11/04/2020 | 07:15 AM
07/22/2020 |  | RoutineScheduled | 137-STS-25542 | Orange | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Wastemaster Inc |  | Timothy | Jenkins | 2.000000 |  | Recirculating Sand Filter |  | Pump | Gravity | Discharge | Chlorination |  | [] | [] |  | Musty | Clear | 6.600000 |  |  | 2.100000 | [11 empty] | EHS entered visit date based on data history | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 07/22/2020 | 02:30 PM
01/03/2020 |  | Routine, Scheduled | 093-02-0320 | Isle of Wight County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Western Tidewater | R & K Septic, Inc. |  | John | Butt, Jr |  |  |  |  | Pump | Distribution Box |  |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] |  |  |  | 7.000000 | 3.000000 | [13 empty] | [Comments]: Replaced aerator, air line going through the riser and alarm bulb. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/03/2020 | Jan 1 1900 11:00AM
04/27/2020 |  | RoutineScheduled | 033-15-0166-SWP | Caroline | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | UV |  | ["Distribution Pump Operation" ,"Level Sensor Operation" ,"Control Operation" ,"Auxiliary Filter" ,"Recirculation Pump"] | ["Level Sensor Operation" ,"Recirculation Pump" ,"Control Operation" ,"Auxiliary Filter" ,"Distribution Pump Operation"] | NA | [15 empty] | Will be sent separately | Inspected | High level alarm in both compartments. Splice box for discharge floats was full of water and timer float wire had rotted in half. Made new connections for all 3 float switches and suctioned out water. Replaced broken recirc pump switch. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
07/25/2020 |  | Routine/Scheduled |  | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump | Drip | Elevated Sand Mound | UV Light |  | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  |  | 7.000000 | 5.000000 | [13 empty] | Replaced UV bulb | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 07/25/2020 | Jan 1 1900 11:45AM
04/06/2020 | Alternative | Routine/Scheduled | 136-01-0027 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | Hydro-Action ATU | None | Pump | Distribution Box | Aggregate Trench | None |  |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | Heavy sludge/solids in the Septic Tank; concrete Crock on Discharge Tank was leaking | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/07/2020 | 05:13 PM
08/08/2020 |  | RoutineScheduled | 109-05-0908 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1000 | Multi Flo |  | Pump | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | [17 empty] | Inspected | Septic 6" Sludge/ Pump Tank 16" fine sludge, cleaned spin filter, Added 1 2lb Rootx | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 08/08/2020 | 02:00 PM
11/30/2020 | Alternative | Routine/Scheduled | 151-14-0122 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | Clearstream | None | Pump | Distribution Box | Aggregate Bed | None | 450.000000 |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | Musty | Clear | [15 empty] | Routine Service Primary Septic Tank - normal operating level Aeration Tank - normal level - compressor serviced - Air diffuser connector cracked. Pump Tank - normal level - pump, float sensors & controls operating properly. Distribution Box - plastic - intact - all laterals accepting effluent. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 12/01/2020 | 07:45 AM
11/23/2020 |  | RoutineScheduled | SD-13-154 | Fauquier | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Level Sensor Operation"] | ["Attached Growth Medium" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | YES | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
10/02/2020 |  | Routine/Scheduled |  | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Gravity | Distribution Box |  | None |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Level Sensor (Float) Operation","Recirculation Pump","Sludge/Scum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Level Sensor (Float) Operation","Recirculation Pump","Sludge/Scum Accumulation"] | N/A |  | 14.71 | 6.710000 | 6.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 10/02/2020 | Jan 1 1900 2:00PM
10/27/2020 |  | RoutineScheduled | 033-08-0163-swp | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Wastemaster Inc |  | Timothy | Jenkins | 2.000000 |  | PuraFlo |  | Pump | Gravity | Discharge | UV |  | [] | [] |  | Musty | Clear | 7.200000 | 5.300000 |  |  |  | 10/27/2020 |  | 2.000000 |  | 0.800000 | 7.500000 | [5 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 11/16/2020 | 02:30 PM
11/17/2020 |  | RoutineScheduled | VAG408096 | Rockingham | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 | Approved | EHD - Central Shenandoah | Onsite Wastewater Services - May Supply | 1942001627 | Drew | Shull | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity |  | Chlorination |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | system needs to pumped let ows know when this has been done Inspection by Ds | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 |  | 05/28/2021 | 05:41 AM
09/17/2020 |  | RoutineScheduled |  | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 2705051738 | Joshua | Hott | 1.000000 | 1500 | Septic | Puraflo | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
06/13/2020 |  | RoutineScheduled | 2096-04-153 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Wastemaster Inc |  | Timothy | Jenkins | 2.000000 |  | ATU | Polishing Sandfilter | Pump | Gravity | Discharge | Chlorination |  | [] | [] |  | Musty | Clear | 6.300000 | 5.200000 |  | 2.200000 |  |  |  | 1.900000 |  |  | 2.300000 |  |  | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 06/29/2020 | 06:00 PM
05/06/2020 |  | Reportable Incident | SWP 99-20 | Spotsylvania | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Distribution Pump Operation"] | ["Distribution Pump Operation"] | NA | [15 empty] | Will be sent separately | Inspected | High level alarm due to groundwater infiltration at pipe penetration in recirc tank at drip force main. Cleaned dirty effluent filter that was causing high level in septic tank. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
12/29/2020 |  | RoutineScheduled | 107-03-0548 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | None | Clear | 7.230000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 01/12/2021 | 12:10 PM
06/16/2020 |  | RoutineScheduled | 181-05-0036 | Rockbridge | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central Shenandoah | Hunter E. Ayres, General Contractor | 1942001166 | Hunter | Ayres | 2.000000 | 2500 | Best 1 |  | Pump | Pressure | Drip | Not Applicable |  | ["SludgeScum Accumulation","BlowerCompressorAerator Operation"] | ["SludgeScum Accumulation","BlowerCompressorAerator Operation"] | YES | None | [15 empty] | Pumped Out | Pumped and cleaned Best 1 treatment unit and pumped and cleaned pump tank. Cleaned effluent screen, spin filter and air filter. Removed and cleared aeration holes in pipe. Refilled tanks to proper levels. Control functioning properly. No apparent in system or drain field area. Lids properly secured. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 06/19/2020 | 12:00 PM
05/12/2020 |  |  | {FIPSCode}-STS-2889 | Dickenson | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 05/12/2020 |  | 13.900000 |  |  | 1.300000 |  |  | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 05/12/2020 | 12:00 AM
05/05/2020 |  | RoutineScheduled | 177-07-0363-SWP | Spotsylvania | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Septic Works LLC | 1942001080 | michael | smith | 1.000000 |  | Puraflo | none | Gravity | Gravity |  | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/25/2021 | 08:10 AM
03/02/2020 |  | Follow-Up |  | Prince William County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Prince William | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Orenco Advantex | None | Pump | Distribution Box |  |  |  | ["Level Sensor Operation"] | ["Level Sensor Operation"] | [18 empty] | [Comments]: Indoor alarm panel and float for panel were replaced. New riser was installed on septic tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/06/2020 | 02:45 PM
11/25/2020 |  | RoutineScheduled | 10-113-188 | Buchanan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
06/09/2020 |  | Routine, Scheduled | 175-02-0602 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Puraflo |  |  |  |  | None |  | ["Effluent Screens","Sludge/Scum Accumulation"] | ["Effluent Screens","Sludge/Scum Accumulation"] | [18 empty] | Pump Amps 7.40 ETM 1170.75 Cycles 35392 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 06/09/2020 | 04:22 PM
09/10/2020 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump | Distribution Box | Aggregate Bed | UV Light |  | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  | 2.48 | 7.940000 | 6.400000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 09/10/2020 | Jan 1 1900 10:30AM
03/10/2020 |  | Routine, Scheduled |  | Loudoun County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | None | Pump | Distribution Box | Gravel-Less Trench | [23 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/12/2020 | 02:21 PM
06/01/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/27/2021 | 01:26 PM
10/28/2020 |  | RoutineScheduled | 154-11-0045 | Louisa | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Blue Ridge | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Attached Growth Medium" ,"Control Operation"] | ["Distribution Pump Operation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Attached Growth Medium" ,"Control Operation" ,"Dispersal System Operation"] | YES | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
06/22/2020 |  | RoutineScheduled | 179-12-0218-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Effluent Screens" ,"Recirculation Pump" ,"Distribution Pump Operation"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 |  | 04/09/2021 | 03:25 PM
09/02/2020 |  | RoutineScheduled | 69090340 | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 2705110225 | Larry | Royston | [9 empty] | ["None"] | ["None"] | YES | [16 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 09/23/2020 | 12:00 AM
08/24/2020 | Alternative | Routine/Scheduled | 151-11-0125 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | PremierTech, EFX | None | Pump | Distribution Box | Aggregate Trench | None | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | Musty | Clear | [15 empty] | Routine service conducted. Primary septic tank in normal operation level - effluent screen serviced. Peatmoss biofilter in poor condition - peatmoss biofilter changeout being proposed - raked and turned. Pump Basin - pump, float sensors and controls operating properly | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 08/27/2020 | 09:45 AM
12/21/2020 |  | RoutineScheduled |  | Rockingham | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/26/2021 | 09:04 AM
03/06/2020 |  | Routine, Scheduled | 05-113-278 | Buchanan County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Cumberland Plateau | DEEL, DENNY M | 1942001097 | DENNY | DEEL |  |  | Norweco Singulair ATU | None | Gravity | Distribution Box | Aggregate Bed | None | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Effluent Screens"] |  | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/16/2020 | Jan 1 1900 12:09PM
12/03/2020 | Alternative | Routine/Scheduled | 166-97-304 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 3.000000 | 2600 | Clearstream |  | Pump | Distribution Box | Aggregate Trench |  |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12/03/2020 | 05:00 PM
08/14/2020 |  | RoutineScheduled | 043-16-0064 | Clarke | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Greenway Engineering | 1942001008 | Jeremy | Ferguson | 1.000000 | 1500 | Microfast | none | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","SludgeScum Accumulation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 09/03/2020 | 01:55 PM
07/14/2020 |  | RoutineScheduled | 175-14-0330 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/Microfast | Pump Tank | Pump | Pressure | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [17 empty] | Septic-6"sludge0"scum/Microfast-4"sludge/ Pump Tank-0"sludge. No pump out required at this time.Pump cnts-523 ETM-31.57/Blower air filter cleaned. Drainfield good. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
03/23/2020 |  | RoutineScheduled | SD-113-15-125 | Madison | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Greenway Engineering | 1942001008 | Jeremy | Ferguson | 1.000000 | 1500 | Advantex | none | Pump | Pressure | Drip | Not Applicable |  | ["Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | YES | [7 empty] | 03/23/2020 | Pump Chamber | 2.130000 | [5 empty] | Will be sent separately |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 09/28/2020 | 10:30 AM
01/22/2020 |  | Routine, Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Chesapeake | R & K Septic, Inc. |  | John | Butt, Jr |  |  | Clearstream ATU |  | Pump | Drip | Elevated Sand Mound | UV Light |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] |  |  | 18.09 | 6.610000 | 4.000000 | [13 empty] | [Comments]: Needs a UV Bulb | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/22/2020 | Jan 1 1900 9:00AM
04/01/2020 |  | Routine, Scheduled | 02-177-1381 | Pulaski County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - New River | Conner, Timothy Wayne | 1942001003 | Timothy | Conner |  |  | Microfast | Septic Tank Only | Pump | Drip | Drip Tubing | None | [21 empty] | [Pumpout Comments]: LAST PUMP AND CLEANED IN 2017. RECOMMEND TANK BE PUMPED AND CLEANED EVERY 3-5 YEARS. [Comments]: EVERYTHING APPEARS TO BE FUNCTIONING PROPERLY AT THIS TIME. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/15/2020 | 12:04 PM
03/13/2020 |  | Routine, Scheduled |  | Northumberland County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Three Rivers | PINNIX, JOEL S | 1934000193 | JOEL | PINNIX |  |  | Septic Tank Only | Septic Tank Only | None | None | None | None | [22 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/15/2020 | 10:19 AM
03/03/2020 |  | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Combs Wastewater Management LLC | 1942001353 | Amy | Combs | 2.000000 | 1000 |  |  | Gravity | Gravity | Trenches | Not Applicable | 450.000000 | ["None"] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | YES | None | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12/18/2020 | 12:00 PM
07/08/2020 | Alternative | RoutineScheduled | 159-14-0072 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Church View Septic Service Inc. | 1942001302 | Charles | Langford | 1.000000 | 1000 | Ecoflo |  | Pump | Gravity | Pad | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 07/08/2020 | 12:00 AM
12/02/2020 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump | Drip | Elevated Sand Mound | UV Light |  | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  |  | 7.000000 | 5.000000 | [13 empty] | UV is not working | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 12/02/2020 | Jan 1 1900 2:00PM
04/10/2020 |  | Follow-Up | SWP-03-949 | Spotsylvania County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Puraflo | None | Pump | Distribution Box | [23 empty] | [Comments]: Pump out of septic tank & pump tank by Marshalls 4/8. Peat replacement completed. Peat was purchased from Vamac and degraded peat was disposed at Spotsylvania County Refuse. Cleaned sample box and distribution box. Replaced floats and installed proper float tree. Installed septic inlet riser. Sealed pump tank wedge lid. Resealed force main pipe penetration. Measured pump tank dimensions to determine size 1000 gallons. Sealed section of mid-seam on inlet end that had roots (inside seal). | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/27/2020 | 04:14 AM
03/04/2020 |  | Routine, Scheduled |  | Loudoun County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | None | Pump | Distribution Box | Aggregate Bed | [23 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/12/2020 | 02:21 PM
08/20/2020 |  | Reportable Incident |  | Virginia Beach | This AOSS should now return to normal function after having provided the above state routine maintenance | Pending Payment | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Whitewater ATU |  | Pump | Distribution Box |  |  |  | ["Control Operation","Dispersal System Operation","Distribution Pump Operation"] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation"] | N/A | [17 empty] | Replaced pump | This AOSS should now return to normal function after having provided the above state routine maintenance |  | 08/20/2020 | Jan 1 1900 6:30PM
09/29/2020 |  | Follow-Up | 175-12-0508 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green | [9 empty] | ["Level Sensor (Float) Operation"] | ["Level Sensor (Float) Operation"] | [18 empty] | Replaced timer enable float & yard box cover. | This AOSS should now return to normal function after having provided the above state routine maintenance |  | 09/29/2020 | 04:00 PM
12/01/2020 |  | Reportable Incident | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance | Approved | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green | [9 empty] | ["Disinfection"] | ["Disinfection"] | [18 empty] | Replaced (2) UV Bulbs. | This AOSS should now return to normal function after having provided the above state routine maintenance |  | 12/01/2020 | Jan 1 1900 4:00PM
02/27/2020 |  | Routine, Scheduled | 145-09-0034 | Highland County | This AOSS should now return to normal function after having provided the above stated routine maintenance. | Approved | EHD - Central Shenandoah |  |  |  |  | 2.000000 | 2000 |  | Sandfilter, Recirculating | Pump | Manifold | Aggregate Trench | None |  | ["Control Operation","Level Sensor Operation"] | ["Control Operation","Level Sensor Operation"] | [18 empty] | [Comments]: The system did not need to be pumped. The timer enable float was not working at time of inspection so it was replaced. The timer float and the high water float were wired backwards so they were repaired. The sand filter was inspected and was operating as designed. The lids were properly secured. | This AOSS should now return to normal function after having provided the above stated routine maintenance. |  | 03/10/2020 | 30-12-1899 03:47 PM
08/19/2020 |  | Follow-Up | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green | [9 empty] | ["None"] | ["None"] | [18 empty] | Zone 1 coming to surface,soft & spongy at opposite end. Zone 2 soft & spongy. Check valves & hydraulic unit isolating zones. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 08/19/2020 | Jan 1 1900 1:55PM
03/12/2020 |  | Routine, Scheduled | 10-125-001 | Dickenson County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Cumberland Plateau | DEEL, DENNY M | 1942001097 | DENNY | DEEL |  |  | Norweco Singulair ATU | None | Gravity | None | Alternative Discharge | Chlorine | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens"] |  | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/20/2020 | Jan 1 1900 4:03PM
12/17/2020 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Elevated Sand Mound | UV Light |  | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  |  | 7.630000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 12/17/2020 | Jan 1 1900 10:45AM
04/27/2020 |  | RoutineScheduled | 154-07-0576 | Fluvanna | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Aiternative Systems Inspection Services, LLC | 1942001047 | Wesley | Basore | 1.000000 | 500 | Norweco 960 |  | Pump | Pressure | Mound | Not Applicable | 150.000000 | ["BlowerCompressorAerator Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation","Control Operation","Dispersal System Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","SludgeScum Accumulation","Dispersal System Operation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 06/20/2020 | 10:35 AM
05/26/2020 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Gravity | Gravity |  | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Sale inspection on a conventional gravity septic system. The concrete septic tank lid was dug up it was 10' under the ground. The tank was pumped out and inspected for any leaks or cracks none were found. The sewer line was camera snaked and the conveyance line both are pvc piping and both were clear. The 9 port plastic d-box was dug up it was 12" under the ground. All 7 header lines were camera snaked and the drain field was probed. At time of inspection all components were in working condition. | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 |  | 04/14/2021 | 04:27 PM
03/13/2020 |  | Routine, Scheduled | 10-113-099 | Buchanan County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Cumberland Plateau | DEEL, DENNY M | 1942001097 | DENNY | DEEL |  |  | Norweco Singulair ATU | None | Gravity | None | Alternative Discharge | Chlorine | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens"] |  | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/20/2020 | Jan 1 1900 3:50PM
08/17/2020 | Alternative | Routine/Scheduled | 157-12-0064 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | Serviced system. Checked the pump, panel, & floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. Replaced the light bulb for the alarm light. There is visible wetness on the drainfield - have had a lot of rain - need to keep an eye on it. The timer is set to 4 minutes every 2.5 hours. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 08/17/2020 | 12:00 PM
09/29/2020 |  | RoutineScheduled | 124-STS-2379 | Rockbridge | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Rejected | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Gravity | Gravity | Discharge | UV |  | ["Disinfection"] | ["Disinfection"] | NA | Musty | Clear | [15 empty] | no disharge during visit | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 06/09/2021 | 12:00 AM
05/22/2020 |  | RoutineScheduled | 175-12-0084 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Prince William | Dominion Septic, Inc | 1942001125 | Tom | Jackson |  |  | Orenco Advantex | none | Pump | Gravity | Drip | UV |  | ["Auxiliary Filter" ,"Control Operation" ,"Disinfection"] | ["Disinfection" ,"Auxiliary Filter" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Verified inside alarm working. Replaced UV lamp and cleaned sleeve. Replaced broken valve box for ARV's. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
07/11/2020 |  |  | {FIPSCode}-STS-4677 | Dickenson | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 07/11/2020 |  | 11.800000 | [7 empty] | UNABLE TO UPLOAD RESULTS - GET ERROR. TSS: BDL | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 07/11/2020 | 12:00 AM
04/09/2020 |  | Routine, Scheduled | SWP-04-186 | Spotsylvania County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Biomicrobics MicroFAST | None | Pump | Drip | Drip Tubing |  |  | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [18 empty] | [Comments]: System in high level upon arrival. Blower was turned off. When the panel door opens, it will swing and turn off the blower!! A few roots are growing in Fast unit. Replaced drop pressure gauge and drip filter. Proposal to be sent to homeowner: Dig up Fast unit and reseal. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/27/2020 | 04:14 AM
06/18/2020 |  | Routine/Scheduled |  | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Western Tidewater | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1500 | Orenco Advantex |  | Pump | Distribution Box | Aggregate Trench | None | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | Musty | Clear | [15 empty] | Routine pumpout by Goodman's Septic Service Routine pumpout of processing tank as recommended during annual service - pumpout conducted by Goodman's Septic Service. Recirc components removed from processing tank and serviced - restored system to proper operation and refilled processing tank to operating level. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 06/19/2020 | Jan 1 1900 8:00AM
02/18/2020 |  | Routine, Scheduled |  | Fluvanna County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Blue Ridge | CLARK, MICHAEL J | 1934000023 | MICHAEL | CLARK |  |  | Septic Tank Only | Septic Tank Only | None | None | None | None |  |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/24/2020 | 04:58 AM
07/23/2020 |  | RoutineScheduled | 182-14-0221 | Rockingham | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Central Shenandoah | Onsite Wastewater Services - May Supply | 1942001022 | Sara | Tusing | 1.000000 |  | none | none | Pump | Pressure | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | INSPECTION BY DS | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/28/2021 | 05:41 AM
01/31/2020 |  | Routine, Scheduled | 15-100-0429 | Accomack County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Eastern Shore | DUER, PETE C | 1942001051 | PETE | DUER | 4.000000 | 4000 | Septic Tank Only | Delta Environmental Products, DF Series | Pump | None | None | None |  | ["None"] | ["None"] | [18 empty] | [Comments]: Aoss Inspection. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/03/2020 | 01:51 PM
10/22/2020 |  | Initial Visit |  | Pulaski | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Payment | EHD - New River | MSS INC |  | Tim | Conner | 2.000000 | 2000 GALLONS | MICROFAST |  | Pump | Pressure | Drip | Not Applicable |  | ["on"] | ["on"] | NA | Septic | Cloudy | [5 empty] | 10/22/2020 | Sample Chamber | [6 empty] | Attached to this report | Inspected |  | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. |  | 11/13/2020 | 12:00 PM
11/11/2020 |  | RoutineScheduled | {FIPSCode}-STS-22991 | Wise | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | CLEARSTREAM |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
08/27/2020 |  | Routine, Scheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Biomicrobics MicroFAST |  | Pump | Drip | Drip Tubing | UV Light |  | ["Blower/Compressor/Aerator Operation","Disinfection"] | ["Blower/Compressor/Aerator Operation","Disinfection"] |  | Acceptable | Good | [15 empty] | Spin filter cleaned. Pump Amps 5.46 ETM 416 hrs Cycles 3187 Water Meter Reading 201600 Septic Sludge 8" Scum 7" ATU Sludge 12" Scum 0 Pump Sludge 2" Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 08/27/2020 | Jan 1 1900 9:07AM
11/12/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim |  |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/14/2021 | 04:27 PM
01/22/2020 |  | Routine, Scheduled |  | Loudoun County | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Paid | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | None | Pump | Distribution Box | Aggregate Trench | [22 empty] | [Comments]: The pump tank riser needs parge cracked so ground water can get in | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 03/02/2020 | 04:43 AM
06/08/2020 |  | RoutineScheduled | 109-03-0112 | Bedford | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Advantex AX20 |  | Gravity | Gravity | Trenches | Not Applicable |  | [] | [] | NA | [16 empty] | Inspected | Sludge level-Minimal scum-6" sludge in Septic zone of tank - Recirculation zone 16-18" Sludge, Pump counter 488885 meter 2441.52 - Cleaned Effluent filter and Biofilter, Brushed and flushed manifold, cleaned rsv, sprayed off media, pulled cleaned pump, tested float switches, flushed system. ALarm is good. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 06/28/2020 | 12:30 PM
10/12/2020 |  |  | 069-17-0401 | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 2705110225 | Larry | Royston | [9 empty] | ["None"] | ["None"] | YES | [16 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
01/28/2020 |  | Routine, Scheduled | 07-197-190 | Wise County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Lenowisco | DEEL, DENNY M | 1942001097 | DENNY | DEEL |  |  | Norweco Singulair ATU | None | Gravity | None | Alternative Discharge | Chlorine | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens"] |  | Musty | Clear | [15 empty] | [Comments]: 5 Blue Crystal added | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/18/2020 | Jan 1 1900 11:47AM
09/14/2020 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Gravity | Distribution Box |  | None |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  |  | 7.000000 | 3.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 09/14/2020 | Jan 1 1900 2:00PM
02/04/2020 |  | Routine, Scheduled |  | Loudoun County | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Paid | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | None | None | Gravity | [24 empty] | [Comments]: Sale inspection on a conventional pump septic system. The septic control panel is a interior demand dose. The septic tank was dug up and pumped out. The pvc sewer line was camera snaked and the septic tank was inspected for any cracks or leaks none were found. The pump tank, pump, floats and force main were inspected the only issue found was the unused inlet hole that was leaking and will need parget. The concrete 14 port d-box was dug up and is in working condition. The 7 header lines were camera snaked. The 5th, 6th and the 7th line were crushed 15 feet out and will need to be fixed. The rest of the header lines were clear. The drain field was probed and was dry. At this time the septic system is not in working condition. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 03/02/2020 | 04:43 AM
06/22/2020 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump | Distribution Box |  | None |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  |  | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 06/22/2020 | Jan 1 1900 10:00AM
12/03/2020 |  | Routine/Scheduled | 05-190-149 | Surry | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Crater | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | Delta Environmental Products, DF Series |  | Pump | Distribution Box | Aggregate Trench | None | 450.000000 |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | Musty | Clear | [15 empty] | Routine Service Primary Septic Tank - normal level - effluent screen serviced. Aeration Tank - Normal level - air compressor serviced. Pump Tank - normal level - pump, float sensors & controls operating Surge & Distribution box - plastic - intact - all laterals accepting effluent. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 12/04/2020 | Jan 1 1900 7:45AM
10/28/2020 |  | RoutineScheduled | 154-05-0614 | Louisa | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Blue Ridge | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Attached Growth Medium"] | ["Attached Growth Medium" ,"Recirculation Pump"] | NA | [15 empty] | Will be sent separately | Inspected | The inlet side of the septic tank has roots growing at the base of the risers, and the pump tank risers are leaking. We recommend excavating and resealing all risers, inlets and outlets, and wedge lid doors on the septic tank and pump tank. The distribution box is located very close to the edge of the driveway and appears to there has been traffic over the distribution box, header lines and drainfield. We recommend relocating the driveway away from the distribution box, or taking other measures to ensure it is not driven over in the future | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/09/2021 | 03:25 PM
02/28/2020 |  | Follow-Up | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 | Approved | EHD - Fairfax | Ace Contracting Services Inc | 1942001120 | Lawrence | Fellenz Jr. | 1.000000 |  | Puraflo | none | Gravity | Gravity |  | Not Applicable |  |  |  | NA | [9 empty] | 101.000000 | [5 empty] | Will be sent separately | Inspected | BOD Results | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 |  | 06/29/2021 | Jan 1 1900 10:39PM
07/11/2020 |  | RoutineScheduled | 153-STS-20180 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Wastemaster Inc |  | Timothy | Jenkins | 2.000000 |  | ATU |  | Pump | Gravity | Discharge | Chlorination |  | [] | [] |  | Musty | Clear | 6.800000 | 5.300000 |  | 2.200000 |  |  |  | 14.000000 |  |  | 8.400000 |  |  | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 03:05 PM
06/25/2020 |  | Routine/Scheduled |  | Warren | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Review | EHD - Lord Fairfax | POWELLS PLUMBING, INC. | 1942001036 | Kurt | Holthaus | 1.000000 | 1500 | Microfast |  | Pump | Drip | Drip Tubing |  | 450.000000 | ["Sludge/Scum Accumulation"] |  | N/A | [17 empty] | Annual Inspection - Microfast processing tank needs pumped due to sludge accumulation. Serviced spin filter | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. |  | 07/09/2020 | 01:07 PM
02/27/2020 |  | Routine, Scheduled | 145-97-0072 (LEGACY ALT. SYSTEM) | Highland County | This AOSS should now return to normal function after having provided the above stated routine maintenance. | Approved | EHD - Central Shenandoah |  |  |  |  | 2.000000 | 2000 |  | Sandfilter, Recirculating | Pump | Manifold | Aggregate Trench | None |  | ["Level Sensor Operation"] | ["Level Sensor Operation"] | [18 empty] | [Comments]: The system did not need to be pumped. There were no visible leaks in the leech field. The float wires had been chewed on by mice. The wires were repaired. A visible hole in the riser was repaired where the mice were apparently getting in. The sand filters were inspected and operating as designed. The lids were properly secured. | This AOSS should now return to normal function after having provided the above stated routine maintenance. |  | 03/10/2020 | 30-12-1899 04:08 PM
06/03/2020 | Alternative | Routine/Scheduled | 159-04-300 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | Ecoflo | None | Pump | Distribution Box | Aggregate Trench | None |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | Ecoflo Biofilter has severely deteriorated and is no longer properly filtering water; the Distribution Box was not located and we will attempt to locate it during our next scheduled visit -- Homeowner has replaced Biofilter | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 06/10/2020 | 05:02 PM
07/30/2020 |  | RoutineScheduled | 181-02-0335 (LEGACY ALT. SYSTEM) | Rockbridge | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1500 | Septic Tank Only | Advantex AX 20 | Pump | Gravity | Trenches | Not Applicable |  | ["Dispersal System Operation"] | [] | NO | [17 empty] | The system did not need to be pumped. The leech field had been run through for several years with a tractor causing two out of three chamber lines to collapse. It was also determined by and engineer that the leech field was under designed and needed more linear feet. Test holes were dug on the property for a drip field. The land owner advised me that he wanted to get bids on the drip field. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. |  | 02/04/2021 | 07:45 PM
04/14/2020 |  | Reportable Incident | 175-16-0385 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green | [9 empty] | ["Disinfection"] | ["Disinfection"] | [18 empty] | Replaced UV Bulb, cord & test tube. | This AOSS should now return to normal function after having provided the above state routine maintenance |  | 04/14/2020 | 02:00 PM
12/10/2020 |  | RoutineScheduled | SWP-03-300 | Stafford | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Attached Growth Medium"] | ["Recirculation Pump" ,"Attached Growth Medium"] | NA | [15 empty] | Will be sent separately | Inspected | Cleaned clogged recirculation filter. Roots are growing around the RSV valve on your Advantex system. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/09/2021 | 03:25 PM
04/01/2020 |  | Routine, Scheduled |  | Loudoun County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | None | None | Pump | Manifold | [24 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/12/2020 | 02:21 PM
07/21/2020 |  | Reportable Incident | 2001-143-0121 | Henrico | This AOSS should now return to normal function after having provided the above state routine maintenance | Approved | EHD - Henrico | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1500 | Orenco Advantex | None | Pump | Drip | Drip Tubing | None | 450.000000 | ["Dispersal System Operation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Recirculation Pump","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | Musty | Clear | [15 empty] | Pump tank pumped empty for storage - Alarm event - found discharge tank in high level condition - system evaluation indicates that the K-rain hydraulic splitter valve is not rotating / camming as designed - pump dead heading against valve and not moving effluent to drip fields. Valve disassembled, dosing both drip fields at same time - new valve ordered. | This AOSS should now return to normal function after having provided the above state routine maintenance |  | 07/22/2020 | 07:45 AM
04/22/2020 |  | Routine, Scheduled | 109-08-0517 | Bedford County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Central | WAUGH, IAIN C | 1942001512 | IAIN | WAUGH | 1.000000 | 1500 | Septic Tank Only | Orenco Advantex | Gravity | Distribution Box | Gravel-Less Trench | None |  | ["Attached Growth Medium","Effluent Screens"] | ["Attached Growth Medium","Effluent Screens"] | [18 empty] | [Pumpout Comments]: No pumping at this time [Comments]: Septic/recic zone 3-4" scum 8" sludge Discharge zone 16" sludge Cleaned Recirc spiltter valve, Biofilter Flushed and brushed sprayer manifold Checked all floats and alarm - all functional Ran system in test mode No major alarms in history - All good | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/23/2020 | 10:16 PM
12/19/2020 |  | RoutineScheduled | {FIPSCode}-STS-83101 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Wastemaster Inc |  | Timothy | Jenkins | 2.000000 |  | Recirculating Sand Filter | P04 Removal | Pump | Gravity | Discharge |  |  | [] | [] | [18 empty] | No Discharge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 01/14/2021 | 09:45 AM
01/16/2020 |  | Routine, Scheduled | 234-15-418 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesapeake | R & K Septic, Inc. |  | John | Butt, Jr |  |  | Clearstream ATU |  | Pump | Drip | Elevated Sand Mound | UV Light |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] |  |  | 5.53 | 7.880000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/16/2020 | Jan 1 1900 9:15AM
05/07/2020 |  | RoutineScheduled | SD-08-147 | Fauquier | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Control Operation" ,"Distribution Pump Operation"] | ["Control Operation" ,"Auxiliary Filter" ,"Distribution Pump Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Post for control panel now wobbles and top backer board has rotted loose. Needs to be replaced. No infiltration observed today, but Vericomm panel did call in for extremely high recirculating override cycles after/ during a big rain on April 25th. Measured 35 psi on center ARV (supply for lower zone) and 32 psi on left ARV (common return). Measured 27 psi on right ARV (supply for upper zone) and 23 psi on left ARV (common return). In the past 30 days, system averaged 11.0 discharge cycles per day but at only 1.8 minutes per cycle. Adjusted run and rest times slightly to try and get a little bigger cycle to the dripfield. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
02/17/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Fairfax | SEAMON, CHARLIE L | 1942001108 | CHARLIE | SEAMON |  |  | Septic Tank Only | Puraflo | Pump | Manifold | Aggregate Trench | None |  | ["None"] | ["None"] | [18 empty] | [Comments]: Performance Inspection: Puraflo to LPD Drainfield Septic tank-6"sludge 0"scum/Pump tank to Puraflo 1"sludge/Pump Tank to LPD-2"sludge. Puraflo Panel- cc1-8032 ETM-285.78/cc2-8204 ETM-278.70/ Discharge LPD Panel is demand dose no counts or ETM. System does not need a pump out at this time. LPD Pumps Zoeller-295 16.6A 124gpm. Drainfield area good. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/19/2020 | Jan 1 1900 6:08AM
10/17/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | The alternative septic system was inspected . The state requires that all alternative septics must be inspected EVERY year and filed with the state and county. The septic control panel is an exterior time dose panel. There are 3 cleanouts. The sewer line was camera snaked and was clear. The septic tank was pumped out. The atu air blower was inspected and filter cleaned. The pump tank, pump, floats and force main were inspected. The hydraulic unit were the spin filters and water meter are was inspected. The drain field was walked over and no issues were seen. At time of inspection all components were in working condition. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/14/2021 | 04:27 PM
10/23/2020 |  | RoutineScheduled | 04-197-065 | Wise |  | Approved | EHD - Lenowisco | VDH | [15 empty] | Pungent | Clear | 7.500000 | 0.000000 | [13 empty] | Aerator was making a noise, but no signs of air getting to the chamber |  |  |  | 12:00 AM
11/03/2020 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | McKim Construction | 1942001330 | Michelle | McKim | 2.000000 | 2500 septic | 2000 pump tank |  | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 11/05/2020 | 12:00 AM
01/08/2020 |  | Routine, Scheduled | 12-120-0189AR | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesterfield | CARRINGTON, JOHN W, SR | 1934000128 | JOHN | CARRINGTON |  |  | Norweco Singulair ATU | None | Pump | Distribution Box | None | None |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles"] | [18 empty] | [Comments]: The Norweco treatment tank needs cleaning at this time. The Norweco aerator and filer was cleaned. Lab results not reported by Operator, EHS chose "No" in order to allow saving updated entry. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/14/2020 | Jan 1 1900 9:22AM
02/24/2020 |  | Routine, Scheduled | 179-13-0228-SWP | Stafford County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | None | Pump | Distribution Box | Aggregate Trench |  |  | ["Attached Growth Medium","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Recirculation Pump"] | ["Distribution Pump Operation","Effluent Screens","Recirculation Pump"] | [18 empty] | [Comments]: The pump line is exposed near the distribution box. We recommend covering it with at least 12" of soil. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/06/2020 | 02:45 PM
10/08/2020 |  | RoutineScheduled | 179-16-0186-SWP | Stafford | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Septic Works LLC | 1942001080 | michael | smith |  |  | Orenco Advantex | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/25/2021 | 08:10 AM
10/20/2020 |  | RoutineScheduled | 182-02-0481 (LEGACY ALT. SYSTEM) | Rockingham | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Central Shenandoah | Onsite Wastewater Services - May Supply | 1942001627 | Drew | Shull | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Pressure | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/28/2021 | 05:41 AM
02/06/2020 |  | Routine, Scheduled | 05-177-1188 | Pulaski County | This AOSS should now return to normal function after having provided the above stated routine maintenance. | Approved | EHD - New River | KING, DAVID A | 1942001094 | DAVID | KING | 2.000000 |  | PremierTech, STB | Septic Tank Only | Pump | Distribution Box | Gravel-Less Trench | None | 75.000000 | ["Attached Growth Medium","Effluent Screens"] | ["Attached Growth Medium","Effluent Screens"] | [18 empty] | [Comments]: Raked peat, cleaned Effluent Screen, system is working correctly. | This AOSS should now return to normal function after having provided the above stated routine maintenance. |  | 02/12/2020 | 08:03 AM
12/07/2020 |  | RoutineScheduled | 181-12-0021 | Rockbridge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Hunter E. Ayres, General Contractor | 1942001166 | Hunter | Ayres | 4.000000 | 6000 | Biomicrobics MicroFAST | Biomicrobics MicroFAST | Pump | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","Effluent Screens"] | ["Auxiliary Filter","Effluent Screens"] | YES | [17 empty] | Filters checked and cleaned. Control panels, floats and pumps all functioning properly. System did not need to be pumped. No apparent leaks in system or drain field area. Lids properly secured | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 01/08/2021 | 07:55 AM
05/05/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | SES MidAtlantic LLC | 1942001203 | James | Green |  |  | Best 1 | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Effluent Screens"] | ["BlowerCompressorAerator Operation" ,"Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/15/2021 | 09:00 AM
10/07/2020 |  | RoutineScheduled |  | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001301 | Joshua | Hott | [9 empty] | [] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
06/03/2020 |  | RoutineScheduled | 179-12-0276-SR | Stafford | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Effluent Screens" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Effluent Screens" ,"Recirculation Pump"] | YES | [15 empty] | Will be sent separately | Inspected | As noted previously, the RSV is leaking around the pitless adapter. We have adjusted the pump settings to compensate for this, but we recommend replacing the RSV and split flow tee | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 |  | 04/09/2021 | 03:25 PM
09/19/2020 |  | RoutineScheduled | 109-07-0039 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1000 | Advantex |  | Gravity | Gravity | Trenches |  |  | ["None"] | ["None"] | [18 empty] | 12" of solids in septic tank. Flushed treatment unit spray manifold. Cleaned recirculation basket filter. Tested floats, pump and alarm. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 10/12/2020 | 07:00 PM
04/01/2020 |  | Follow-Up |  | Loudoun County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | None | None | Pump | Distribution Box | [23 empty] | [Comments]: The d-box replacement permit was issued and a new 8 port concrete d-box with speed levelers was installed. Loudoun County inspected and it was backfilled, seeded and strawed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/12/2020 | 02:21 PM
08/14/2020 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | EcoPod | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Conventional septic system | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 |  | 04/14/2021 | 04:27 PM
01/03/2020 |  | Routine, Scheduled | 093-03-0092 | Isle of Wight County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Western Tidewater | R & K Septic, Inc. |  | John | Butt, Jr |  |  |  |  | Pump | Distribution Box |  | None |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] |  |  | 7.48 | 7.540000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/03/2020 | Jan 1 1900 9:45AM
09/05/2020 |  | RoutineScheduled | 2008-01-153 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Wastemaster Inc |  | Timothy | Jenkins | 2.000000 |  | PuraFlo |  | Pump | Gravity | Discharge | Chlorination |  | [] | [] | YES | Musty | Clear | 7.800000 |  |  | 1.400000 | [11 empty] | Contact Tank Scum o | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 09/11/2020 | 12:00 PM
12/03/2020 |  | Routine/Scheduled | 11-120-0116ACR | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesterfield | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1500 | Biomicrobics MicroFAST |  | Pump | Drip | Drip Tubing | None | 600.000000 |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | Musty | Clear | [15 empty] | Routine Service Trash Tank - normal level Aeration Tank - normal level - air compressor serviced. Pump Tank - normal level - pump, float sensors, & controls operating properly. Drip Field - 2 Zone - Automatic - headworks serviced - disk filters serviced - field flushed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 12/04/2020 | Jan 1 1900 7:30AM
10/23/2020 |  | RoutineScheduled | 14-184-055 | Scott | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | EHD - Lenowisco |  |  | John | Hyder |  |  | Eco-Pure Peat Moss Biofilter |  | Gravity |  |  | UV | 450.000000 |  |  |  | None | Clear | 8.000000 | 6.000000 | [13 empty] | No laboratory tests performed. Field inspection only. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 10/23/2020 | 12:00 AM
06/12/2020 |  | RoutineScheduled | 162-07-0154 | Nelson | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Blue Ridge | Onsite Wastewater Services - May Supply | 1942001022 | Sara | Tusing | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | DREW DID INSPECTION SET REPLACED PUMP | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/28/2021 | 05:41 AM
08/28/2020 |  | RoutineScheduled | 07-120-0630A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Wastemaster Inc |  | Timothy | Jenkins | 2.000000 |  | Advantex |  | Pump | Pressure | Drip |  |  | [] | [] | [18 empty] | In for alarm. Found all levels normal. GOing into low level alarm with recirculating pump on cycle. Biofilter clogged. Performed annual cleaning and service of system. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 09/15/2020 | Jan 1 1900 2:15PM
08/12/2020 |  | RoutineScheduled | 061-18-432 | Fauquier | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [7 empty] | 08/12/2020 | [7 empty] | Will be sent separately | Inspected | Routine inspection. Collected first sample for BOD test. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
10/24/2020 |  | RoutineScheduled | SD-86-373 | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Wastemaster Inc |  | Timothy | Jenkins | 2.000000 |  | ATU | Polishing Sand Filter |  | Gravity | Discharge | Chlorination |  | [] | [] |  | Musty | Clear | 6.900000 |  |  | 1.700000 | [12 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 11/06/2020 | 11:40 AM
09/01/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Middle module ponding. Recommend installing ball valves on manifolds to better regulate flow | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/27/2021 | 01:26 PM
09/02/2020 |  | RoutineScheduled |  | Warren | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | Panel alarm was turned off but was corrected | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance |  | 04/26/2021 | 09:04 AM
08/04/2020 |  | RoutineScheduled | 181-05-0374 | Rockbridge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Hunter E. Ayres, General Contractor | 1942001166 | Hunter | Ayres | 2.000000 | 3000 | Biomicrobics MicroFAST |  | Pump | Pressure | Drip |  |  | ["Auxiliary Filter","Effluent Screens"] | ["Auxiliary Filter","Effluent Screens"] | YES | [17 empty] | All filters checked and cleaned. Control panels functioning properly. No apparent leaks in system or drain field area. Septic system did not need to be pumped. Lids properly secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 08/15/2020 | 04:15 PM
04/10/2020 |  | Routine, Scheduled | C102-07-0035 | Alleghany County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Alleghany-Roanoke | AYRES, HUNTER E | 1942001166 | HUNTER | AYRES | 1.000000 | 1500 | Septic Tank Only | Orenco Advantex | Pump | Drip | Drip Tubing | None |  | ["None"] | ["None"] | [18 empty] | [Comments]: filters checked and cleaned. No apparent leaks in system or drain field area. System did not need to be pumped. Pump vault, filter and screen cleaned. Textile sheets checked and sprayed off. Control panel functioning properly. Textile sheets in good condition. Lids properly secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/13/2020 | Jan 1 1900 9:44AM
04/29/2020 | Alternative |  | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | McKim Construction | 1942001330 | Michelle | McKim | 2.000000 |  |  |  | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 10/23/2020 | Dec 30 1899 3:15AM
05/21/2020 |  | Reportable Incident |  | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  |  |  | ["Control Operation","Disinfection"] | ["Control Operation","Disinfection"] | N/A | [17 empty] | Replaced UV Bulb, pressure gauge on supply line, buzzer. | This AOSS should now return to normal function after having provided the above state routine maintenance |  | 05/21/2020 | Jan 1 1900 3:00PM
07/13/2020 |  | Reportable Incident | 15-142-0093 | Hanover | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chickahominy | Atlee Sewage Disposal, LLC | 1942001144 | Francis | Frere | 1.000000 | 1850 | Clearstream ATU |  | Pump | Pressure | Pad | Not Applicable | 600.000000 | ["Control Operation","Dispersal System Operation"] | ["Control Operation","Dispersal System Operation"] | NA | None | Clear | [14 empty] | Pumped Out |  | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 07/31/2020 | Jan 1 1900 9:30AM
05/12/2020 |  | RoutineScheduled | 177-06-0074-SP | Spotsylvania | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation" ,"Level Sensor Operation" ,"Control Operation"] | ["Distribution Pump Operation" ,"Control Operation" ,"Level Sensor Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Needs new Orenco Durafiber lid on inlet end of recirc tank. Orenco vent/ grate has uv damage and needs replaced. Top riser on discharge tank has a hole in it right at grade. Needs patched or replaced. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
09/21/2020 |  | RoutineScheduled | SD-10-247 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Environmental Systems Service | 19420001050 | Troy | Jenkins | 2.000000 |  | Septic Tank | Septic Tank |  | Pressure | Drip |  | 30.000000 | [] | [] |  |  |  | 7.180000 |  |  |  |  | 09/21/2020 | Sample Tap | 2.000000 |  |  | 1.500000 | 15.220000 |  | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 02:45 PM
02/11/2020 |  | Routine, Scheduled | 11-100-0021 | Accomack County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Eastern Shore | DUER, PETE C | 1942001051 | PETE | DUER | 1.000000 | 750 | Septic Tank Only | Puraflo | Pump | None | None | None |  | ["None"] | ["None"] | [18 empty] | [Comments]: Aoss Inspection. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/13/2020 | 10:39 AM
06/04/2020 |  | RoutineScheduled | SP-05-307 | King George | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Recirculation Pump" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Control Operation" ,"Dispersal System Operation" ,"Auxiliary Filter" ,"Attached Growth Medium" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Level Sensor Operation"] | ["SludgeScum Accumulation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Control Operation" ,"Auxiliary Filter" ,"Attached Growth Medium" ,"Effluent Screens" ,"Recirculation Pump" ,"Septic Tank Baffles"] | YES | [15 empty] | Will be sent separately | Inspected | Advantex tank needs pumped. A flow meter needs to be installed. Proposal to be sent to homeowner. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
08/27/2020 |  | Follow-Up |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Gravity | Gravity |  | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | D-box was replaced | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 |  | 04/14/2021 | 04:27 PM
11/16/2020 |  | Routine/Scheduled | 03-120-0734AR | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesterfield | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | Orenco Advantex |  | Pump | Drip | Drip Tubing | None | 600.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | None | Clear | [15 empty] | Routine service Primary septic tank - normal operating level Processing Tank - normal operating level - RSV, recirc. pump, & effluent screen serviced. Treatment Module - media drapes & spray grid serviced. Discharge Tank - pump serviced, float sensors & controls operating properly. Drip Headworks - drip screen serviced, drip field flushed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 11/17/2020 | Jan 1 1900 7:00AM
11/17/2020 |  | RoutineScheduled | 165-STS-335060 | Rockingham | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Central Shenandoah | Onsite Wastewater Services - May Supply | 1942001627 | Drew | Shull | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Broken elbow in pump tank and air relief valve needs replaced. Repair done inspection by Ds | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/28/2021 | 05:41 AM
05/11/2020 |  | Routine/Scheduled | 10-120-0056AR | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. |  |  | Bionest |  | Pump | Drip |  |  |  | ["Attached Growth Medium","Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Attached Growth Medium","Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 05/11/2020 | Jan 1 1900 11:00AM
07/27/2020 |  |  | {FIPSCode}-STS-21106 | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | ["None"] | ["None"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 07/28/2020 | 12:00 AM
04/02/2020 |  | Reportable Incident | 179-16-0209-SPWT | Stafford County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | None | None | Pump |  |  |  |  | ["Distribution Pump Operation","Level Sensor Operation"] | ["Distribution Pump Operation","Level Sensor Operation"] | [18 empty] | [Comments]: Panel alarmed for low level in pump tank. Replaced timer float that was intermittently sticking on. Zoeller tri-check assembly was leaking at check valve gasket. Replaced with individual components: brass check valve, ball valve, and sch 80 union. Flushed the spin filter and drip field. Added water back to the pump tank to get it out of low level alarm. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/27/2020 | 04:14 AM
01/15/2020 |  | Routine, Scheduled | 12-177-1030 | Pulaski County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - New River | Conner, Timothy Wayne | 1942001003 | Timothy | Conner | 1.000000 |  | Microfast | None | Gravity | Distribution Box | None | None | [21 empty] | [Comments]: EVERYTHING APPEARS TO BE FUNCTIONING PROPERLY AT THIS TIME. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/10/2020 | 11:18 AM
11/19/2020 |  | RoutineScheduled |  | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Catoctin Environmental |  | Cameron | Creighton | 2.000000 | 1500 | Microfast |  | Pump | Pressure | Drip | UV |  | [] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 11/20/2020 | 12:00 AM
08/24/2020 | Alternative | RoutineScheduled | 10-167-038 | Nottoway | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Piedmont | Bryant Farms | 1965005795 | Raymond | BRYANT JR. |  |  |  |  | Gravity | Pressure |  |  |  | ["None"] | ["None"] |  | None | Clear | [15 empty] | None Due | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 08/24/2020 | Dec 30 1899 10:00AM
01/17/2020 |  | Routine, Scheduled | 07-163-0042 | New Kent County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chickahominy | Braxton, Corey Vance | 1942001039 | Corey | Braxton |  |  | Orenco Advantex | None | Pump | Distribution Box | None | None |  |  | ["Attached Growth Medium","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump"] |  | None | 7.3 | 6.800000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/18/2020 | Jan 1 1900 7:14PM
01/27/2020 |  | Follow-Up |  | Manassas | This AOSS should now return to normal function after having provided the above stated routine maintenance. | Paid | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green | [9 empty] | ["Level Sensor Operation"] | ["Level Sensor Operation"] | [18 empty] | [Comments]: Replaced off & on floats. | This AOSS should now return to normal function after having provided the above stated routine maintenance. |  | 01/27/2020 | 04:00 PM
06/03/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | SES MidAtlantic LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/15/2021 | 09:00 AM
05/07/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/14/2021 | 04:27 PM
03/06/2020 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 | Approved | EHD - Fairfax | Soils, Inc. | 1942001004 | Mark | Smith |  |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Drip | UV |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 |  | 05/31/2021 | Jan 1 1900 9:08AM
05/12/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Delta Environmental Products, DF Series | Delta Environmental Products, DF Series | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/27/2021 | 01:26 PM
09/16/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/27/2021 | 01:26 PM
07/14/2020 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | Drainfield looks much better than last year. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 04/13/2021 | Jan 1 1900 11:22AM
05/27/2020 |  | RoutineScheduled | 182-04-0070 | Rockingham | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Central Shenandoah | Onsite Wastewater Services - May Supply | 1942001627 | Drew | Shull | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Pressure | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/28/2021 | 05:41 AM
03/31/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS should now return to normal function after having provided the above stated routine maintenance. | Paid | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green | [9 empty] | ["None"] | ["None"] | [18 empty] | [Comments]: Repaired clean out.Lime applied to affected area. | This AOSS should now return to normal function after having provided the above stated routine maintenance. |  | 03/31/2020 | Jan 1 1900 1:30PM
11/20/2020 | Alternative | Initial Visit | 128-08-0184 | Essex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | Biomicrobics MicroFAST | None | Pump | Drip | Drip Tubing | None | 450.000000 |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | Musty | Clear | [15 empty] | Initial Visit - Real Estate Inspection Primary Septic Tank - normal operation level Aeration Tank - normal operating level - compressor serviced. Pump Tank - normal operating level - pump, float sensors & controls operating properly. Drip headworks serviced - field flushed - drip screen replaced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 11/23/2020 | 09:00 AM
06/16/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Sale inspection on a alternative septic system. In the state of Virginia all alternative septic systems must be inspected every year between Jan 1st and July 1st and filed with the state and county. The septic control panel is a timed dose. there is 1 pvc clean out near the house. The pvc sewer line was camera snaked and was clear. The septic tank was pumped out and the tank inspected for any cracks or leaks and none were found. There is a filter in the septic tank that was cleaned. The manufacture recommends cleaning it every 6 months. The pump tank, pump, floats and force main were inspected. All 5 purflo pods were were opened up and each one was dug down to the bottom to check for any standing effluent and none were found. The 8 port concrete d-box was dug up and the header lines were camera snaked. all were clear. the drain field was probed and was dry. At time of inspection all inspected components were in working condition. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/14/2021 | 04:27 PM
10/14/2020 |  | Routine/Scheduled |  | Frederick | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Lord Fairfax | POWELLS PLUMBING, INC. | 1942001036 | Kurt | Holthaus | 1.000000 | 750 | Sandfilter, Recirculating |  | Pump | Distribution Box | Aggregate Trench |  | 360.000000 | ["Dispersal System Operation"] | ["Dispersal System Operation"] | N/A | [17 empty] | Annual Inspection - Media was cleaned and raked by others. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 11/17/2020 | 11:19 AM
11/05/2020 |  | RoutineScheduled | C-122-17-0024 | Craig | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Alleghany-Roanoke | King's Alternative Septic | 1942001112 | William | King, II | 1.000000 | 1000 | Biomicrobics Microfast 0.5 |  | Gravity | Gravity | Trenches | UV | 250.000000 | ["Disinfection"] | ["Disinfection"] | NA | [17 empty] | Cleaned UV light, system is working correctly. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 11/17/2020 | 12:00 AM
06/03/2020 |  | Routine, Scheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Biomicrobics MicroFAST |  |  |  |  | None |  | ["Blower/Compressor/Aerator Operation"] | ["Blower/Compressor/Aerator Operation"] |  | Good | Clear | [15 empty] | Pump 1 Amps 10.99 ETM 41 hrs 33 mins Cycles 859 Pump 2 Amps 9.10 ETM 40 hrs 45 mins Cycles 834 Septic Sludge 4" Scum 4" ATU Sludge 3" Scum 0 Pump Sludge 1" Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 06/03/2020 | Jan 1 1900 10:13AM
11/06/2020 |  | RoutineScheduled | 04-197-A4 | Wise | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | Wise Health Dept |  | Rodney | Neece |  |  | AtU |  | Gravity | Gravity | Discharge | Chlorination |  |  |  |  | None | Clear | 6.600000 | 0.000000 |  | 0.000000 | Tables are good | [11 empty] | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 11/09/2020 | 12:00 AM
06/19/2020 |  | RoutineScheduled | 177-06-0458-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Effluent Screens" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Effluent Screens" ,"Recirculation Pump"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 |  | 04/09/2021 | 03:25 PM
01/17/2020 |  | Routine, Scheduled | SWP-05-499 | Stafford County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001350 | Mike | Cook | 1.000000 |  | Puraflo | None | Pump | Distribution Box | Aggregate Trench |  |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | [Comments]: small tree by last pod needs removed. home owner will take care of this in spring | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/28/2020 | 01:39 PM
03/09/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Paid | EHD - Fairfax | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Puraflo | None | Pump | Distribution Box | Aggregate Trench |  |  | ["Dispersal System Operation"] | [19 empty] | [Comments]: The distribution box side walls are starting to cave in. Plugs have come loose & effluent is leaking into the soil. We recommend contacting an installer for replacement of the distribution box.We also recommend replacing the alarm horn on the dispersal pump control panel. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 04/06/2020 | Jan 1 1900 2:45PM
02/19/2020 |  | Routine, Scheduled | 136-06 0128 | Gloucester County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers | LANGFORD, CHARLES T | 1934000143 | CHARLES | LANGFORD | 1.000000 | 1250 | Clearstream | Septic Tank Only | None | None | None | None |  | ["None"] | ["None"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/02/2020 | 10:39 AM
07/29/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 2.000000 |  | none | none | Gravity | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/27/2021 | 01:26 PM
01/17/2020 |  | Routine, Scheduled |  | Loudoun County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim |  |  | Orenco Advantex | None | Pump | Distribution Box | Aggregate Trench | [22 empty] | [Comments]: The septic and recirc tank need pumed out | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/02/2020 | 04:43 AM
11/09/2020 | Alternative | Routine/Scheduled | 136-08-0123 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1500 | Biomicrobics MicroFAST |  | Pump | Drip | Drip Tubing | None | 450.000000 |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | Musty | Clear | [15 empty] | Real Estate Inspection Trash Tank - normal operating level Aeration Tank - normal operating level - compressor serviced. Pump Tank - normal operating level - pump serviced, float sensors, and controls operating properly. Drip Headworks - serviced, drip screen serviced, drip field flushed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 11/10/2020 | 07:45 AM
09/11/2020 |  | Routine/Scheduled | 01-172-0468A | Powhatan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. |  |  | Orenco Advantex |  | Pump |  |  |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump","Sludge/Scum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump","Sludge/Scum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 09/11/2020 | Jan 1 1900 11:00AM
09/11/2020 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump | Drip | Elevated Sand Mound | UV Light |  | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  | 5.79 | 7.810000 | 5.600000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 09/11/2020 | Jan 1 1900 2:30PM
01/06/2020 |  | Routine, Scheduled | 179-16-0257-SP | Stafford County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Orenco Advantex | None | Pump | Distribution Box | Aggregate Trench |  |  | ["Attached Growth Medium","None","Recirculation Pump"] | ["Attached Growth Medium","None","Recirculation Pump"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/04/2020 | 07:46 AM
12/07/2020 |  | RoutineScheduled | SWP-04-557 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Attached Growth Medium" ,"Dispersal System Operation"] | ["Dispersal System Operation" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter" ,"Attached Growth Medium"] | NA | [15 empty] | Will be sent separately | Inspected | Semi-annual inspection. Defective blower was replaced. | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 |  | 04/09/2021 | 03:25 PM
09/01/2020 |  | RoutineScheduled | 03-160-0132 | Montgomery | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - New River | King's Alternative Septic | 1942001112 | William | King, II | 2.000000 | 2000 | Biomicrobics Microfast.5 |  | Pump | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Distribution Pump Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Distribution Pump Operation"] | NA | [17 empty] | Replaced blower and distribution pump, cleaned spin filter; system is working correctly. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 10/23/2020 | 12:00 AM
09/19/2020 |  |  |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | dovel enterprises |  | jerry | dovel | 2.000000 | 1000 | 1000 |  | Pump | Pressure | Drip | Not Applicable | 0.000000 | [] | [] | YES | Septic | Clear | [14 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 10/09/2020 | 12:00 AM
02/19/2020 |  | Routine, Scheduled |  | Loudoun County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | Delta Environmental Products, DF Series | None | Gravity | Drip | Drip Tubing | [22 empty] | [Comments]: Sale inspection of a alternative septic system. The septic control panel is a exterior time dose. There a 2 pvc cleanouts. The sewer line was camera snaked and was clear. The septic tank has a plastic riser on the outlet side and was pumped out. The septic tank was inspected for any cracks or leaks and none were found. The ATU tank, air blower and control panel were inspected. Just a note the air blower and panel are inside the home. The pump tank, pump, floats and force main were inspected. The pump tank is going to need pumped out. The hydraulic unit is in working condition. The drain fields was walked and no wet or soft spots were noted. At this time the septic system is not in working condition. The pump tank needs to be pumped out. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/02/2020 | 04:43 AM
12/03/2020 |  | RoutineScheduled | SD-07-163 | Orange | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  | ["Attached Growth Medium" ,"Control Operation" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | ["Attached Growth Medium" ,"Control Operation" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
03/27/2020 |  | Reportable Incident | 061-16-250 | Fauquier County | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001068 | David | Stewart | 5.000000 |  | Bio Barrier | Bio Barrier | Pump | Drip | Drip Tubing |  |  | ["Dispersal System Operation","Distribution Pump Operation"] | ["Dispersal System Operation","Distribution Pump Operation"] | [18 empty] | [Comments]: Mulch plant lift station in high level. Pulled both E1 grinder pumps and had rebuilt. Force main appeared to be air-locked, released air. Appeared to be working fine afterwards. Suspect new construction may be causing the issue. Repaired 2 leaks in zone 2 of the dripfield. Performed detailed inspection of surge tank and discovered multiple points of infiltration. Will send repair estimate for resealing to airport manager. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 04/27/2020 | 04:14 AM
04/15/2020 | Alternative | Routine/Scheduled | 157-14-0054 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | [9 empty] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | Serviced system. Checked the pump, panel, & floats (ok). Cleaned the filter and the diffuser in the Clearstream and cleaned the filter in the aerator. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 04/15/2020 | 12:00 PM
07/27/2020 |  | Routine, Scheduled | 175-17-0444 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Biomicrobics MicroFAST |  | Pump | Drip | Drip Tubing | UV Light |  | ["Blower/Compressor/Aerator Operation"] | ["Blower/Compressor/Aerator Operation"] |  | Good | Clear | [15 empty] | Pump Amps 7.9 ETM 1417 hrs 40 mins Cycles 6476 Septic Sludge 2" Scum 1" ATU Sludge 0 Scum 0 Pump Sludge 0 Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 07/27/2020 | 01:00 PM
01/17/2020 |  | Routine, Scheduled |  | Page County | This AOSS should now return to normal function after having provided the above stated routine maintenance. | Paid | EHD - Lord Fairfax | Cubbage, Harrison Lee, II | 1942001021 | Harrison | Cubbage | 1.000000 | 1500 | Septic Tank Only | Biomicrobics MicroFAST | Pump | Drip | Drip Tubing | None |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] |  | Musty | Clear | [15 empty] | [Comments]: All tanks pumped and discharge pump was replaced. Pump Settings: Off 2.5Hr On 10min | This AOSS should now return to normal function after having provided the above stated routine maintenance. |  | 01/18/2020 | 01:58 PM
05/22/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | none | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/27/2021 | 01:26 PM
11/19/2020 |  | RoutineScheduled | 37821 | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | Musty |  | 7.330000 | 6.810000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 11/24/2020 | 05:00 PM
05/27/2020 |  | RoutineScheduled | {FIPSCode}-STS-17672 | Frederick | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["Control Operation" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | Will send estimate for pumping and riser installation we discussed on next inspection | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/26/2021 | 09:04 AM
12/16/2020 |  |  | 167-STS-15451 | Russell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 12/16/2020 |  | 16.300000 |  |  | 2.600000 |  |  | Attached to this report |  | BOD: 16.3 TSS: 2.60 | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12/16/2020 | Jan 1 1900 12:30PM
11/20/2020 |  | RoutineScheduled | 187150221 | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax |  |  | Michael | Edmonson | 1.000000 | 1250 | Microfast | none | Pump | Pressure | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 01/01/2021 | 02:15 PM
08/31/2020 |  | Initial Visit | 06-120-0795AR | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesterfield | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1250 | Orenco Advantex |  | Pump | Distribution Box | Aggregate Trench | None | 600.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | None | Clear | [15 empty] | Last known inspection conducted 2014 - Initial Inspection Primary septic tank - normal operating level. Processing Tank - normal operating level - RSV, Recirc. pump and effluent screen serviced. Treatment Module - media drapes and spray grid serviced. Discharge Tank - discharge pump serviced, float sensors and controls operating properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 09/02/2020 | Jan 1 1900 2:30PM
12/16/2020 |  | RoutineScheduled | 05-142-0100 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Lyttle Service Co., LLC dba Stamie E. Lyttle Co | 1942001332 | Benjamin | Chapin | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12/16/2020 | 12:00 AM
05/08/2020 |  | RoutineScheduled | 2126-09-153 | Prince William | This AOSS is functioning as designed and in accord | Approved | EHD - Prince William | Wastemaster | 1965-001817 | Tim | Jenkins | 2.000000 |  |  | UV | Pump |  | Discharge | UV |  | [] | [] |  | Musty | Clear | 6.800000 |  |  |  |  | 05/08/2020 |  | 3.000000 |  | 110.000000 | 4.400000 |  |  | Will be sent separately |  |  | This AOSS is functioning as designed and in accord |  | 05/08/2020 | 08:30 AM
07/24/2020 |  | RoutineScheduled | 05-125-003 | Dickenson | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
11/11/2020 |  |  | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Gravity | Pad | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [17 empty] | Septic-8"sludge 5"scum/ microfast-8"sludge/ pump tank-0"sludge/ no pump out needed/ Blower air filter cleaned/ No spongy or breakout areas on the pad area/ Counts: Pump1-481 ETM-16h 52m/ pump2-473 ETM-16h 39m/ Peak-6/ High-7 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
04/10/2020 |  | Reportable Incident | 800-STS-13213 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [9 empty] | 25.000000 | [7 empty] | Owner called due to the alarm going off. Serviced system. Checked the pump, panel, & floats (ok). Cleaned the filter and the diffuser in the Clearstream and cleaned the filter in the aerator. Installed a check valve for the pump. The timer was set at 1.5 minutes every 2 hours it is now set at 2.5 minutes every 2 hours. Took initial BOD sample. NOTE: The BOD Sample was a little high - system should function properly after service. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 04/10/2020 | Jan 1 1900 12:00PM
12/01/2020 | Alternative | Routine/Scheduled | 166-12-058 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 3.000000 | 2500 | Clearstream |  | Pump | Distribution Box | Aggregate Bed |  |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12/01/2020 | 04:30 PM
06/30/2020 |  | Follow-Up | SD-10-208 | Fauquier | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Rappahannock-Rapidan | SES Mid Atlantic | 1942001236 | S. Michael | Lynn | 1.000000 | 20000 | EcoPod | EcoPod | Pump | Pressure | Drip | Not Applicable | 6980.000000 | ["None"] | ["None"] | N/A | Musty | Clear | [5 empty] | 05/28/2020 | Pump Chamber | 12.000000 |  |  | 4.000000 | 53.000000 |  | Will be sent separately |  | 56 houses connected installed 3 new floats in reciorc tank and cleaned solenoids, system not recirculating correctly | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 06/30/2020 | 01:00 PM
02/18/2020 |  | Follow-Up |  | Fairfax County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Fairfax | BLEVINS, JOEL R, SR | 1934000415 | JOEL | BLEVINS |  |  | Microfast | Septic Tank Only | None | None | None | None |  | ["None"] | ["None"] | [8 empty] | 02/18/2020 |  | 72.000000 | [5 empty] | Attached to this report |  | [Lab Comments]: Will be taking another sample in 30 days. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/05/2020 | Jan 1 1900 9:44AM
02/07/2020 |  | Routine, Scheduled | 069080331 | Frederick County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Lord Fairfax | Ferguson, Jeremy | 1942001008 | Jeremy | Ferguson | 1.000000 | 1000 | Puraflo | None | Pump | Drip | Drip Tubing | None |  |  | ["Control Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | [Comments]: Recommended to have st&pt pumped but system is in compliance with approved plans and health department regulations. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/10/2020 | 03:19 PM
08/25/2020 |  | Follow-Up |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Blower replaced. Alarms functioning at time of repair. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/27/2021 | 01:26 PM
11/19/2020 |  |  | 06-142-0350 | Hanover | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chickahominy | Atlee Sewage Disposal, LLC | 1942001144 | Francis | Frere | 1.000000 | 1000 | Best1 |  | Gravity | Gravity | Trenches | Not Applicable | 450.000000 | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["SludgeScum Accumulation","Level Sensor Operation","Control Operation","BlowerCompressorAerator Operation"] | YES | Musty | Cloudy |  |  | 30.000000 | [11 empty] | Pumped Out | Serviced Best1 aerator, pumped all compartments of system, refilled treatment compartment with fresh water. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 11/20/2020 | Jan 1 1900 4:25PM
06/18/2020 |  | RoutineScheduled | 124-STS-2379 | Orange | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 | Rejected | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 |  | 04/09/2021 | 03:25 PM
02/11/2020 |  | RoutineScheduled | 107-13-0145 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Pump | Gravity | Trenches | Not Applicable |  | ["None"] | ["None"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 06/02/2021 | 12:00 AM
09/22/2020 |  | RoutineScheduled | 175-04-0608 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | Aquarobic Services | 1934000142 | Michael | Blake |  |  | none | none | Pump | Gravity | Mound | Not Applicable |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | Air pre-filter cleaned and element for blower canister filter replaced as maintenance. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 07/01/2022 | 10:30 AM
04/02/2020 |  | Routine, Scheduled |  | Buckingham County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Piedmont | CLARK, MICHAEL J | 1934000023 | MICHAEL | CLARK |  |  | Septic Tank Only | Septic Tank Only | None | None | None | None |  |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/12/2020 | Jan 1 1900 4:51AM
03/17/2020 |  | Routine, Scheduled | 16-160-0025 | Montgomery County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - New River | Conner, Timothy Wayne | 1942001003 | Timothy | Conner | 1.000000 | 1000 | Whitewater ATU | None | Gravity | Distribution Box | Aggregate Trench | None | [21 empty] | [Lab Comments]: SAMPLE DUE AT NEXT INSPECTION DATE. [Comments]: EVERYTHING APPEARS TO BE FUNCTIONING PROPERLY AT THIS TIME. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/20/2020 | 10:17 AM
04/15/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 | Approved | EHD - Loudoun | SES MidAtlantic LLC | 1942001203 | James | Green | 2.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Dispersal System Operation"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. Could not inspect pump tank due to condition of lid. Puraflo's ponding. | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 |  | 04/15/2021 | 09:00 AM
05/19/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Loudoun Enviromental | 1942001460 | Austin | Kirkpatrick | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NO | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/28/2021 | 10:17 AM
10/23/2020 |  | Routine/Scheduled | 10-160-0176 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 2.000000 |  | Biomicrobics MicroFAST |  | Gravity | Distribution Box |  | None |  | ["None"] | ["Blower/Compressor/Aerator Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 10/23/2020 | 11:30 AM
02/04/2020 |  | Routine, Scheduled |  | Prince William County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Prince William | Ware, Michele P | 1942001165 | Michele | Ware |  |  | Septic Tank Only | Septic Tank Only | None | None | None | None |  |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | [18 empty] | [Comments]: Sludge Levels: Septic Tank: 5" Pump Tank: 0" | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/05/2020 | 08:43 AM
05/19/2020 |  | RoutineScheduled | 41010 | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Greenway Engineering | 1942001008 | Jeremy | Ferguson | 1.000000 | 1500 | Advantex | none | Pump | Pressure | Drip | Not Applicable |  | ["Control Operation","SludgeScum Accumulation","Level Sensor Operation"] | ["Control Operation","SludgeScum Accumulation","Level Sensor Operation"] | YES | [17 empty] | System is operational | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 09/28/2020 | 11:20 AM
11/04/2020 |  | RoutineScheduled | 175-15-0438 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Pressure | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation"] | NA | [17 empty] | Septic-12"sludge 0"scum/ Microfast-12"sludge, Needs pump out/ Pump tank-0"sludge/ pump intake and spin filter clogged and cleaned both/ geoflo drip rates now 4.8 gpm/ Pump start-22964/ Pump run-2422/ Override-23/ HL-18/ H-18/ Water meter-0139655 | This AOSS should now return to normal function after having provided the above state routine maintenance. |  |  | 12:00 AM
01/17/2020 |  | Routine, Scheduled | 124-STS-2379 | Charles City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Rejected | EHD - Henrico | Old Dominion Onsite, Inc. |  | Russell | Revis | [9 empty] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump"] | [18 empty] | [Comments]: Cleaned RSV and effluent screen. Flushed manifold, checked float and pump operation. System working properly. Suggest pumpout of septic tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/17/2020 | 10:30 AM
10/06/2020 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [11 empty] | N/A | [9 empty] | 4.000000 |  | 718.000000 | [6 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 10/12/2020 | Jan 1 1900 8:30AM
05/27/2020 |  | RoutineScheduled | 179-STS-87294 | Stafford | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Dispersal System Operation"] |  | NA | [15 empty] | Will be sent separately | Inspected | The distribution box is holding water. Owner reported effluent coming to the ground surface. Installer is aware of the issue. | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 |  | 04/09/2021 | 03:25 PM
03/03/2020 |  | RoutineScheduled |  | Warren | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Lord Fairfax | Onsite Wastewater Services - May Supply | 1942001022 | Sara | Tusing | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/28/2021 | 05:41 AM
06/27/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | SES MidAtlantic LLC | 1942001203 | James | Green | 1.000000 |  | EcoPod | none | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. Control panel inside of house did not enter due to Covid19. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/15/2021 | 09:00 AM
11/05/2020 |  | RoutineScheduled | 153-STS-20158 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Wastemaster Inc |  | Timothy | Jenkins | 2.000000 |  | Recirculating Sand Filter |  | Pump | Gravity | Discharge | Chlorination |  | [] | [] |  | Musty | Clear | 6.700000 |  |  | 1.400000 | [12 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 11/20/2020 | 07:03 PM
04/24/2020 |  | RoutineScheduled | SD-12-255 | Fauquier | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Rappahannock-Rapidan | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | [9 empty] | ["BlowerCompressorAerator Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation"] | NA | [17 empty] | Sludge in Septic/ATU- 7" 0" scum in septic and 14" in ATU Septic/ATU should be pumped out and media in ATU flushed with water hose. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  |  | 12:00 AM
06/30/2020 |  | RoutineScheduled |  | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | 1500 Hanover w/.75 Microfast Septic Tank | Hanover 2000 Pump Tank | Pump | Pressure | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [17 empty] | Septic tank-3"sludge 4"scum/microfast-4"sludge/Pump tank-0"sludge. No pump out needed at this time.P1 cnt-1108 ETM-37h 18m/ P2 cnt-1060 ETM-35h 46m/ both pumps @ 45gpm. Blower air filter cleaned. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 09/01/2020 | 12:00 AM
08/13/2020 |  | Routine, Scheduled | 175-17-0388 | Prince William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Biomicrobics MicroFAST |  | Pump | Drip | Drip Tubing | UV Light |  | ["Blower/Compressor/Aerator Operation","Disinfection"] | ["Blower/Compressor/Aerator Operation","Septic Tank Baffles"] |  | Good | Good | [15 empty] | UV Bulb & cord needs replacement. Spin filter cleaned. Pump Amps 10.32 ETM 455 hrs Cycles 2730 Water Meter Reading 190890 Septic Sludge 6" Scum 3" ATU Sludge 12" Scum 0 Pump Sludge 3" Scum 0 | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 08/13/2020 | 09:58 AM
10/14/2020 |  | RoutineScheduled | 187170362 | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Greenway Engineering | 1942001008 | Jeremy | Ferguson | 1.000000 | 1500 | Microfast | none | Pump | Pressure | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [17 empty] | Inital inspection was completed on 10/01/20. Blower line needed placed and was replaced on 10/14/20. System is now operation. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 10/14/2020 | 02:55 PM
07/21/2020 |  | Follow-Up | 153-STS-20175 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green | [9 empty] | ["Dispersal System Operation"] | ["Dispersal System Operation"] | [18 empty] | Fixed leak at spin filter. | This AOSS should now return to normal function after having provided the above state routine maintenance |  | 07/21/2020 | 04:00 PM
05/06/2020 |  | Reportable Incident | 093-18-0087 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | Owner called due to the alarm being on and also stated that they had lost power a couple of days ago. Serviced system. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream, changed the filter in the aerator, and changed the mesh screen in the spinfilter. The return was shut off in the pump. Set pressures to 30 lbs on the pump and 15 lbs on the return. THe pump tank needs to be pumped and cleaned as well as the septic tank. Need to flush the drainfield drip tubing with fresh H2O. The timer is set to 11 minutes every 2 hours. The drainfield was wet at the toe - found that they had a leaking toilet - need to keep an eye on it. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 05/06/2020 | Jan 1 1900 12:00PM
07/30/2020 |  |  | 39296 | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | dovel enterprises |  | jerry | dovel | 1.000000 |  | 1000 |  | Pump |  | Drip |  |  | [] | [] | NO | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 07/28/2020 | 12:00 AM
06/01/2020 |  | RoutineScheduled | 109-18-0505 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1000 | Advantex |  | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | NA | [16 empty] | Inspected | New system installed, Yet old panel was left in place and began alarming. (not connected) Reomved old panel, No issues with new system | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 06/02/2020 | 09:30 AM
07/07/2020 |  | RoutineScheduled | SD-06-l84 | Fauquier | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Rappahannock-Rapidan | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic Tank | Pump Tank for Puraflo | Pump | Gravity | Pad | Not Applicable |  | ["SludgeScum Accumulation"] | [] | YES | [17 empty] | Septic-12"sludge 0"scum/ Pump tank-3"sludge (recommend both tanks pumped out within 3 months) Recommend septic filter upgrade with screen to prevent solids from flowing through when filter is cleaned/ Puraflo peat in good condition and fluffed. Counts: Pump-34102 ETM-438.84/ No breakout or spongy areas on the pad area. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  |  | 12:00 AM
08/13/2020 |  | RoutineScheduled | 10-183-016 | Russell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Effluent Screens"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
06/18/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim |  |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Anua tank 2" scum 9"sludge The anua control panel the alarm and light are not working | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 |  | 04/14/2021 | 04:27 PM
11/19/2020 |  | RoutineScheduled |  | Rockingham | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 4.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity |  | Not Applicable |  | ["SludgeScum Accumulation" ,"BlowerCompressorAerator Operation" ,"Control Operation" ,"Disinfection" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | Will be pumping necessary tanks in January | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/26/2021 | 09:04 AM
04/07/2020 |  | Reportable Incident | 175-05-0659 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green | [9 empty] | ["None"] | ["None"] | [18 empty] | Repaired broken vent pipes in mound. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/07/2020 | 04:00 PM
10/15/2020 |  | RoutineScheduled | 175-13-0085 | Prince William | This AOSS is not functioning as designed or in accordance with the performance/Maintenance requirements | Approved | EHD - Prince William | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Distribution Pump Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Distribution Pump Operation"] | NA | [15 empty] | Will be sent separately | Inspected | There appears to be broken plumbing at the distal end of the middle zone. We recommend digging by hand & repairing. We also recommend replacing all 3-zone check valves to ensure the zones are being dosed equally. We ask that the grass around the tanks be mowed and maintained in a mowed condition. | This AOSS is not functioning as designed or in accordance with the performance/Maintenance requirements |  | 04/09/2021 | 03:25 PM
06/03/2020 |  |  |  | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | great falls septic | 1942001301 | Joshua | Hott |  |  |  |  | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
11/09/2020 |  | RoutineScheduled | SD-05-424 | Orange | This AOSS is not functioning as designed or in accordance with the performance/Maintenance requirements | Approved | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | ["BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | We recommend replacing a 5" spin filter in the headworks box, an EZ Set riser lid, and the water meter for the drip dispersal system. | This AOSS is not functioning as designed or in accordance with the performance/Maintenance requirements |  | 04/09/2021 | 03:25 PM
09/23/2020 |  | Routine, Scheduled | 175-16-0385 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Biomicrobics MicroFAST |  |  |  |  | UV Light |  | ["Blower/Compressor/Aerator Operation"] | ["Blower/Compressor/Aerator Operation"] |  | Acceptable | Clear | [15 empty] | Spin filter cleaned. Pump Amps 11.12 ETM 443 hrs Cycles 4092 Water Meter Reading 218940 Septic Sludge 14" Scum 5" ATU Sludge 12" Scum 0 Pump Sludge 2" Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 09/23/2020 | 10:30 AM
07/22/2020 |  | Routine/Scheduled | 03-174-0047 | Prince George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Crater | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | PremierTech, EFX |  | Gravity | None | Aggregate Bed | None | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | Musty | Clear | [15 empty] | Routine service conducted. Primary Septic tank in normal level - effluent screen serviced. Pump Basin intact and at normal level - pump, float sensors and controls operating properly. Peatmoss Biofilter - peat in good condition - raked & turned. All components operating properly | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 07/23/2020 | Jan 1 1900 7:30AM
02/19/2020 |  | Routine, Scheduled | 033-13-0006-SP | Caroline County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Ware, Michele P | 1942001165 | Michele | Ware |  |  | Septic Tank Only | Septic Tank Only | None | None | None | None |  |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/04/2020 | 07:22 AM
05/15/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 2.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Minor roots were observed in Microfast riser. They were removed. We plan to check again in a month or two to determine if the riser needs to be resealed from the outside. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/27/2021 | 01:26 PM
10/22/2020 |  | Routine/Scheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | POWELLS PLUMBING, INC. | 1942001036 | Kurt | Holthaus | 1.000000 | 1000 | Puraflo |  | Pump | Drip | Drip Tubing |  | 600.000000 | ["Effluent Screens"] | ["Effluent Screens"] | N/A | [17 empty] | Annual Inspection - Serviced spin filter and effluent screen(s). | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 10/26/2020 | 01:58 PM
12/21/2020 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump | Drip | Elevated Sand Mound | UV Light |  | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  | 8.52 | 6.320000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 12/21/2020 | Jan 1 1900 1:30PM
09/10/2020 |  | RoutineScheduled | 08-183-100 | Russell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. |  | Denny | Deel |  |  | FAST |  | Gravity | Gravity | Discharge | UV | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
06/11/2020 |  | RoutineScheduled |  | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | [9 empty] | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | [18 empty] | Septic/ATU had 6" sludge and 6" scum ATU had 8" sludge. Pumpn tank had 0" sludge. Cleaned air filter for blower. Pump#1- 7528 ETM1-28h 53m Pump#2-375 ETM2-13h 32m | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
06/12/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | There was a small knick in one of the drip lines resulting in a small area being misted. 6" of tubing was removed and repaired. The blower connection into the tank has come uncoupled. Blower was reconnected. When the current blower fails we recommend replumbing the airline. There are a few spots where drip tubing is visible and we have recommended installers to properly add cover to those areas. The system appears to be functioning as designed at this time | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/27/2021 | 01:26 PM
10/12/2020 |  | RoutineScheduled | 193-STS-92916 | Westmoreland | This AOSS is not functioning as designed or in accordance with the performance/Maintenance requirements | Approved | EHD - Three Rivers | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation"] |  | NA | [15 empty] | Will be sent separately | Inspected | 90-DAY INSPECTION The risers on the inlet & outlet side of the septic tank and the riser on the inlet side of the pump tank are leaking. We recommend contacting your builder & asking him to contact the installer for repairs to the tanks. The drip dispersal area shows signs of water surfacing at the distal end. We recommend contacting your builder and asking them to have the system designer evaluate the drip dispersal area further,for possible repairs or modifications. We will also send an electronic copy of this report to your builder. | This AOSS is not functioning as designed or in accordance with the performance/Maintenance requirements |  | 04/09/2021 | 03:25 PM
09/22/2020 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump | Distribution Box | Aggregate Bed |  |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  |  | 6.150000 | 5.700000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 09/22/2020 | Jan 1 1900 1:30PM
02/04/2020 |  | Routine, Scheduled |  | James City County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Peninsula | HERMAN, ADAM C | 1934000195 | ADAM | HERMAN | 1.000000 |  | Orenco Advantex | None | Pump | Drip | Drip Tubing | None | [21 empty] | [Comments]: System Functioning properly. Cleaned Biotube | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/06/2020 | Jan 1 1900 10:53AM
07/28/2020 |  | Routine/Scheduled | 04-120-0643A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesterfield | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1500 | Orenco Advantex |  | Pump | Distribution Box | Aggregate Trench | None | 600.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | None | Clear | [15 empty] | Routine service conducted. Processing Tank - normal level - RSV, Effluent Screen and recirc. pump serviced. AdvanTex Module - media drapes and spray grid serviced. Discharge tank - normal level - discharge pump serviced - float sensors and controls operating properly | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 07/29/2020 | Jan 1 1900 7:30AM
08/08/2020 |  | RoutineScheduled | 175-04-0856 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Wastemaster Inc |  | Timothy | Jenkins | 2.000000 |  | PuraFlo |  | Pump | Gravity | Discharge | Chlorination |  | [] | [] |  | Musty | Clear | 7.600000 |  |  | 2.200000 | [12 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 11/19/2020 | 01:00 PM
05/01/2020 |  | Follow-Up |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Replaced the alarm | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/14/2021 | 04:27 PM
09/04/2020 |  | Follow-Up | 175-14-0076 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green | [9 empty] | ["Blower/Compressor/Aerator Operation"] | ["Blower/Compressor/Aerator Operation"] | [18 empty] | Repaired compressor airline. | This AOSS should now return to normal function after having provided the above state routine maintenance |  | 09/04/2020 | 04:00 PM
05/12/2020 |  | Routine/Scheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Loudoun | POWELLS PLUMBING, INC. | 1942001036 | Kurt | Holthaus | 1.000000 | 1500 | EcoPod |  | Pump | Drip | Drip Tubing |  | 600.000000 | ["Blower/Compressor/Aerator Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | Annual Inspection - Pumped treatment side of Ecopod, washed out filter and pumped pump chamber. Serviced spin filter and blower. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 05/21/2020 | 09:47 AM
06/09/2020 |  | RoutineScheduled | 13-183-116 | Russell | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. |  | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Effluent Screens"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Effluent Screens"] | YES | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  |  | 12:00 AM
09/03/2020 |  | RoutineScheduled | S102-08-0014 | Alleghany | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | Hunter E. Ayres, General Contractor | 1942001166 | Hunter | Ayres | 2.000000 | 1500 | Biomicrobics MicroFAST |  | Pump | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","Effluent Screens"] | ["Auxiliary Filter","Effluent Screens"] | YES | [17 empty] | Filters checked and cleaned. New spin filter installed. No apparent leaks in system or drain field area. System did not need to be pumped. Control panels functioning properly. Lids properly secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 09/03/2020 | Jan 1 1900 9:45PM
09/15/2020 |  | RoutineScheduled | 109-15-0012 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1000 | Advantex |  | Pump | Gravity | Trenches |  |  | ["None"] | ["None"] | [18 empty] | 14" of solids in septic tank. Cleaned septic tank filter. Flushed treatment unit spray manifold. Removed solids from recirculation chamber. Tested floats, pumps and alarm. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 10/19/2020 | 07:03 PM
05/19/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/27/2021 | 01:26 PM
10/06/2020 |  | RoutineScheduled | 182-03-0209 (LEGACY ALT. SYSTEM) | Rockingham | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Central Shenandoah | Onsite Wastewater Services - May Supply | 1942001022 | Sara | Tusing | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Pressure | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Inspection DKS | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/28/2021 | 05:41 AM
08/31/2020 | Alternative | RoutineScheduled | {FIPSCode}-STS-54259 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | KC Forge Environmental Service, LLC | 1942001034 | Kent | Cuthbertson |  |  |  |  | Pump | Pressure | Drip | Not Applicable | 5613.000000 | ["None"] | ["None"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 09/14/2020 | 06:05 PM
01/08/2020 |  | Routine, Scheduled |  | Fluvanna County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Blue Ridge | CLARK, MICHAEL J | 1934000023 | MICHAEL | CLARK |  |  | Septic Tank Only | Septic Tank Only | None | None | None | None |  |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/14/2020 | 03:25 AM
09/19/2020 |  | Routine/Scheduled |  | Southampton | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump | Distribution Box |  | None |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  |  | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 09/19/2020 | Jan 1 1900 10:45AM
08/19/2020 |  | RoutineScheduled | 101-16-0223 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Aiternative Systems Inspection Services, LLC | 1942001047 | Wesley | Basore | 1.000000 | 500 | Aquasafe 600 EZ |  | Gravity | Gravity | Trenches | Not Applicable | 150.000000 | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 09/01/2020 | 07:15 PM
09/29/2020 |  | Follow-Up | 099-STS-86749 | King George | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [9 empty] | 29.000000 | [5 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
12/03/2020 | Alternative | RoutineScheduled | {FIPSCode}-STS-84055 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
12/15/2020 |  | RoutineScheduled | SD-113-15-089 | Madison | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Rappahannock-Rapidan | Onsite Wastewater Services - May Supply | 1942001627 | Drew | Shull | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Pad | Not Applicable |  | ["Attached Growth Medium" ,"Auxiliary Filter"] | ["Attached Growth Medium" ,"Auxiliary Filter"] | NO | None | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/01/2022 | 12:13 PM
01/28/2020 |  | Initial Visit |  | Louisa County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Blue Ridge | ARNOLD, ARCHIE G | 1942001291 | ARCHIE | ARNOLD | 1.000000 | 1250 | Aqua Safe ATU | Septic Tank Only | Pump | Distribution Box | Aggregate Trench | None | 300.000000 | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] |  | earthy | clear | [15 empty] | [Comments]: Preformed typical maintenance, High Level Alarms = 2, low level Alarms = 4, 15 min delay in alarm, off time 3:50h on time 2:31m Override off time 3:24h, override in time 2:13 m | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/06/2020 | 12:40 PM
06/30/2020 |  | RoutineScheduled | 15-113-104 | Buchanan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Effluent Screens"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
05/26/2020 | Alternative | RoutineScheduled | 115-10-0225 | Campbell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1000 | Advantex AX20 |  | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Effluent Screens"] | NA | Musty | [15 empty] | Inspected | Sludge levels-Scum layer 1"in. and 6" in. sludge in Septic tank -Recirc zone 7" Sludge and 6" Sludge in Discharge zone of tank. Cleaned effluent screen, Flushed Sprayer maniflod, cleaned Biofilter. pumps are functional, alarm functional, sprayed off media, tested floats. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 05/30/2020 | 05:30 PM
04/10/2020 |  | Routine, Scheduled | C 800-17-0320 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Western Tidewater | Farmer’s Septic Service, Inc. |  | Ross | Cole | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | [Comments]: Serviced system. Checked the pump, panel, & floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. The timer is set to 1.75 minutes every 2 hours. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/10/2020 | Jan 1 1900 12:00PM
12/11/2020 |  | Routine/Scheduled | 08-163-0037 | New Kent | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Chickahominy | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1500 | Orenco Advantex |  | Pump | Distribution Box | Aggregate Trench | None | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | None | Clear | [15 empty] | Routine Service Processing Tank - normal level - RSV, recirc pump & effluent screen serviced. Treatment Module - media drapes & spray grid serviced. Pump Tank - normal level - pump, float sensors & controls operating properly. Distribution Box - concrete - intact - evidence of overflow - site visits made and evaluation - absorption laterals are root clogged. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 12/14/2020 | Jan 1 1900 7:30AM
03/23/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Paid | EHD - Fairfax | MCKIM, STEPHEN E | 1934000043 | STEPHEN | MCKIM |  |  | Septic Tank Only | Septic Tank Only | None | None | None | None |  | ["SludgeScum Accumulation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | [18 empty] | [Comments]: Septic/Atu needs pumped out | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 04/20/2020 | Jan 1 1900 10:33AM
09/03/2020 |  | Follow-Up | SD-15-204 | Fauquier | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [9 empty] | 7.000000 | [5 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
09/29/2020 |  | RoutineScheduled | 107-99-0102 (LEGACY ALT. SYSTEM) | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Onsite Wastewater Services - May Supply | 1942001022 | Sara | Tusing | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Inspected by DKS | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 05/28/2021 | 05:41 AM
01/16/2020 |  | Routine, Scheduled | 07-113-163 | Buchanan County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Cumberland Plateau | DEEL, DENNY M | 1942001097 | DENNY | DEEL |  |  | Norweco Singulair ATU | None | Gravity | None | Alternative Discharge | Chlorine | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens"] |  | Musty | Clear | [15 empty] | [Comments]: 5 Blue Crystal Added | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/05/2020 | Jan 1 1900 3:01PM
11/05/2020 |  | RoutineScheduled | 179-STS-91661 | Stafford | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Attached Growth Medium" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | ["Control Operation" ,"Attached Growth Medium" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Level Sensor Operation"] | YES | [15 empty] | Will be sent separately | Inspected | Pod #1 is flooded, pod # 2 pump line is broken. Peat is degraded but OK for now. Sample box needs to be located and extended to above grade. Proposal for repairs to be sent to homeowner. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
08/20/2020 |  | RoutineScheduled | {FIPSCode}-STS-4677 | Dickenson | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Effluent Screens"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Effluent Screens"] | YES | Musty | Clear | [16 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  |  | 12:00 AM
06/02/2020 |  | RoutineScheduled |  | Rockingham | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Bio Barrier | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Distribution Pump Operation" ,"SludgeScum Accumulation"] | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Distribution Pump Operation" ,"SludgeScum Accumulation"] | NA | [7 empty] | 06/02/2020 |  | 232.000000 | [5 empty] | Will be sent separately | Inspected | Repaired electrical connection to pump and floats Installed tank riser Will be pumping all tanks. | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance |  | 04/26/2021 | 09:04 AM
03/18/2020 |  | Follow-Up | SD-15-177 | Fauquier County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Biomicrobics MicroFAST | None | Pump | [16 empty] | 34.000000 | [8 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/01/2020 | 06:33 AM
11/06/2020 |  | RoutineScheduled | {FIPSCode}-STS-68288 | Stafford | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Attached Growth Medium" ,"Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | ["Control Operation" ,"Dispersal System Operation" ,"Attached Growth Medium" ,"Auxiliary Filter" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | YES | [15 empty] | Will be sent separately | Inspected | Sheets clogged, treatment is bad we wanded sheets. Flow meter needs to be installed for drip. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
04/06/2020 |  | Routine, Scheduled | 11-172-0100A | Powhatan County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesterfield | Mamunes, Peter S. | 1942001010 | Peter | Mamunes | 1.000000 | 1000 | Clearstream | None | Pump | Drip | Drip Tubing | None | 450.000000 | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | [Comments]: Sludge = 2" Scum = 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/21/2020 | Jan 1 1900 10:38AM
08/19/2020 |  | Routine/Scheduled | SD-10-208 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | SES Mid Atlantic | 1942001236 | S. Michael | Lynn | 1.000000 | 20000 | EcoPod | EcoPod | Pump | Pressure | Drip | Not Applicable | 7546.000000 | ["None"] | ["None"] | N/A | Musty | Clear | [5 empty] | 08/19/2020 | Pump Chamber | 15.000000 |  |  | 4.000000 | 26.000000 |  | Will be sent separately |  | Still having issues with N limit checking recric rates and alkalinity is 66 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 08/19/2020 | 05:00 PM
11/17/2020 |  | Routine/Scheduled | 228-14-0153 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | Serviced system. Red light was on when we arrived. Checked the pump, panel, & floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. The pressure switch on the aerator is not hooked up. The timer is set to 9 minutes every 2 hours. The septic tank needs additional risers on it so it can be properly inspected in the future. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 11/17/2020 | Jan 1 1900 12:00PM
02/07/2020 |  | Routine, Scheduled | 800-11-0073 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Western Tidewater | R & K Septic, Inc. |  | John | Butt, Jr |  |  |  |  | Pump |  |  |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] |  |  |  | 7.560000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/07/2020 | Jan 1 1900 11:00AM
09/22/2020 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Hoot |  | Pump | Drip | Elevated Sand Mound | UV Light |  | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  | 1.62 | 7.170000 | 6.100000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 09/22/2020 | Jan 1 1900 1:00PM
12/29/2020 |  | RoutineScheduled | 187-STS-32182 | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax |  |  | Michael | Edmonson | 1.000000 | 1500 | Microfast | none | Pump | Pressure | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation","SludgeScum Accumulation","Dispersal System Operation"] | ["BlowerCompressorAerator Operation","SludgeScum Accumulation","Dispersal System Operation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 01/01/2021 | 12:25 PM
12/07/2020 |  | RoutineScheduled | 196-11-040 | Westmoreland | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | UV light is only fault on system. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. |  |  | 12:00 AM
10/08/2020 |  | RoutineScheduled | 01-197-A4 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | Wise Health Dept. |  | Rodney | Neece | 1.000000 |  | ATU |  | Gravity | Gravity | Discharge | Chlorination |  |  |  |  | None | Clear | 6.700000 | 5.000000 |  |  | Chlorine effluent (0) | [11 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 10/08/2020 | Jan 1 1900 1:30PM
01/02/2020 |  | Reportable Incident | 033-15-0166-SWP | Caroline County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001350 | Mike | Cook | 1.000000 |  | Orenco Advantex | None | Pump |  |  | UV Light | [21 empty] | [Comments]: High level alarm, bad UV cord & bulb, replaced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/15/2020 | 10:52 AM
01/30/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Fairfax | SEAMON, CHARLIE L | 1942001108 | CHARLIE | SEAMON |  |  | Septic Tank Only | Puraflo | Pump | Distribution Box | Aggregate Bed | None | [21 empty] | [Comments]: Performance Inspection: Puraflo Pad System Septic Tank-8"sludge 0"scum/ Pump Tank-2"sludge. No pump out needed at this time. Pump #1 CC-4440 ETM-76.63/ Pump #2 CC-4521 ETM-73.02 Noted some roots in the puraflo modules but not impeding discharge. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/21/2020 | Jan 1 1900 6:34AM
10/10/2020 |  | RoutineScheduled | SD-12-167 | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Wastemaster Inc |  | Timothy | Jenkins | 2.000000 |  | ATU |  | Pump | Gravity | Discharge | Chlorination |  | [] | [] |  | Musty | Clear | 7.100000 |  |  | 2.200000 | [12 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 10/26/2020 | 09:40 AM
09/04/2020 |  | RoutineScheduled | 107-04-0340 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Onsite Wastewater Services - May Supply | 1942001627 | Drew | Shull | 1.000000 |  | Orenco Advantex | none | Pump | Gravity |  | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 05/28/2021 | 05:41 AM
07/20/2020 |  | Routine/Scheduled | 174-120-0339A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. |  |  | Clearstream ATU |  | Pump |  |  |  |  | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 07/20/2020 | Jan 1 1900 12:30PM
09/18/2020 |  |  |  | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | McKim Construction | 1942001330 | Michelle | McKim | 3.000000 |  |  |  | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 11/13/2020 | Jan 1 1900 11:40AM
06/16/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/14/2021 | 04:27 PM
09/22/2020 |  | RoutineScheduled |  | Warren | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity |  | Not Applicable |  | ["Control Operation" ,"Recirculation Pump"] | ["Control Operation" ,"Recirculation Pump"] | NA | [7 empty] | 09/22/2020 |  | 176.000000 | [5 empty] | Will be sent separately | Inspected | Repaired electrical to effluent pump | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance |  | 04/26/2021 | 09:04 AM
06/25/2020 |  | RoutineScheduled | 177-09-0074 SP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 |  | 04/09/2021 | 03:25 PM
03/18/2020 |  | Routine, Scheduled | 2014-143-0052 | Henrico County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Henrico |  |  |  |  | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | [Comments]: Serviced system. Checked the pump, panel, & floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream, changed the filter in the aerator, and changed the mesh screen in the spinfilter. Fixed the alarm float wire in the panel - wire was too short. The aerator needs to be raised. The septic tank needs additional risers on it so it can be properly inspected in the future. The pipe in the Clearstream is cocked up but working. The pump tank should have an additional 6" riser on the inlet end. The timer is set to 7 minutes every 2 hours. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/18/2020 | 12:00 PM
06/10/2020 |  | RoutineScheduled | 16-137-0179 | Goochland | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Chickahominy | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Ecoflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Control Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | ["Attached Growth Medium" ,"Distribution Pump Operation" ,"Control Operation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | YES | [15 empty] | Will be sent separately | Inspected | 1? water ponding on media, raked; now OK, few roots in surge basin; we removed. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | Jan 1 1900 11:22AM
05/24/2020 |  | RoutineScheduled |  | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Soils, Inc. | 1942001004 | Markham | Smith | 2.000000 | 2000 | MicroFAST 0.75 |  | Pump | Pressure | Trenches | UV |  | [] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 05/30/2020 | Jan 1 1900 11:00AM
09/23/2020 |  | Routine, Scheduled | 175-02-0474 | Manassas | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Orenco Advantex |  |  |  |  | None |  | ["Level Sensor (Float) Operation"] |  |  | Acceptable | Clear | [15 empty] | On/Off floats needs replacing. Pump Amps 9.28 ETM 431440 mins Cycles 883845 Pump Amps 12.43 ETM 62529 mins Cycles 6743 Septic Sludge 6" Scum 0 ATU Sludge 4" Scum 0 Pump Sludge 0 Scum 0 | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 09/23/2020 | 01:50 PM
12/11/2020 |  | RoutineScheduled | 177-STS-87379 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | EZ Treat Sandfilter | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | The headworks box appears to have settled and is in a low location. We contacted the installer who said he would address the issue. | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 |  | 04/09/2021 | 03:25 PM
02/07/2020 |  | Routine, Scheduled |  | Loudoun County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | None | Pump | Distribution Box | Gravel-Less Trench | [23 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/02/2020 | 04:43 AM
10/13/2020 |  | RoutineScheduled | 175-04-0448 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic Tank | Pump Tank for Puraflo | Pump | Gravity | Trenches |  |  | ["Attached Growth Medium"] | ["Attached Growth Medium"] | NO | [17 empty] | Septic Tank-3"sludge 0"scum/ Pump Tank-0"sludge. No pump out needed at this time. Puraflo media fluffed and is in good condition. The concrete lid on the pump tank requires replacement ,owner stated he already has a company that is going to replace it. No breakout or spongy areas on the drainfield. Counts: cc1-35620 ETM-955.21 | This AOSS should now return to normal function after having provided the above state routine maintenance. |  |  | 12:00 AM
03/16/2020 |  | Routine, Scheduled | SWP-03-462 | Stafford County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Ware, Michele P | 1942001165 | Michele | Ware |  |  | Septic Tank Only | Septic Tank Only | None | None | None | None |  |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/16/2020 | 12:35 PM
01/02/2020 |  | Routine, Scheduled |  | Warren County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Lord Fairfax | POWELLS PLUMBING, INC. | 1942001036 | Kurt | Holthaus |  |  | Microfast | [6 empty] | ["SludgeScum Accumulation"] | ["SludgeScum Accumulation"] | [18 empty] | [Comments]: Pumped Microfast. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/02/2020 | 03:33 PM
03/17/2020 |  | Routine, Scheduled | 177-15-0199-SWP | Spotsylvania County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001350 | Mike | Cook | 1.000000 |  | None | None | Gravity | Distribution Box | Aggregate Trench |  |  | ["BlowerCompressorAerator Operation","Control Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","SludgeScum Accumulation"] | [18 empty] | [Comments]: System needs to be pumped out. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/01/2020 | 06:33 AM
08/05/2020 |  | Reportable Incident | 196-12-093 | Westmoreland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers |  |  | joel | pinnix | [9 empty] | [] | [] | [18 empty] | Alarm due to high water condition in pump tank. Probable high flow event due to laundry. All components working as designed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
01/03/2020 |  | Pump-Out Only | 171-08-0450 | Shenandoah | This AOSS should now return to normal function after having provided the above stated routine maintenance. | Approved | EHD - Lord Fairfax | LAM, JOHN W | 1942001218 | JOHN | LAM |  |  |  | None | Pump | Drip | Drip Tubing | None |  | ["SludgeScum Accumulation"] | ["SludgeScum Accumulation"] | [18 empty] | [Pumpout Comments]: FAST treatment tank pumped out by First Choice Septic, Inc. due to a normal build-up of solids. | This AOSS should now return to normal function after having provided the above stated routine maintenance. |  | 01/21/2020 | 05:11 PM
04/14/2020 |  | Follow-Up | 153-STS-19043 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green | [9 empty] | ["Blower/Compressor/Aerator Operation"] | ["Blower/Compressor/Aerator Operation"] | [18 empty] | Rebuild compressor. | This AOSS should now return to normal function after having provided the above state routine maintenance |  | 04/14/2020 | 09:30 AM
12/02/2020 |  | RoutineScheduled |  | Rockingham | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NO | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/26/2021 | 09:04 AM
05/04/2020 |  | RoutineScheduled | 13-142-0099 | Hanover | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Clearstream |  | Gravity | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | YES | [16 empty] | Pumped Out | Replace the Clearstream diffuser 05/04/2020 | This AOSS should now return to normal function after having provided the above state routine maintenance. |  |  | 12:00 AM
11/23/2020 |  | RoutineScheduled | 061-18-166 | Fauquier | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | EZ Treat Sandfilter | none | Pump | Gravity | Drip | Not Applicable |  | ["Distribution Pump Operation" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Control Operation"] | ["Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"Recirculation Pump"] | NA | [7 empty] | 11/23/2020 | [7 empty] | Will be sent separately | Inspected | Routine inspection and maintenance. Collected first sample for BOD test. Cleaned recirc pump intake. High level count at 7 and peak count at 14 in drip tank. Installer did come back and add a disconnect (sch 80 union) for recirc pump and adjust float switches. Treatment appears to be much better than at last inspection. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
04/09/2020 |  | Routine, Scheduled | SD-01-70 | Madison County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | JENKINS, TIMOTHY R | 1942001062 | TIMOTHY | JENKINS | 1.000000 |  | Aero-flo ATU | Septic Tank Only | None | Drip | Alternative Discharge | Chlorine |  | ["None"] | ["None"] |  | Musty | Clear | 7.000000 |  | 25.000000 | 1.800000 | [11 empty] | [Pumpout Comments]: Functioning as Designed | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/22/2020 | 01:30 AM
03/09/2020 |  | Routine, Scheduled | 09-120-0251A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesterfield | Madison Environmental LLC |  | Larry | Madison, Jr. |  |  | Biomicrobics MicroFAST |  | Pump | Distribution Box |  |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [18 empty] | Lab results not reported by Operator, EHS chose "No" in order to allow saving updated entry. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/09/2020 | Jan 1 1900 1:30AM
03/24/2020 |  | Routine, Scheduled | 11-183-190 | Russell County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Cumberland Plateau | DEEL, DENNY M | 1942001097 | DENNY | DEEL |  |  | Norweco Singulair ATU | None | Gravity | None | Alternative Discharge | Chlorine | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens"] |  | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/30/2020 | Jan 1 1900 5:24PM
12/15/2020 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  |  |  | Elevated Sand Mound | UV Light |  | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  |  | 7.000000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 12/15/2020 | Jan 1 1900 9:00AM
12/23/2020 |  | RoutineScheduled | 107-14-0324 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Central Shenandoah | Onsite Wastewater Services - May Supply | 1942001627 | Drew | Shull | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Pressure | Drip | Not Applicable |  |  |  | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | INSPECTION COMPLETED ON 12-23-2020 BY DKS. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 06/09/2022 | 04:10 PM
10/27/2020 |  | RoutineScheduled | 11-184-5001 | Scott | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Effluent Screens"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
06/16/2020 |  | Routine/Scheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Loudoun | POWELLS PLUMBING, INC. | 1942001036 | Kurt | Holthaus | 1.000000 | 1500 | Orenco Advantex |  | Pump | Drip | Drip Tubing |  | 450.000000 |  |  | N/A | [17 empty] | Annual Inspection - Serviced spin filter. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 06/24/2020 | 10:09 AM
07/02/2020 |  | RoutineScheduled | SD-12-312 | Fauquier | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 2.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | On site for routine quarterly inspection. Observed blower running, but no bubbling taking place in Microfast tank. Diagnosed and replaced broken airline coupling inside tank. Waterless urinals help reduce daily flow, but also is driving up influent waste strength. Owner has been adding chemicals to attempt to improve nitrogen reduction. Sampling will be done next month to allow system time to recover from broken airline. Atu panel gives audible alarm only and cannot be silenced. High level alarm for pump tank worked correctly this time (silenced and reset properly). | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
12/05/2020 |  | RoutineScheduled | 2084-03-153 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Wastemaster Inc |  | Timothy | Jenkins | 2.000000 |  | PuraFlo |  | Pump | Gravity | Discharge | Chlorination |  | [] | [] |  | Musty | Clear | 7.400000 | 6.300000 |  | 2.200000 |  | 12/05/2020 |  | 10.000000 |  |  | 6.700000 | [5 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12/18/2020 | 11:40 AM
02/17/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Biomicrobics MicroFAST |  | Pump | Drip | Drip Tubing | UV Light |  | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] |  | Good | Clear | [5 empty] | 02/17/2019 |  | 16.000000 |  | 1600.000000 | [5 empty] | [Comments]: Pump 1 Amps 8.02 ETM 402h Cycles 2485Pump Amps 7.86Water Meter Reading 84600Septic Sludge 7" Scum 5"ATU Sludge 12" Scum 0Pump Sludge 0 Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/17/2020 | Jan 1 1900 2:29PM
12/08/2020 |  | RoutineScheduled | 2008-01-153 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Wastemaster Inc |  | Timothy | Jenkins | 2.000000 |  | PuraFlo |  | Pump | Gravity | Discharge | Chlorination |  | [] | [] |  | Musty | Clear | 6.600000 |  |  | 2.200000 | [12 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12/16/2020 | 02:05 PM
06/03/2020 |  | Routine, Scheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Biomicrobics Retrofast |  |  |  |  | None |  | ["Blower/Compressor/Aerator Operation"] | ["Blower/Compressor/Aerator Operation"] |  | Good | Clear | [15 empty] | Pump 1 Amps 9.10 ETM 56 hrs 35 mins Cycles 1079 Pump 2 Amps 9.87 ETM 58 hrs 57 mins Cycles 1100 Septic Sludge 4" Scum 3" ATU Sludge 15" Scum 0 Pump Sludge 1" Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 06/03/2020 | Jan 1 1900 11:30AM
03/27/2020 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump | Drip | Elevated Sand Mound | UV Light |  | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  | 4.45 | 8.040000 | 5.000000 | [13 empty] | Needs UV Bulb & UV cord | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/27/2020 | Jan 1 1900 10:30AM
12/10/2020 | Alternative | Routine/Scheduled | 157-13-0008 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | Serviced system. Checked the pump, panel, & floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. Pumped out the pump tank (12/08/2020). Replaced the pressure switch on the aerator. Could not locate the vacuum breakers. The whole yard is wet - have had alot of rain - when it dries up need to watch the drainfield. The timer is set to 3.5minutes every 1 hour. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12/10/2020 | 12:00 PM
12/02/2020 |  | RoutineScheduled | SD-04-455 | Culpeper | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Pad | Chlorination |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Effluent sample taken. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/09/2021 | 03:25 PM
10/14/2020 |  | RoutineScheduled | 107-05-0195 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Onsite Wastewater Services - May Supply | 1942001627 | Drew | Shull | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Pressure | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 05/28/2021 | 05:41 AM
04/08/2020 | Alternative | Routine/Scheduled | 128-06-132 | Essex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | Ecoflo | None | Pump | Distribution Box | Aggregate Trench | None |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | Septic Tank Riser was cracked | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/09/2020 | 04:32 PM
03/30/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Paid | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Biomicrobics MicroFAST |  | Pump |  |  | None |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] |  | Good | Clear | [5 empty] | 03/30/2020 |  | 42.000000 | [7 empty] | [Comments]: D/F has standing water at mound. Recommended going on pump and haul to client.Pump 1 Amps 16.79 ETM 29h 56m Cycles 710Pump 2 Amps 17.25 ETM 38h 03m Cycles 888Septic Sludge 8" Scum 0.50ATU Sludge 10" Scum 0Pump Sludge 0 Scum 0 | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 03/30/2020 | Jan 1 1900 11:50AM
03/19/2020 |  | RoutineScheduled |  | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | FIVE STAR SEPTIC INC | 1944001248 | AARON | GOINS | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 03/19/2020 | 12:00 AM
01/08/2020 | Alternative | RoutineScheduled | 115-15-0020 | Campbell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | WAUGH, IAIN C | 1942001512 | IAIN | WAUGH | 1.000000 | 1000 | Advantex AX20RT |  | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium"] | ["Attached Growth Medium"] | [18 empty] | [Pumpout Comments]: Not Needed [Comments]: Septic 1" Scum 10" Sludge -Recirc 8" Sludge, Discharge 12" Sludge. Entire system a whiteish gray color not normal green or brown. Phoned Orenco advised recirc pump setting change 36min off 48s Run, Also possible renters using bleach bombs in toilet as mentioned last year by renter. Cleaned Filter & manifold. Alarm good | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 01/10/2020 | 08:48 PM
01/09/2020 |  | Routine, Scheduled | SD-06-27 | Fauquier County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Puraflo | None | Pump | Distribution Box | Aggregate Trench |  |  | ["Control Operation","Distribution Pump Operation","Level Sensor Operation"] | ["Control Operation","Distribution Pump Operation","Level Sensor Operation"] | [18 empty] | [Comments]: Small puddles under most grid emitters, went away after raking peat. Peat appears to be still working, but is beginning to show its age. Re-evaluate next year. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/15/2020 | 10:52 AM
07/11/2020 | Alternative | Reportable Incident | 157-09-0221 | Mathews | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | Owner called due to the aerator not working. Serviced system. Checked the pump, panel, & floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. Installed a re-build kit on the aerator. The septic tank needs additional risers on it so it can be properly inspected in the future. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 07/11/2020 | 12:00 PM
10/03/2020 |  |  | 08-113-152 | Buchanan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 10/03/2020 |  | 9.630000 | [5 empty] | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 10/03/2020 | 12:00 AM
10/13/2020 | Alternative | Routine/Scheduled | 157-06-0201 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | Serviced system. Checked the pump, panel, & floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. The pressure switch on the aerator is not hooked up. The septic tank needs additional risers on it so it can be properly inspected in the future. There is visible wetness on the drainfield - most likely from rain - need to keep an eye on it. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 10/13/2020 | 12:00 PM
10/22/2020 | Alternative | Routine/Scheduled | 157-12-0156 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | Serviced systems. Checked the pump, panel, and floats (ok). Cleaned the filter in the Clearstream on both. Changed the diffuser in the Clearstream and the filter in the aerator on both. The timer is set to 4.5 minutes every 2 hours. The grade on the pipe in one of the Clearstreams is not okay. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 10/22/2020 | 12:00 PM
09/12/2020 |  | RoutineScheduled | 133 17 0243 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1000 | Advantex |  | Pump | Pressure | Drip |  |  | ["None"] | ["None"] | [18 empty] | 8" of solids in septic tank. Cleaned drip field manifold spin filter. Cleaned septic tank filter. Tested floats, pumps and alarm. Drip field pressure 38 psi. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 10/19/2020 | 07:00 PM
09/10/2020 |  | Follow-Up | 2049-97-153 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Prince William | Wastemaster Inc |  | Timothy | Jenkins | 2.000000 |  | Recirculating Sand Filter |  | Pump | Gravity | Discharge |  |  | [] | [] | [18 empty] | Installed new pump. Level falling on departure. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  |  | 12:00 AM
07/21/2020 |  | RoutineScheduled | 13-165-0082 | Northampton | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Bundick Well & Pump | 1942001051 | Peter | Duer | 7.000000 | 196,000 | Septic Tank | EZ Treat Sandfilter | Pump | Pressure | Trenches | Not Applicable | 6000.000000 | ["None"] | [] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 09/17/2020 | 10:00 AM
08/28/2020 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump | Drip | Elevated Sand Mound | UV Light |  | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  | 2.25 | 7.900000 | 5.300000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 08/28/2020 | Jan 1 1900 1:30PM
11/02/2020 |  | Routine/Scheduled | 136-13-0041 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | Clearstream |  | Pump | Manifold | Aggregate Trench | None | 450.000000 |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | Musty | Clear | [15 empty] | Routine Service Septic Tank - normal operating level. Aeration Tank - normal operating level - compressor serviced. Discharge tank - normal operating level, pump, float sensors and controls operating properly. LPP Manifold - exercised valve and re-set. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 11/03/2020 | 02:30 PM
06/29/2020 |  | Reportable Incident | 2016-143-0115 | Henrico | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Henrico | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | Owner called due to the alarm going off. Serviced system. Checked the pump, panel, & floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream, changed the filter in the aerator, and changed the mesh screen in the spinfilter. Installed a re-build kit on the aerator. The Clearstream tank needs to be pumped as well as the septic tank. The drainfield needs to be repaired (need tubing) and the tee needs to be replaced. The timer is set to 10 minutes every 1 hour. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. |  | 06/29/2020 | 12:00 PM
01/15/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Clearstream ATU |  |  |  |  | UV Light |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] |  | Good | Good | [15 empty] | [Comments]: Spin filter cleaned.Pump Amps 5.50Septic Sludge 6" Scum 0.50ATU Sludge 0 Scum 0Pump Sludge 2" Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/15/2020 | Jan 1 1900 11:35AM
05/01/2020 |  | Routine, Scheduled | 179-15-0183-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | EZ Treat Sandfilter |  |  |  |  | None |  | ["Effluent Screens"] | ["Effluent Screens"] |  | Good | [16 empty] | Pump Amps 8.73 Septic Sludge 12" Scum 4" Pump Sludge 6" Scum 0.25 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 05/01/2020 | 12:59 PM
05/30/2020 |  | Routine/Scheduled | 2016-143-0010 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Henrico | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | EZ Treat Sandfilter | None | Pump | Distribution Box | Aggregate Trench | None |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | The Riser on the Septic Tank was leaking at the Baseplate; the Pump was found 100% clogged and not operating properly - Homeowner has approved all repairs | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 06/11/2020 | 03:55 PM
01/03/2020 |  | Routine, Scheduled | 228-16-0402 A | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Virginia Beach | [8 empty] | Pump | Distribution Box | Gravel-Less Trench | None |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] |  |  |  | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/03/2020 | Jan 1 1900 11:15AM
03/30/2020 |  | Routine, Scheduled |  | Fluvanna County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Blue Ridge | CLARK, MICHAEL J | 1934000023 | MICHAEL | CLARK |  |  | Septic Tank Only | Septic Tank Only | None | None | None | None |  |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/12/2020 | 04:47 AM
10/14/2020 |  | Routine/Scheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | POWELLS PLUMBING, INC. | 1942001036 | Kurt | Holthaus | 1.000000 | 1250 | Microfast |  | Pump | Drip | Drip Tubing |  | 450.000000 | ["Blower/Compressor/Aerator Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | Annual Inspection - Pumped Microfast tank and pump chamber. Serviced spin filter and blower. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 11/04/2020 | 02:30 PM
02/05/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Fairfax | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Biomicrobics MicroFAST | None | Pump | Distribution Box | Aggregate Trench |  |  | ["Control Operation"] | ["BlowerCompressorAerator Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/02/2020 | Jan 1 1900 11:52AM
05/08/2020 |  | Routine/Scheduled | SD-89-66 | Clarke | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | POWELLS PLUMBING, INC. | 1942001036 | Kurt | Holthaus | 1.000000 | 1000 |  |  | Pump | Manifold | Aggregate Trench |  | 450.000000 | ["None"] | ["None"] | N/A | [17 empty] | Annual Inspection - No repairs or service needed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 05/12/2020 | 02:35 PM
02/13/2020 |  | Routine, Scheduled | 04-197-176 | Wise County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Lenowisco | DEEL, DENNY M | 1942001097 | DENNY | DEEL |  |  | Orenco Advantex | None | Pump | Distribution Box | Aggregate Bed | None | 200.000000 | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump"] |  | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/18/2020 | Jan 1 1900 10:53AM
03/03/2020 |  | Routine, Scheduled |  | Loudoun County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | None | Pump | Distribution Box | Aggregate Trench | [23 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/12/2020 | 02:21 PM
02/07/2020 |  | Reportable Incident | 228-11-0654 | Virginia Beach | This AOSS should now return to normal function after having provided the above stated routine maintenance. | Approved | EHD - Virginia Beach | [13 empty] | ["Control Operation","Distribution Pump Operation","Effluent Screens"] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation"] | [18 empty] | [Comments]: Cleaned screen filter and pump screen | This AOSS should now return to normal function after having provided the above stated routine maintenance. |  | 02/07/2020 | Jan 1 1900 8:30AM
09/11/2020 | Alternative | Routine/Scheduled | 151-04-207 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | PremierTech, EFX | None | Pump | None | Aggregate Bed | None | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | Musty | Clear | [15 empty] | Routine service Septic tank - normal operating level - effluent screen serviced. Pump Basin - Minor bulging noted at bottom of unit - pump, float sensors and controls operating Peatmoss biofilter changed out 2020 - excellent condition - raked and turned. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 09/14/2020 | 07:30 AM
10/15/2020 |  | Follow-Up | 234-15-433 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [10 empty] | N/A | [17 empty] | Replaced UV circuit board, assembly, light cord, and bulb. (Used 3' of 3 wire and 2 - H2O tight water connectors.) Need a 3/4" brass check valve to go in front of the spinfilter assembly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 10/15/2020 | Jan 1 1900 12:00PM
05/06/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/14/2021 | 04:27 PM
05/12/2020 |  | RoutineScheduled |  | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | [9 empty] | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | [8 empty] | 05/12/2020 | Sample Chamber | 12.000000 | [7 empty] | Septic/ATU had 3" sludge 0" scum ATU had 0" sludge cleaned air filter for blower. Pump cnts-327 ETM- 71h 13m Zone#1-1 ff-7 Zone#2-0 ff-7 Peak-15 H/L-12 ETM-59h 30m | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
06/12/2020 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Eco Virginia | 1942001235 | William | Poindexter | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected | 7.3 A 250.58 hrs 16074 cy | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 |  | 06/03/2021 | 05:53 AM
02/27/2020 |  | Routine, Scheduled |  | Loudoun County | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Paid | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | None | None | Pump | Distribution Box | Aggregate Trench | [22 empty] | [Comments]: Sale inspection on a conventional pump system . The septic control panel is a exterior demand dose. There is 1 pvc clean out near the house. The sewer line was camera snaked and was clear. The septic tank has risers on both the inlet and outlet side of tank. The tank was pumped out and inspected for any leaks or cracks and the filter was cleaned. The state law requires the septic tank be pumped out every 5 years and the manufacture recommends the filter be cleaned every 6 months. The pump tank, pump, floats and force main were inspected. The 10 port splitter box and both 8 port d-boxes were dug up and all 3 are cracked and broken and will need to be replaced. The pvc header lines were camera snaked and were clear. The drain field was probed and was dry. At this time the septic system is not in working condition. The health dept will need to come out and issue a permit to replace all 3 boxes | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 04/12/2020 | 02:21 PM
11/06/2020 |  | Routine/Scheduled | 04-174-0078 | Prince George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Crater | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. |  |  | Ecoflo |  | Pump |  |  |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 11/06/2020 | Jan 1 1900 4:00AM
02/03/2020 |  | Routine, Scheduled | SWP-04-355 | Spotsylvania County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001350 | Mike | Cook | 1.000000 |  | Puraflo | None | Pump | Distribution Box | Aggregate Trench |  |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/11/2020 | 01:54 PM
10/10/2020 |  | RoutineScheduled | SD-02-431 | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Wastemaster Inc |  | Timothy | Jenkins | 2.000000 |  | Recirculating Sand Filter |  | Pump | Gravity | Discharge | Chlorination |  | [] | [] |  | Musty | Clear | 6.600000 |  |  | 1.700000 | [12 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 10:15 AM
12/07/2020 |  | Routine, Scheduled | 124-STS-2379 | Fairfax | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | EcoPod | EZ Treat Sandfilter |  |  |  | UV Light |  | ["Blower/Compressor/Aerator Operation","Disinfection"] | ["Blower/Compressor/Aerator Operation"] |  | Good | Clear | 7.300000 | 20.600000 |  |  |  | 12/07/2020 | Discharge | 23.000000 |  | 2420.000000 | 7.000000 |  |  |  |  | UV bulb needs replacement. Pump 1 Amps 9.93 ETM 131 hrs Cycles 7313 Pump 2 Amps 9.60 ETM 140 hrs Cycles 7800 Septic Sludge 5" Scum 5" ATU Sludge 4" Scum 0 Pump Sludge 4" Scum 0 | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12/07/2020 | Jan 1 1900 1:30PM
03/13/2020 |  | Routine, Scheduled |  | Loudoun County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | None | None | Pump | Distribution Box | Aggregate Trench | [23 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/16/2020 | 11:28 AM
04/09/2020 |  | Routine, Scheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Puraflo |  |  |  |  | None |  | ["Effluent Screens"] | ["Effluent Screens"] | [18 empty] | Pump 1 ETM 102.06 Cycles 6710 Pump 2 ETM 108.08 Cycles 6629 Septic Sludge 8" Scum 1" Pump Sludge 0 Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/09/2020 | Jan 1 1900 11:35AM
10/30/2020 | Alternative | Routine/Scheduled | 159-13-0068 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | PremierTech, EFX |  | Pump | Distribution Box | Aggregate Trench | None | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | Musty | Clear | [15 empty] | Routine Service Primary Septic Tank - normal operating level - effluent screen serviced. Biofilter - Concrete - Peatmoss in good condition - raked / turned. Pump Basin - normal operating level - pump, float sensors & controls operating properly. Distribution box - intact - all laterals accepting effluent. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 11/03/2019 | 08:00 AM
03/25/2020 |  | Routine, Scheduled | 04-160-0449 | Montgomery County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - New River | Conner, Timothy Wayne | 1942001003 | Timothy | Conner | 1.000000 | 1000 | Microfast | None | Gravity | Distribution Box | Aggregate Trench | None | [21 empty] | [Pumpout Comments]: TANK WAS LAST PUMPED ON 12/12/2017 RECOMMEND TANK BE PUMPED AND CLEANED [Lab Comments]: NO SAMPLE PORT ONSITE [Comments]: EVERYTHING APPEARS TO BE FUNCTIONING PROPERLY AT THIS TIME RECOMMEND TANK BE PUMPED AND CLEANED. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/26/2020 | 09:15 AM
07/30/2020 |  | Reportable Incident | 181-06-0267 | Rockbridge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Valley Soil & Environmental Consulting, LLC | 1942001218 | John | Lam | 4.000000 | 4000 | Septic tank only |  | Pump | Pressure | Trenches | Not Applicable | 600.000000 | ["Control Operation"] | [] | NA | [17 empty] | Service call due to alarm event at LPD #4 transfer pump control panel; found control panel alarm light activated; inspected transfer pump tank-water level at normal level below alarm float; found alarm float operational; suspect a faulty circuit board relay within the control panel and recommend replacing panel with a new control panel or new circuit board. The wiring within the electrical subpanel supplying power to the pump control panels does not appear to meet electrical code-ground wire from feeder line terminates on neutral buss bar with no separate neutral feeder line. Recommend evaluation by a licensed electrician. Transfer pump alarm float activates that alarm buzzer when float is raised. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
09/08/2020 |  | RoutineScheduled | 061-17-398 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
10/15/2020 |  | Routine, Scheduled | 175-03-0407 | Manassas | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Orenco Advantex |  |  |  |  | None |  | ["Dispersal System Operation","Effluent Screens","Recirculation Pump","Sludge/Scum Accumulation"] | ["Dispersal System Operation","Effluent Screens","Recirculation Pump"] | [18 empty] | Strongly recommend pumping. Pump Amps 12.50 ETM 418733 mins Cycles 842561 Pump Amps 11.61 ETM 23355 mins Cycles 636931 Septic Sludge 18" Scum 2" ATU Sludge 20" Scum 0 Pump Sludge 3" Scum 0 On 4 mins 23 secs Off 12 hrs | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 10/15/2020 | 11:56 AM
01/03/2020 |  | Routine, Scheduled | SD-01-573 | Fauquier County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Puraflo |  |  |  |  | None |  | ["Effluent Screens"] | ["Effluent Screens"] | [18 empty] | [Comments]: Pump Amps 8.45 ETM 333.83 Cycles 25749Septic Sludge 9" Scum 2"Pump Sludge 1" Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/03/2020 | 10:48 AM
05/19/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Payment | EHD - Loudoun | Great Falls Septic Service, Inc | 1942001301 | Josh | Hott | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/27/2021 | 11:51 AM
12/10/2020 |  | RoutineScheduled | 02-113-378 | Buchanan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Effluent Screens"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
05/21/2020 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU | [6 empty] | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  |  | 7.000000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 05/21/2020 | Jan 1 1900 11:00AM
09/22/2020 |  | RoutineScheduled | 061-STS-21686 | Fauquier | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [7 empty] | 09/22/2020 | [7 empty] | Will be sent separately | Inspected | Routine inspection and first BOD sample. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
02/04/2020 |  | Routine, Scheduled | {FIPSCode}-STS-3098 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesapeake | R & K Septic, Inc. |  | John | Butt, Jr |  |  | Clearstream ATU |  | Pump | Drip | Elevated Sand Mound | UV Light |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] |  |  |  | 7.960000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/04/2020 | Jan 1 1900 12:30PM
10/09/2020 |  | RoutineScheduled | 187140143 | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Greenway Engineering | 1942001008 | Jeremy | Ferguson | 1.000000 | 1500 | Advantex | none | Pump | Pressure | Drip | Not Applicable |  | ["Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 10/12/2020 | 10:30 AM
10/17/2020 | Alternative | RoutineScheduled | 171-03-0190 | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | dovel enterprises |  | jerry | dovel | 2.000000 | 1000 | 1000 |  | Pump | Pressure | Drip |  |  | [] | [] |  | None | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 10/29/2020 | 12:00 AM
05/04/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/27/2021 | 01:26 PM
09/16/2020 |  | RoutineScheduled | 154-05-0954 | Louisa | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 | Approved | EHD - Blue Ridge | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Effluent Screens" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Effluent Screens" ,"Recirculation Pump"] | YES | [15 empty] | Will be sent separately | Inspected | We recommend replacing the EZ Set riser & lid on the Pump Tank & installing a new Orenco lid on the Septic Tank. The Advantex Module has settled and is not draining properly. The owner indicated he can probably complete this repair. | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 |  | 04/09/2021 | 03:25 PM
04/07/2020 |  | Routine, Scheduled |  | Loudoun County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim |  |  | None | None | Pump | [7 empty] | YES | YES | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/12/2020 | 02:21 PM
07/22/2020 |  | RoutineScheduled | 05-113-076 | Buchanan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. |  | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Mound | Not Applicable | 200.000000 | ["BlowerCompressorAerator Operation","Effluent Screens"] | ["BlowerCompressorAerator Operation","Control Operation","Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
10/21/2020 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump | Distribution Box | Aggregate Bed | None |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  |  | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 10/21/2020 | Jan 1 1900 3:30PM
10/23/2020 |  | RoutineScheduled | 033-07-0354-ST | Caroline | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Control Operation"] | ["Recirculation Pump" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | House vacant since early August. Tank does not need pumping. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
02/21/2020 |  | Routine, Scheduled |  | Loudoun County | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Paid | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | None | Pump | Distribution Box | Gravel-Less Bed | [22 empty] | [Comments]: 2nd pump tank needs pumped out | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 04/12/2020 | 02:21 PM
09/08/2020 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintanence requirements | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Gravity | Gravity |  | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | A septic inspection was done on a conventional pump system. The state requires that all septic tanks must be pumped out EVERY 5 years and filed with the state and county. The septic control panel is an interior demand dose. There are 2 pvc clean outs. The 2nd clean out is broken and will need to be fixed. The sewer line was camera snaked and was clear. The concrete septic tank was pumped out and the filter was cleaned. There is a plastic riser on the outlet The manufacture recommends the filter be cleaned every 6 months. The pump tank, pump, floats and force main were inspected. The concrete lid will need to be replaced. The 6 port concrete splitter and both d-boxes were dug up they were 12" under the ground. All 12 header lines were camera snaked and were clear. The drain field was probed and dry. At time of inspection the system was not in working condition. | This AOSS is not functioning as designed or in accordance with the performance/maintanence requirements |  | 04/14/2021 | 04:27 PM
09/25/2020 |  | Routine/Scheduled | 05-160-0397 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Orenco Advantex |  | Gravity | Distribution Box |  | None |  | ["None"] | ["Control Operation","Level Sensor (Float) Operation","Recirculation Pump","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 09/25/2020 | 03:15 PM
12/09/2020 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Fairfax | FIVE STAR SEPTIC INC | 1944001248 | AARON | GOINS | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
12/10/2020 |  | RoutineScheduled | 107-11-0285 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Central Shenandoah | Onsite Wastewater Services - May Supply | 1942001627 | Drew | Shull | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/03/2022 | 12:05 PM
12/23/2020 |  | Follow-Up | 175-18-0488 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green | [9 empty] | ["Disinfection"] | ["Disinfection"] | [18 empty] | Installed new Salcor UV Bulb. | This AOSS should now return to normal function after having provided the above state routine maintenance |  | 12/23/2020 | 04:00 PM
02/04/2020 |  | RoutineScheduled | 069051086 | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Combs Wastewater Management LLC | 1942001353 | Amy | Combs | 2.000000 | 1000 |  |  | Pump | Gravity | Drip | Not Applicable | 450.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12/28/2020 | 12:00 AM
06/19/2020 |  | RoutineScheduled | SD-03-151 | Madison | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["SludgeScum Accumulation"] |  | NA | [15 empty] | Will be sent separately | Inspected | Quarterly Inspection We recommned pumping the Septic Tank due to scum & sludge accumulation. Pumping has been scheduled for July 8, 2020. Replaced damaged 24" EZ Set Lid | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/09/2021 | 03:25 PM
06/26/2020 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Loudoun | Soils, Inc. | 1942001004 | Markham | Smith | 2.000000 | 1500, 2000 | MicroFAST .75 ATU |  | Pump | Gravity | Trenches | Not Applicable | 57.000000 | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [17 empty] | Checked and cleared blower vents. System in good condition - no issues found. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 08/06/2020 | 05:00 PM
08/28/2020 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump | Drip | Elevated Sand Mound | UV Light |  | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  | 1.29 | 7.500000 | 4.700000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 08/28/2020 | Jan 1 1900 2:30PM
11/18/2020 |  | RoutineScheduled | 2016-143-0120 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | GeoEnvironmental Services, Inc. | 1942001010 | Peter | Mamunes | 1.000000 | 1000 | EcoPOD |  | Pump | Pressure | Drip |  |  | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["SludgeScum Accumulation","Level Sensor Operation","Effluent Screens","Distribution Pump Operation","Dispersal System Operation","BlowerCompressorAerator Operation","Control Operation","Attached Growth Medium","Auxiliary Filter"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12/15/2020 | 11:25 AM
06/11/2020 |  | Follow-Up |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Unclogged pods 1,3 and 4. System working as it should | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/14/2021 | 04:27 PM
09/28/2020 |  | RoutineScheduled | SP-04-335 | Stafford | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Effluent Screens" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Effluent Screens" ,"Recirculation Pump"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 |  | 04/09/2021 | 03:25 PM
09/14/2020 |  | Reportable Incident | 175-17-0444 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green | [9 empty] | ["Dispersal System Operation"] | ["Dispersal System Operation"] | [18 empty] | Replaced broken ARV & yard box. | This AOSS should now return to normal function after having provided the above state routine maintenance |  | 09/14/2020 | 04:00 PM
10/13/2020 |  |  | 185-STS-17515 | Tazewell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 10/13/2020 | [10 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 10/13/2020 | 12:00 AM
07/24/2020 |  | Routine/Scheduled | 12-163-0075 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chickahominy | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. |  |  | Clearstream ATU |  | Pump |  |  |  |  | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | Rebuilt blower | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 07/24/2020 | Jan 1 1900 9:00AM
05/20/2020 |  | RoutineScheduled | 107-03-0367 (LEGACY ALT. SYSTEM) | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Onsite Wastewater Services - May Supply | 1942001022 | Sara | Tusing | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 05/28/2021 | 05:41 AM
01/02/2020 |  | Routine, Scheduled | 136-18-0101 | Gloucester County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers | Farmer’s Septic Service, Inc. |  | Ross | Cole | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | [Comments]: Serviced system. Checked the pump, panel, & floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. The timer is set to 2 minutes every 2 hours. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/02/2020 | 12:00 PM
08/10/2020 |  | Routine/Scheduled |  | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Whitewater ATU |  | Pump | Distribution Box |  | None |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  |  | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 08/10/2020 | Jan 1 1900 9:30AM
09/29/2020 |  | RoutineScheduled | 099-STS-86749 | King George | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Control Operation" ,"Attached Growth Medium" ,"Auxiliary Filter" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | ["Control Operation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Attached Growth Medium" ,"Auxiliary Filter" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | YES | [15 empty] | Will be sent separately | Inspected | BOD collected, waiting on results. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
01/13/2020 |  | Routine, Scheduled |  | Louisa County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Blue Ridge | CLARK, MICHAEL J | 1934000023 | MICHAEL | CLARK |  |  | Septic Tank Only | Septic Tank Only | None | None | None | None |  |  | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/14/2020 | 03:17 AM
02/12/2020 |  | Routine, Scheduled |  | Buchanan County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Cumberland Plateau | DEEL, DENNY M | 1942001097 | DENNY | DEEL |  |  | Norweco Singulair ATU | None | Gravity | None | Alternative Discharge | Chlorine | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens"] |  | Musty | Clear | [15 empty] | [Comments]: 5 Blue Crystal 15 Bio Max Added | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/18/2020 | Jan 1 1900 11:34AM
04/17/2020 |  | Routine, Scheduled |  | Louisa County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Blue Ridge | CLARK, MICHAEL J | 1934000023 | MICHAEL | CLARK |  |  | Septic Tank Only | Septic Tank Only | None | None | None | None |  |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/19/2020 | 04:03 AM
09/02/2020 |  | RoutineScheduled |  | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Ashleys Septic Service | 1930332 | Shane | Majewski | 1.000000 | 1500 |  |  | Pump | Gravity | Trenches | Not Applicable | 750.000000 | ["None"] | ["None"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 09/17/2020 | Jan 1 1900 2:05AM
08/25/2020 |  | RoutineScheduled | 01-197-416 | Wise | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Mound | Not Applicable | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","Effluent Screens"] | ["BlowerCompressorAerator Operation","Control Operation","Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
03/14/2020 |  | Routine, Scheduled |  | Page County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Lord Fairfax | DOVEL, JERRY A | 1942001116 | JERRY | DOVEL | 1.000000 |  | Biomicrobics MicroFAST | Septic Tank Only | None | Drip | None | None | [22 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/22/2020 | 09:41 AM
05/08/2020 | Alternative | RoutineScheduled | 104-07-0142 | Amherst | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Acres of Virginia, Inc. | 1942001044 | Melvin | Collins | 1.000000 | 500 | BEST 1 |  | Gravity | Gravity | Trenches | Not Applicable | 450.000000 | ["None"] | ["None"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 06/24/2020 | 01:05 PM
05/04/2020 |  | Reportable Incident | 175-16-0407 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 | Approved | EHD - Prince William | Ace Contracting Services Inc | 1942001120 | Lawrence | Fellenz Jr. | 1.000000 |  | none | none | Pump | Gravity |  | Not Applicable |  | ["Effluent Screens" ,"Recirculation Pump"] | ["Effluent Screens" ,"Recirculation Pump"] | YES | [15 empty] | Will be sent separately | Inspected | Pumped Out Pump Station And Septic Tank Upgraded Pump From Zoeller N140 To A Zoeller N163 | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 |  | 06/29/2021 | 10:39 PM
12/30/2020 |  | RoutineScheduled | 175-05-0542 | Prince William | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Attached Growth Medium" ,"SludgeScum Accumulation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Attached Growth Medium"] | NA | [15 empty] | Will be sent separately | Inspected | We recommend pumping the Aerobic Treatment Unit due to sludge accumulation. The Pump Tank is leaking where the filter return pipe exits the tank. | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 |  | 04/09/2021 | 03:25 PM
08/21/2020 |  | Routine, Scheduled | 175-04-0222 | Prince William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Aquarobic Mini Plant |  |  |  |  | None |  | ["Blower/Compressor/Aerator Operation"] |  |  | Acceptable | Clear | [15 empty] | Only 3 of 8 air diffusers are working. Pump Amps 4.24 Compressor 2.3 Amps ATU Sludge 5" Scum 0 | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 08/21/2020 | 10:49 AM
06/11/2020 |  | RoutineScheduled | SD-05-094 | Orange | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Ecoflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Attached Growth Medium"] | ["SludgeScum Accumulation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Septic Tank Baffles" ,"Attached Growth Medium" ,"Distribution Pump Operation"] | YES | [15 empty] | Will be sent separately | Inspected | Retimed distribution box best as possible; it has settled. Few roots on inlet wedge lid of septic tank. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
06/30/2020 |  | Routine/Scheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | POWELLS PLUMBING, INC. | 1942001036 | Kurt | Holthaus | 1.000000 | 1000 | Microfast |  | Gravity | Distribution Box | Aggregate Trench |  | 400.000000 | ["Blower/Compressor/Aerator Operation","Dispersal System Operation"] | ["Blower/Compressor/Aerator Operation","Dispersal System Operation"] | N/A | [17 empty] | Annual Inspection - Serviced blower and customer replaced 6" cleanout cap. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 07/17/2020 | 12:07 PM
11/10/2020 |  | RoutineScheduled | 10-197-071 | Wise | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | CLEARSTREAM |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Effluent Screens"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
05/13/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Payment | EHD - Loudoun | Great Falls Septic Service, Inc | 1942001301 | Josh | Hott |  |  | Delta Environmental Products, UC Series | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/27/2021 | 11:51 AM
10/20/2020 |  | Routine/Scheduled | 800-STS-14487 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Western Tidewater | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 9000 | Advanced Septic |  | Pump | Distribution Box | Aggregate Trench | None | 4500.000000 |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Recirculation Pump","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | Musty | Clear | [5 empty] | 10/20/2020 | Clarifier Outfall | 26.000000 |  |  | 42.700000 |  |  |  |  | Monthly Service conducted for Consent Order. Septic Tank / Flow Equalization Tank - normal operating level - both pumps pulled and "de-ragged". Pumps, float sensors and controls operating properly. Aeration tank - normal operating level - serviced compressor #2 & #4. Clarifier functioning properly - Laboratory samples for BOD5 & TSS obtained at Clarifier outfall. - Lab samples transported to Universal Laboratories, Hampton. Pump Tank - normal operating level - pumps, float sensors and controls operating properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 10/21/2020 | Jan 1 1900 7:30AM
12/09/2020 | Alternative | Routine/Scheduled | 166-05-818 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 2.000000 | 2500 | Microfast |  | Pump | Distribution Box | Aggregate Trench |  |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12/09/2020 | 05:00 PM
06/06/2020 |  | RoutineScheduled | 06-192-361 | Tazewell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. |  | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Effluent Screens"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
06/10/2020 |  | Routine/Scheduled |  | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Three Rivers | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | None | None | Pump | Distribution Box | Aggregate Trench | None | 450.000000 |  | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | [17 empty] | Routine scheduled pumpout of septic tank. Routine pumpout of Septic Tank | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 06/15/2020 | 8:30AM
04/09/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS should now return to normal function after having provided the above stated routine maintenance. | Approved | EHD - Fairfax | SEAMON, CHARLIE L | 1942001108 | CHARLIE | SEAMON |  |  | Septic Tank Only | Septic Tank Only | None | None | None | None |  | ["BlowerCompressorAerator Operation","Disinfection","Dispersal System Operation"] | ["BlowerCompressorAerator Operation"] | [18 empty] | [Comments]: Performance Inspection:Microfast to Jet UV Light to American Drip.Septic-8"sludge 4"scum/Microfast- 6"sludge/Pump tank-0"sludge. No pump out needed. Blower air filter cleaned. Counts:Z1-339 ff-22/Z2-336 ff-21/Pump-718 ETM-161h 43m/Peak-6 ETM-24h 49m/High-8 ETM-0/ Water meter-049429.08 No breakout or spongy areas on the drip field. | This AOSS should now return to normal function after having provided the above stated routine maintenance. |  | 04/14/2020 | Jan 1 1900 6:11AM
04/21/2020 |  | Routine/Scheduled |  | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump | Drip | Elevated Sand Mound | None |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  |  | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/21/2020 | Jan 1 1900 10:00AM
10/02/2020 | Alternative | RoutineScheduled | 40977 | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Combs Wastewater Management LLC | 1942001353 | Amy | Combs | 2.000000 | 1000 |  |  | Gravity | Gravity | Trenches | Not Applicable | 450.000000 | [] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12/28/2020 | 12:00 AM
07/27/2020 |  | RoutineScheduled | 187090198 | Warren | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Rejected | EHD - Lord Fairfax | Greenway Engineering | 1942001008 | Jeremy | Ferguson | 1.000000 | 1250 | Microfast | none | Pump | Pressure | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation","SludgeScum Accumulation"] | ["SludgeScum Accumulation"] | NA | [17 empty] | Needs Blower pipe fixed. Approved once repaired. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. |  | 07/27/2020 | 02:40 AM
07/30/2020 |  | Routine/Scheduled | 196-09-162 | Westmoreland | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Three Rivers | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 500 | Biomicrobics MicroFAST | None | Pump | Distribution Box | Gravel-Less Trench | None | 450.000000 | ["Blower/Compressor/Aerator Operation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | Pungent | Discolored | [15 empty] | Annual service conducted. Trash Tank at normal operating level BioMicrobics FAST - not operational at this time - Blower unit appears to have failed - power to controls, but blower unit is non functional - Pump Tank - found at normal operating level - discharge pump, float sensors and controls operating properly. Distribution box - at normal operating level - all laterals accepting effluent. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 07/31/2020 | 07:30 AM
01/10/2020 |  | Routine, Scheduled |  | Warren County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Lord Fairfax | Ferguson, Jeremy | 1942001008 | Jeremy | Ferguson | 1.000000 | 1000 | Biomicrobics MicroFAST | None | Pump | Drip | Drip Tubing | None |  |  | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | [Comments]: System is in compliance with approved plans and health department regulations. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/31/2020 | 04:21 PM
10/26/2020 |  | RoutineScheduled | 179-12-0022-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump" ,"Attached Growth Medium"] | ["Effluent Screens" ,"Recirculation Pump" ,"Attached Growth Medium" ,"Distribution Pump Operation"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 |  | 04/09/2021 | 03:25 PM
10/13/2020 |  | Routine, Scheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Biomicrobics MicroFAST |  | Pump |  |  | None |  | ["Blower/Compressor/Aerator Operation"] | ["Blower/Compressor/Aerator Operation"] |  | Acceptable | Clear | [15 empty] | Pump 1 Amps 10.75 ETM 27 hrs Cycles 1216 Pump 2 Amps 10.88 ETM 26 hrs Cycles 1161 Septic Sludge 4" Scum 8" ATU Sludge 4" Scum 0 Pump Sludge 0 Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 10/13/2020 | Jan 1 1900 2:37PM
06/11/2020 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Gravity | Gravity |  | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | A septic system inspection was done on a conventional pump system. The interior control panel is a demand dose. There is a pvc cleanout near the house. The pvc sewer line was camera snaked and was clear. The septic tank has a concrete riser and was pumped out. Just for some info the state law requires that all conventional septic tanks be pumped out every 5 years and filed with the state and local county. The pump tank, pump, floats and force main were inspected. Per the realtor the d-boxes were not dug up. the drain field was probed and was dry. At time of inspection all components were in working condition. | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 |  | 04/14/2021 | 04:27 PM
10/14/2020 |  | RoutineScheduled | VAG401576 | Augusta | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Gravity | Gravity | Discharge | Chlorination |  | ["None"] | ["None"] | NA | Musty | Clear | [15 empty] | no discharge during visit | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  |  | 12:00 AM
10/06/2020 |  | Reportable Incident | 073-STS-93567 | Gloucester | This AOSS should now return to normal function after having provided the above state routine maintenance | Approved | EHD - Three Rivers | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | PremierTech, EFX |  | Pump | Distribution Box | Aggregate Bed | None | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | None | Clear | [15 empty] | Installation Inspection - HDID - 136-20-0109 Primary Septic Tank - pumped empty 09/25/2020 to effect repair. BioFilter - Failed fiberglass unit removed - new concrete unit with integral pump station installed. Pump, float sensors and controls operating properly. Absorption Bed - not disturbed - distribution box intact and balanced properly | This AOSS should now return to normal function after having provided the above state routine maintenance |  | 10/06/2020 | 08:00 AM
09/03/2020 |  | Routine, Scheduled | 175-11-0237 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Puraflo |  |  |  |  | None |  | ["Effluent Screens"] | ["Effluent Screens"] | [18 empty] | Spin filter cleaned. Pump 1 Amps 6.28 ETM 47046 Cycles 3919 Pump 2 Amps 10.10 Cycles 32325 Water Meter Reading 927250 Septic Sludge 6" Scum 0.50 Pump Sludge 3" Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 09/03/2020 | 01:54 PM
11/20/2020 |  | Routine, Scheduled | SD-02-323 | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Orenco Advantex |  |  |  |  | None |  | ["Attached Growth Medium","Effluent Screens"] | ["Attached Growth Medium","Effluent Screens"] |  | Acceptable | Clear | [15 empty] | Pump Amps 12.65 ETM 454254 Cycles 92643 Pump Amps 10.27 ETM 17786 min Cycles 23460 Septic Sludge 5" Scum 1" ATU Sludge 15" Scum 1" Pump Sludge 2" Scum 0 On 4 mins 45 secs Off 4 hrs | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 11/20/2020 | 04:44 PM
10/22/2020 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/Maintenance requirements | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Gravity | Gravity |  | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | ADDRESS 23080 NO record of septic system.. Main House There is a clean out near the tank. The sewer line was camera snaked and was clear. The septic tank was inspected. The conveyance line was camera snaked and was clear. The concrete d-box was dug up and found badly broken and will need replaced. The header lines were camera snaked and the drain field was probed and dry. at time of inspection system is not in working condition. | This AOSS is not functioning as designed or in accordance with the performance/Maintenance requirements |  | 04/14/2021 | 04:27 PM
10/21/2020 |  | RoutineScheduled | 12-197-A4 | Wise |  | Approved | EHD - Lenowisco | VDH |  | Brad | Stallard | [12 empty] | None | Cloudy | 7.500000 | 0.000000 |  | 0.000000 | [11 empty] | No labs submitted |  |  |  | 12:00 AM
09/11/2020 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump | Drip |  | UV Light |  | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  |  | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 09/15/2020 | Jan 1 1900 10:30AM
12/01/2020 |  | Routine, Scheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Puraflo |  |  |  |  | None |  | ["Effluent Screens"] | ["Effluent Screens"] | [18 empty] | Pump 1 Amps 9.70 ETM 404.81 Cycles 27072 Pump 2 Amps 9.72 ETM 418.26 Cycles 27255 Septic & Pump tanks pumped for real estate transfer. On 1 min 30 secs Off 2 hrs | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 12/01/2020 | Jan 1 1900 1:30PM
03/14/2020 |  | RoutineScheduled | 175-13-0413 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Prince William | Onsite Wastewater Services - May Supply | 1942001022 | Sara | Tusing | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/28/2021 | 05:41 AM
03/04/2020 |  | Routine, Scheduled |  | Mathews County | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Paid | EHD - Three Rivers | Farmer’s Septic Service, Inc. |  | Ross | Cole | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | [Comments]: Serviced system. Checked the pump, panel, & floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. The UV is not working - power going to the panel but not to the light - also the alarms on the UV panel are not working. The timer is set to 1.5 minutes every 1.5 hours. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 03/04/2020 | 12:00 PM
08/03/2020 |  | RoutineScheduled | 175-18-0088 | Prince William | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump" ,"Auxiliary Filter" ,"Attached Growth Medium" ,"SludgeScum Accumulation"] | ["Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump" ,"Auxiliary Filter" ,"Attached Growth Medium"] | YES | [15 empty] | Will be sent separately | Inspected | The grommet in the RSV needs to be replaced. A replacement has been ordered from the manufacturer. We recommend pumping the Advantex Tank and the Pump Tank. Please contact our office if you would like our assistance with this work. | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 |  | 04/09/2021 | 03:25 PM
04/01/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Loudoun | SES MidAtlantic LLC | 1942001203 | James | Green | 1.000000 |  | EcoPod | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [9 empty] | 185.000000 | [5 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/15/2021 | 09:00 AM
07/27/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | The drainfield is in an open space/common area. Recommend scheduling inspection earlier in the year before drainfield area gets too high or after the field is bush hogged so we can more clearly see the drainfield area. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/27/2021 | 01:26 PM
05/27/2020 |  | Pump-Out Only |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | POWELLS PLUMBING, INC. | 1942001036 | Kurt | Holthaus |  |  | Puraflo | [6 empty] | ["Sludge/Scum Accumulation"] | ["Sludge/Scum Accumulation"] | N/A | [17 empty] | Pumped septic. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 06/19/2020 | 02:33 PM
07/16/2020 |  | Initial Visit | 175-STS-15139 | Southampton | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Western Tidewater | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | Puraflo | None | Gravity | None | Aggregate Bed | None | 600.000000 | ["Attached Growth Medium","Septic Tank Baffles"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | Pungent | Clear | [15 empty] | Initial service visit ... Primary septic tank in normal operating level - no riser access present over effluent screen - outlet side of tank excavated and effluent screen serviced. Recommend to owner installation of riser access. Discharge tank in normal operating level - evidence of infiltration present at base of riser access - recommend parge / sealing - pump, float sensors and controls operating properly. Peatmoss Biofilter has reached end of life and requires replacement. Ponding evident in modules - no overflow noted. Absorption bed appears to be intact, no indications of surfacing. System marked as good as there is no evidence of backup to residence or treated / untreated sewage to ground surface. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 07/17/2020 | Jan 1 1900 8:00AM
08/04/2020 |  | RoutineScheduled | 069-17-0135 | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Greenway Engineering | 1942001008 | Jeremy | Ferguson | 1.000000 | 1500 | Advantex | none | Pump | Pressure | Drip | Not Applicable |  | ["Level Sensor Operation","SludgeScum Accumulation"] | ["SludgeScum Accumulation","Level Sensor Operation"] | NA | [7 empty] | 08/04/2020 | Pump Chamber | 4.190000 | [5 empty] | Will be sent separately |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 09/28/2020 | 10:00 AM
03/11/2020 |  | Routine, Scheduled | 15-197-006 | Wise County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Lenowisco | DEEL, DENNY M | 1942001097 | DENNY | DEEL |  |  | Septic Tank Only | None | Siphon | Distribution Box | None | None | 200.000000 | ["Dispersal System Operation","Distribution Pump Operation","SludgeScum Accumulation"] | ["Dispersal System Operation","Distribution Pump Operation"] |  | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/20/2020 | Jan 1 1900 1:46PM
07/16/2020 |  | Reportable Incident |  | Mathews | This AOSS should now return to normal function after having provided the above state routine maintenance | Pending Review | EHD - Three Rivers | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | None | None | Pump | Distribution Box | Aggregate Trench | None | 450.000000 |  | ["Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | [17 empty] | Primary septic tank and pump tank pumped empty for repair. Alarm Event - Septic System pumped empty to facility repair. Found discharge forcemain fractured in pump tank. - Repaired. No control panel - piggy back demand - audible alarm in residence. | This AOSS should now return to normal function after having provided the above state routine maintenance |  | 07/17/2020 | 9:00AM
04/18/2020 |  | RoutineScheduled | 133 07 0459 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1000 | Advantex |  | Pump | Gravity | Trenches |  |  | ["None"] | ["None"] | [18 empty] | 12" of solids in septic tank. Flushed treatment unit spray manifold. Tested floats, pumps and alarm. Cleaned septic tank filter. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 10/05/2020 | 07:03 PM
09/23/2020 |  | Routine/Scheduled | 12-160-0147 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | EcoPod |  | Pump | Drip | Drip Tubing | None |  | ["None"] | ["Attached Growth Medium","Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 09/23/2020 | 05:00 PM
03/13/2020 |  | Reportable Incident | 228-10-0468 | Virginia Beach | This AOSS should now return to normal function after having provided the above stated routine maintenance. | Approved | EHD - Virginia Beach | [13 empty] | ["Control Operation","Effluent Screens"] | ["Control Operation","Effluent Screens"] | [18 empty] | [Comments]: Replaced screen filter | This AOSS should now return to normal function after having provided the above stated routine maintenance. |  | 03/13/2020 | Jan 1 1900 8:00AM
03/10/2020 |  | Routine, Scheduled | 177-14-0221-SWP | Spotsylvania County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | None | Pump | Distribution Box | Aggregate Trench |  |  | ["Attached Growth Medium","None","Recirculation Pump"] | ["Attached Growth Medium","None","Recirculation Pump"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/06/2020 | 02:45 PM
12/10/2020 |  | Follow-Up | 04-197-A4 | Wise | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance. |  | EHD - Lenowisco | Wise County Health Dept |  | Rodney | Neece |  |  | ATU |  | Gravity | Gravity | Discharge | Chlorination | [7 empty] | 5.000000 | [14 empty] | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance. |  | 12/10/2020 | 12:00 AM
09/18/2020 |  |  |  | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | McKim Construction | 1942001330 | Michelle | McKim | 2.000000 |  |  |  | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Septic Tank Baffles","SludgeScum Accumulation","Level Sensor Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 11/13/2020 | Jan 1 1900 11:15AM
06/03/2020 |  | RoutineScheduled |  | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | [9 empty] | ["Attached Growth Medium"] | ["Attached Growth Medium"] | [8 empty] | 06/03/2020 | Sample Chamber | 84.000000 | [7 empty] | Septic tank had 14" sludge and 0" scum Pump tank had 4" sludge. EZ Treat module had broken piping inside. Repaired piping. Consulted EZ TREAT to adjust recirc times to improve water quality. BODs were high, however should improve with repaired piping and adjusted recirc. times. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  |  | 12:00 AM
12/08/2020 |  | RoutineScheduled |  | Warren | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity |  | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation"] | ["BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [7 empty] | 12/08/2020 |  | 18.000000 | [5 empty] | Will be sent separately | Inspected | Control panel was turned off Lab sample normal | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance |  | 04/26/2021 | 09:04 AM
08/28/2020 |  | Reportable Incident | 109-06-0001 | Bedford | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 11500 | Microfast |  | Pump | Pressure | Trenches | Not Applicable |  | [] | [] | NA | [16 empty] | Inspected | Pump panel near the large wharehouse had electrical suge, Blew the fuses, Replace fuses and got to operate again, Alarm not working and have put in request to electricians to replace panel | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 08/30/2020 | 09:30 AM
06/01/2020 |  | Routine, Scheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green | [5 empty] | Drip |  | None |  | ["None"] | ["None"] | [18 empty] | Pump 1 Amps 12.1 Pump 2 Amps 13.2 Water Meter Reading 141860 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 06/01/2020 | Jan 1 1900 2:10PM
08/03/2020 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Gravity | Gravity |  | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Installed a riser on the septic tank. And 5 header line crushed sections were replaced and are working as they should. | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 |  | 04/14/2021 | 04:27 PM
04/10/2020 |  | Routine, Scheduled |  | Albemarle County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Blue Ridge | CLARK, MICHAEL J | 1934000023 | MICHAEL | CLARK |  |  | Septic Tank Only | Septic Tank Only | None | None | None | None |  |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/19/2020 | 04:12 AM
06/03/2020 |  | Follow-Up | 179-13-0052-SP | Stafford | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation" ,"Dispersal System Operation"] | ["Dispersal System Operation" ,"Distribution Pump Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Repaired broken pump line. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/09/2021 | 03:25 PM
04/08/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Loudoun | SES MidAtlantic LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/15/2021 | 09:00 AM
08/10/2020 |  | Routine/Scheduled | 06-163-0164 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chickahominy | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. |  |  | Bionest |  | Pump |  |  |  |  | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump","Sludge/Scum Accumulation"] | N/A | [17 empty] | Rebuilt blower | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 08/19/2020 | Jan 1 1900 11:00AM
08/10/2020 |  |  | {FIPSCode}-STS-5420 | Buchanan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 08/10/2020 |  | 6.440000 | [5 empty] | Attached to this report |  | TSS: BDL | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 08/10/2020 | 12:00 AM
08/10/2020 |  | RoutineScheduled | {FIPSCode}-STS-13316 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Wastemaster Inc |  | Timothy | Jenkins | 2.000000 |  | ATU |  | Pump | Gravity | Discharge | Chlorination |  | ["SludgeScum Accumulation"] | [] |  | Musty | Clear | 7.200000 |  | 23.000000 | 1.600000 | [11 empty] | Multi Flo full of trash and grease. Filters showing sign of premature binding due to excessive grease | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 07:03 PM
03/12/2020 | Alternative | Routine/Scheduled | 157-10-0105 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | Serviced system. Checked the pump, panel, & floats (ok). Cleaned the filter and the diffuser in the Clearstream and cleaned the filter in the aerator | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 03/12/2020 | 12:00 PM
04/06/2020 |  | Routine, Scheduled |  | Albemarle County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Blue Ridge | CLARK, MICHAEL J | 1934000023 | MICHAEL | CLARK |  |  | Septic Tank Only | Septic Tank Only | None | None | None | None |  |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/12/2020 | 04:58 AM
02/20/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Puraflo |  |  |  |  | None |  | ["Effluent Screens"] | ["Effluent Screens"] | [18 empty] | [Comments]: Pump Amps 15.02/12.20 ETM 15238/15069 Cycles 11575/11540 Pump Amps 10.20/10.75Septic Sludge 5" Scum 1"Pump Sludge 0/1" Scum 0/0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/20/2020 | Jan 1 1900 9:13AM
04/27/2020 |  | RoutineScheduled | 196-08-033 | Westmoreland | This AOSS is functioning as designed and in accord | Approved | EHD - Three Rivers | [13 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accord |  |  | 12:00 AM
07/16/2020 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Ace Contracting Services Inc | 1942001120 | Lawrence | Fellenz Jr. | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 |  | 06/29/2021 | 10:39 PM
07/21/2020 |  | RoutineScheduled | SWP-04-221 | Stafford | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Attached Growth Medium"] | ["Recirculation Pump" ,"Attached Growth Medium"] | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/09/2021 | 03:25 PM
03/09/2020 |  | Routine, Scheduled |  | Loudoun County | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Paid | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | None | None | Gravity | [24 empty] | [Comments]: Sale inspection on a conventional gravity septic system. There is 1 pvc cleanout near the house. The sewer line was camera snaked all was good. The 1125 concrete septic tank has a plastic riser on it and was pumped out. The septic tank was inspected for leaks or cracks none were found. The pvc conveyance line was camera snaked and was clear. The 10 port concrete d-box was 3 feet under the ground. It was dug up and found to be broken and will need to be replaced. The header lines were camera snaked and were clear. The drain field was probed and dry. At this time the septic system is not in working condition. The Loudoun County Health dept will need to come out and issue a repair permit. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 04/12/2020 | 02:21 PM
05/20/2020 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump | Drip | Elevated Sand Mound | UV Light |  | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  |  | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 05/20/2020 | Jan 1 1900 3:00PM
12/14/2020 |  | Reportable Incident | 2016-143-0161 | Henrico | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Henrico | Old Dominion Onsite, Inc. | 1942001549 | Russell | Revis | [9 empty] | ["Blower/Compressor/Aerator Operation"] | ["Blower/Compressor/Aerator Operation"] | N/A | [17 empty] | Compressor had stopped functioning and needs to be rebuilt. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. |  | 12/14/2020 | 09:37 AM
04/18/2020 |  | RoutineScheduled | 133 07 0459 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1000 | Advantex |  | Pump | Gravity | Trenches |  |  | ["None"] | ["None"] | [18 empty] | 12" in septic tank. Flushed treatment unit spray manifold. Tested floats, pump and alarm. Cleaned septic tank filter. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 09/17/2020 | 07:03 PM
10/01/2020 |  | RoutineScheduled | SWP-04-216 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions | 2705163102 | Michele | Ware |  |  | Puraflo | [6 empty] | [] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 10/01/2020 | 12:00 AM
10/30/2020 |  | RoutineScheduled | 12-142-0020 | Hanover | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Norweco | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | YES | [17 empty] | Replace Norweco aerator and control panel light | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12/04/2020 | 12:00 AM
11/02/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/14/2021 | 04:27 PM
06/25/2020 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Loudoun | Soils, Inc. | 1940001392 | Markham | Smith | 2.000000 | 1500 | Textile: Adantex AX20 Orenco Ax20-2 |  | Pump | Pressure | Drip | Not Applicable |  | [] | ["Control Operation","Attached Growth Medium","Septic Tank Baffles","Recirculation Pump","Level Sensor Operation","SludgeScum Accumulation","Dispersal System Operation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 06/30/2020 | 12:15 AM
05/20/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | As per the new design of the AOSS there is pool construction in progress. The system shows no signs of malfunction at this time, but there is a packed dirt machine path from the driveway to the pool area. This could potentially be on/near conveyance lines/boxes. We strongly recommend that once the phase of the pool construction that requires machinery is completed, uncover the distribution boxes to check for potential damage. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/27/2021 | 01:26 PM
05/21/2020 |  | RoutineScheduled | 182-02-0623 (LEGACY ALT. SYSTEM) | Rockingham | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Central Shenandoah | Onsite Wastewater Services - May Supply | 1942001022 | Sara | Tusing | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/28/2021 | 05:41 AM
06/15/2020 |  | Follow-Up | 107-13-0001 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Onsite Wastewater Services - May Supply | 1942001022 | Sara | Tusing | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | PUMPING DONE BY ROTO ROOTER | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 05/28/2021 | 05:41 AM
10/20/2020 |  |  | 175-07-0149 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 3.000000 |  | Septic/ATU | Pump Tank | Pump | Pressure | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation","Dispersal System Operation","Level Sensor Operation"] | ["BlowerCompressorAerator Operation","Dispersal System Operation","Level Sensor Operation"] | NA | [17 empty] | Septic-7"sludge 0"scum/ ATU-0"sludge 3"scum/ Pump tank-0"sludge/ Blower air filter cleaned/ Replaced narrow angle alarm float. Replaced 24"plastic tank lid/ Replaced male adapter on check valve in the drip field zone 1 return/ Counts: Hand-22/ High-185/ Override-185/ Pump start-16502/ pump run-0/ water meter-1238413/ Recommend insulate zoner lid before winter/ wet area at the spot where the check valve was repaired, should return to normal now. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  |  | 12:00 AM
12/31/2020 |  | RoutineScheduled | 177-07-0079-SWP | Spotsylvania | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Drip | UV |  | ["Attached Growth Medium" ,"Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Recirculation Pump" ,"Disinfection"] | ["Distribution Pump Operation" ,"Recirculation Pump" ,"Disinfection" ,"Dispersal System Operation" ,"Attached Growth Medium" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/09/2021 | 03:25 PM
07/07/2020 |  | Routine, Scheduled | 153-STS-19077 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Biomicrobics MicroFAST |  |  |  |  | UV Light |  | ["Disinfection"] | ["Disinfection"] |  | Good | Clear | [5 empty] | 07/07/2020 | Pump tank | 35.000000 |  | 1600.000000 | [5 empty] | Spin filter cleaned. Pump Amps 11.38 ETM 63 hrs Cycles 472 Water Meter Reading 40500 Septic Sludge 3" Scum 3" ATU Sludge 3" Scum 0 Pump Sludge 0 Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 07/07/2020 | 01:01 PM
02/15/2020 |  | Routine, Scheduled | 139-07-166 | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Lord Fairfax | DOVEL, JERRY A | 1942001116 | JERRY | DOVEL | 1.000000 |  | Biomicrobics MicroFAST | Septic Tank Only | None | Drip | None | None | [22 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/07/2020 | 07:41 PM
01/03/2020 |  | Routine, Scheduled | 800-09-0044 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Western Tidewater | R & K Septic, Inc. |  | John | Butt, Jr |  |  |  |  | Pump |  |  | None |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] |  |  | 5.28 | 8.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/03/2020 | Jan 1 1900 8:30AM
10/27/2020 |  | Reportable Incident | 2016-143-0128 | Henrico | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Henrico | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | Owner called due to the aerator not running. Installed re-build kit on the aerator. Serviced system. Checked the pump, panel, & floats (ok). Changed the diffuser in the Clearstream and changed the filter in the aerator. Owner just had the septic tank pumped out. The timer is set to 3 minutes every 2 hours. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 10/27/2020 | 12:00 PM
12/11/2020 |  | Follow-Up | 08-197-A9 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | Wise County Health Dept |  | Rodney | Neece | 1.000000 |  | ATU |  | Gravity | Gravity | Discharge | Chlorination |  |  |  |  | Musty | Clear | 6.800000 | 5.000000 |  | 0.000000 | Tablets are now located in the chambers. | [11 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12/14/2020 | 12:00 AM
02/07/2020 |  | Routine, Scheduled | 227-01-0386 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Western Tidewater | R & K Septic, Inc. |  | Craig | Van Holten |  |  |  |  | Pump |  |  |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] |  |  | 13.7 | 7.350000 | 3.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/07/2020 | Jan 1 1900 8:30AM
11/02/2020 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump | Distribution Box |  | None |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 11/02/2020 | Jan 1 1900 12:05PM
10/22/2020 |  | RoutineScheduled |  | Rockingham | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [7 empty] | 10/22/2020 |  | 21.000000 | [5 empty] | Will be sent separately | Inspected | Recommend pumping of 2 compartment septic tank.We will be placing on schedule and taking care of. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/26/2021 | 09:04 AM
06/29/2020 |  | RoutineScheduled | -STS-20164 | Prince William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Prince William | Wastemaster Inc |  | Timothy | Jenkins | 2.000000 |  | Recirculating Sand Filter |  | Pump | Gravity | Discharge | Chlorination |  | ["SludgeScum Accumulation"] | [] |  | Musty | Clear | 6.300000 |  |  | 2.200000 | [11 empty] | Pump Tank Requires Cleaning. Pump 1 in alarm. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. |  | 06/29/2020 | 06:10 PM
02/13/2020 |  | Routine, Scheduled | 099-17-0056 SPSA | King George County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001350 | Mike | Cook | 1.000000 |  | None | None | Pump | Distribution Box | Aggregate Trench |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/25/2020 | 07:16 AM
03/06/2020 |  | Initial Visit | 099-18-0120 C-SWP | King George County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson |  |  | Orenco Advantex | None | Pump |  |  | UV Light |  | ["Control Operation"] | ["Control Operation"] | [18 empty] | [Comments]: Both zones tested at 3.7 gpm, which is about 25% higher than design. No leaks seen anywhere, and both solenoid valves were shut. Adjusted run and rest times accordingly. Reset counters to zero. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/09/2020 | 04:39 AM
07/20/2020 |  | RoutineScheduled | 171-05-0118 | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | [6 empty] | tank only |  | Gravity | Pressure | Trenches | Not Applicable |  | ["None"] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 07/20/2020 | 12:00 AM
03/04/2020 |  | Routine, Scheduled | 05-120-0124A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesterfield | Chapin, Ben |  | Ben | Chapin |  |  | Septic Tank Only | Septic Tank Only | None | None | None | None | [21 empty] | Lab results not reported by Operator, EHS chose "No" in order to allow saving updated entry. VENIS File Names: 11300 Taylors Landing Way.jpeg | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/16/2020 | Jan 1 1900 3:35PM
12/12/2020 |  | RoutineScheduled | 03-197-A16 | Wise | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Effluent Screens"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
04/02/2020 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump | Drip | Elevated Sand Mound | UV Light |  | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  |  | 7.000000 | 5.000000 | [13 empty] | Replaced UV bulb | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/02/2020 | Jan 1 1900 3:45PM
08/27/2020 | Alternative | Routine/Scheduled | 136-15-0205 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | Delta Environmental Products, UC Series | None | Pump | Distribution Box | Aggregate Trench | None | 450.000000 |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | Musty | Clear | [15 empty] | Annual service conducted. septic tank - normal operating level - effluent screen serviced. Infiltrator EcoPod - aeration in normal operating level - blower unit serviced. Discharge tank - pump, float sensors, controls operating properly. Distribution box intact - all laterals accepting effluent. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 08/28/2020 | 03:15 PM
06/29/2020 |  | RoutineScheduled | SD-05-16 | Orange | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Enviro-Klean Co. | 1942001087 | michael | clark | [9 empty] | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 05:55 AM
06/30/2020 |  | Reportable Incident | 2015-143-0147 | Henrico | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Henrico | Wastemaster Inc |  | Timothy | Jenkins | 2.000000 |  | ATU |  | Pump | Pressure | Drip |  |  | [] | ["Other"] | [18 empty] | In for alarm. FOund water in pump tank junction box. Re made connections and drained water from box. Pump and aerator not running in auto. Found water coming up in yard when pump is on indicative of broken pipe. Owner will repair. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  |  | 12:10 PM
08/31/2020 |  | RoutineScheduled | SP-04-100 | King George | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Ecoflo | none | Pump | Gravity | Pad | Not Applicable |  | ["Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Attached Growth Medium" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens"] | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Attached Growth Medium" ,"Effluent Screens" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | YES | [15 empty] | Will be sent separately | Inspected | Replaced ON/OFF float and added root kill to pod (roots in pod). Proposal mailed to replace broken effluent filter. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
08/27/2020 |  | Follow-Up | 177-14-0050-SWP | Spotsylvania | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Cleaned media/bleached cleaned system. Tanks and distribution box pumped out by others. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
12/04/2020 |  | RoutineScheduled | 2013-143-0103 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Norweco | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 01/04/2021 | 12:00 AM
09/09/2020 |  | RoutineScheduled | 03-183-001 | Russell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. |  | Denny | Deel |  |  | WHITEWATER |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
08/14/2020 |  | RoutineScheduled | 179-13-0051-SP | Stafford | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Recirculation Pump" ,"Attached Growth Medium"] | ["Effluent Screens" ,"Recirculation Pump" ,"Attached Growth Medium"] | YES | [15 empty] | Will be sent separately | Inspected | We recommend pumping the Advantex Recirculation Tank | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/09/2021 | 03:25 PM
09/19/2020 |  | RoutineScheduled | 154-07-0498 | Louisa | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 | Approved | EHD - Blue Ridge | Dominion Septic, Inc | 1942001068 | David | Stewart | 2.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | System in extreme high level, could not inspect tanks with mirror. Could not do draw down on FAST dose tank. Check valves on zone 1 & 4 are bad. Cleanout by road is broken. FAST control panel is bad, post and board is rotten, owner to replace post. Proposal sent: Replace Fast panel, replace check valves in zones 1 & 4 and repair broken clean out cap by driveway. | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
06/11/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | The breaker for the Norweco was tripped. The distribution box has a crack from the top of the plastic to the force main PVC. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/27/2021 | 01:26 PM
11/02/2020 |  | RoutineScheduled | {FIPSCode}-STS-4956 | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | None | Clear | 6.280000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 11/11/2020 | 02:50 PM
12/08/2020 |  | RoutineScheduled | 2051-98-153 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Wastemaster Inc |  | Timothy | Jenkins | 2.000000 |  | Recirculating SandFilter | Effluent Filter | Pump | Gravity | Discharge | Chlorination |  | [] | [] |  | Musty | Clear | 6.500000 |  |  | 2.200000 | [12 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12/16/2020 | 02:05 PM
08/13/2020 |  | RoutineScheduled | SD-99-215 | Fauquier | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Level Sensor Operation" ,"Control Operation"] | ["Level Sensor Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Recommend adding risers to septic tank to facilitate maintenance. Could not locate any lateral end caps. Lines should be flushed and balanced. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
02/17/2020 |  | Follow-Up | 182-02-0553 (LEGACY ALT. SYSTEM) | Rockingham County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Central Shenandoah |  |  |  |  | 1.000000 | 1500 |  | Biomicrobics MicroFAST | Pump | Drip | Drip Tubing | None |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | [18 empty] | [Comments]: Blower air supply repaired cleanout cap repaired | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/22/2020 | 30-12-1899 04:07 PM
06/27/2020 |  | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Lord Fairfax | Aquarobic Services | 1934000142 | Michael | Blake |  |  | none | none | Pump | Gravity | Mound | Not Applicable |  | ["Level Sensor Operation"] | ["Level Sensor Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced all 3 float switches and cleaned up wiring in control panel. Pump and blower motor starters are overrated, recommend replace with proper size for optimum protection. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 07/01/2022 | 10:30 AM
07/29/2020 | Alternative | Routine/Scheduled | 119-STS-106026 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001063 | K.R. Trapper | Davis | 2.000000 | 2000 | Sandfilter, High rate | Sandfilter, High rate | Pump | Manifold | Aggregate Trench | None | 300.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | None | Clear | [5 empty] | 07/29/2020 | Sandfilter Return | 2.000000 |  |  | 3.900000 |  |  |  |  | Follow-up to upgrade repairs and sand filter rehabilitation. New control panel adjusted for recirculation rest/run time. Drawdown and timer settings adjusted for discharge to LPP field. Laboratory samples obtained to determine baseline. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 08/06/2020 | 11:00 AM
06/11/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Norweco Singulair ATU | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/27/2021 | 01:26 PM
11/17/2020 |  | Routine/Scheduled | 228-12-0400 A | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Virginia Beach | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | Serviced system. Checked the pump, panel, & floats (ok). Cleaned the filter in the Clearstream and cleaned the UV light bulb. Changed the diffuser in the Clearstream, changed the filter in the aerator, and changed the mesh screen in the spinfilter. Drainfield is wet - heavy rain - owner is going to re-grade the area. The timer is set to 10 minutes every 2 hours. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 11/17/2020 | Jan 1 1900 12:00PM
08/11/2020 |  |  | {FIPSCode}-STS-6374 | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 2705110225 | Larry | Royston | 2.000000 | 2000 | 1000 | 1000 | Pump | Gravity |  |  |  | ["None"] | ["None"] | YES | [16 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 08/14/2020 | 12:00 AM
03/14/2020 |  | Routine, Scheduled | SD-13-404 | Fauquier County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | Brown, Jason W | 1942001049 | Jason | Brown | 1.000000 | 1000 | Septic Tank Only | Clearstream ATU | Pump | None | Aggregate Trench | None |  |  |  |  | None | Clean | [15 empty] | VENIS File Names: O&M Log 3-14-20.odt | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/16/2020 | 03:31 PM
03/05/2020 |  | Follow-Up |  | Loudoun County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Loudoun | Triple R Construction Co., Inc. | 1934000238 | Charles | Seamon | 1.000000 |  | Biomicrobics MicroFAST | Biomicrobics MicroFAST | Gravity | Distribution Box | [23 empty] | [Comments]: Replaced faulty Blower (VFC-200)Old blower was overheating. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/26/2020 | 04:49 AM
09/15/2020 |  | Routine/Scheduled | 14-120-0106A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. |  |  | Clearstream ATU |  | Pump |  |  |  |  | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 09/15/2020 | Jan 1 1900 12:00PM
06/11/2020 | Alternative | Routine/Scheduled | {FIPSCode}-STS-75253 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | None | None | Pump | Distribution Box | Aggregate Trench | None | 450.000000 |  | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | [17 empty] | Routine service - COSS - pump to gravity absorption field. Both tanks in normal operating level. Distribution box at normal level. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 06/15/2020 | 07:45 AM
06/15/2020 | Alternative | Routine/Scheduled | 136-04-0816 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1500 | Orenco Advantex | None | Pump | Distribution Box | Aggregate Trench | None | 600.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | [17 empty] | Roots entering system around RSV line. Lid for Advantex unit is detached. Roots entering tank around inlet and outlet pipes and riser on the discharge tank. Roots entering distribution box around header lines. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 06/17/2020 | 11:14 AM
11/10/2020 |  | Routine, Scheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Biomicrobics MicroFAST |  |  |  |  | UV Light |  | ["Blower/Compressor/Aerator Operation","Disinfection","Dispersal System Operation"] | ["Blower/Compressor/Aerator Operation","Disinfection","Dispersal System Operation"] |  | Acceptable | Clear | [15 empty] | Replaced filter. Pump Amps 7.12 ETM 156.53 hrs Cycles 170189 Water Meter Reading 331060 Septic Sludge 6" Scum 10" ATU Sludge 15" Scum 0 Pump Sludge 4" Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 11/10/2020 | Jan 1 1900 10:40AM
10/27/2020 |  | RoutineScheduled | SD-02-805 | Fauquier | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Control Operation" ,"Distribution Pump Operation" ,"SludgeScum Accumulation"] | ["Auxiliary Filter" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Atu tank and pump tank need pumping, owner to make arrangements. Spin filter was dirty and starting to crush, replaced it. Lid for headworks has a large hole in it, needs replaced. Atu lid is chipped, needs replaced. Zoner valve is cracked and leaking badly. Could not check drip rates or verify check valve operation. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
06/23/2020 |  | Initial Visit |  | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Soils, Inc. | 1940001392 | Markham | Smith | 1.000000 | 1500 gallon | MicroFAST 0.75 |  | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Dispersal System Operation"] | ["BlowerCompressorAerator Operation","Dispersal System Operation"] | NA | [9 empty] | 7.000000 | [7 empty] | System in excellent condition. Monster box lid was cracked - replaced with new. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 07/28/2020 | Jan 1 1900 8:55AM
07/17/2020 |  | RoutineScheduled |  | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | [9 empty] | ["Dispersal System Operation"] | ["Dispersal System Operation"] | [8 empty] | 07/17/2020 |  | 6.000000 | [7 empty] | Septic/ATU had6" sludge and 2" scum ATU had 4" sludge Cleaned air filter for blower. Found broken tubing in the drip system- Repaired Pumpcnts-1398 ETM-178h 27m Peak cnts-551 ETM-84h 27m No W/M recorded | This AOSS should now return to normal function after having provided the above state routine maintenance. |  |  | 12:00 AM
11/05/2020 |  | RoutineScheduled | 02-197-091 | Wise | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | Wise County Health Dept |  | Rodney | Neece | 1.000000 |  | atu |  | Gravity | Gravity | Discharge | Chlorination |  | ["BlowerCompressorAerator Operation","Disinfection"] |  |  | Septic | Discolored | 6.000000 | 2.000000 |  | 0.000000 | No tablets in chambers on system needs pumped | [11 empty] | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 11/05/2020 | 12:00 AM
06/09/2020 |  | Follow-Up |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | SES MidAtlantic LLC | 1942001203 | James | Green | 1.000000 |  | Delta Environmental Products, DF Series | Delta Environmental Products, DF Series | Pump | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation"] | ["Dispersal System Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Installed new K4000 Zoner head. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/15/2021 | 09:00 AM
05/01/2020 |  | Reportable Incident | SWP-02-498 | Spotsylvania | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Repaired broken check valve on zone 2. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
09/29/2020 |  | Pump-Out Only |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU | [8 empty] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 09/29/2020 | Jan 1 1900 7:30AM
07/06/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/27/2021 | 01:26 PM
10/23/2020 |  | RoutineScheduled | SD-10-38 | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Wastemaster Inc |  | Timothy | Jenkins | 2.000000 |  | ATU |  | Pump | Pressure |  | Chlorination |  | [] | [] |  | Musty | Clear | 6.400000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 11/06/2020 | 10:35 AM
11/20/2020 |  | RoutineScheduled | 099-07-0123-SWT | King George | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  | ["Attached Growth Medium" ,"Effluent Screens"] | ["Effluent Screens" ,"Attached Growth Medium"] | YES | [15 empty] | Will be sent separately | Inspected | We recommend replacing the top riser section & lid on the Pump Tank. The manufacturer would recommend adding peat where it has settled in the Puraflo modules. Based on the age of the system , this may or may not be cost effective. | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 |  | 04/09/2021 | 03:25 PM
06/17/2020 |  | RoutineScheduled | SWP-05-725 | Spotsylvania | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Distribution Pump Operation" ,"Control Operation"] | ["Control Operation" ,"Distribution Pump Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Routine inspection. Found "blue valve" for backwash valve #1 not closing, replaced it and the solenoid base for #1. Piece of flex tubing and small portion of pvc manifold exposed in zone 3 (was not installed with enough cover). Advised owners to add about 3" of topsoil to protect it from damage. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
04/14/2020 |  | Routine/Scheduled | 800-STS-14487 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Western Tidewater | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 9000 | Advanced Septic |  | Pump | Distribution Box | Aggregate Trench |  | 4500.000000 |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Recirculation Pump","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | Musty | Clear |  | 5.600000 |  |  |  | 04/14/2020 | Clarifier Outfall | 29.000000 |  |  | 20.300000 | 50.920000 |  |  |  | Reported alarm - found flow equalization pump #1 & #2 "ragged" from cloth wipes! - Lab report received 04/20/2020. Routine monthly service conducted - lab samples for BOD5, TSS and Total Nitrogen obtained and transported to Universal Laboratories. NOTE - Preliminary / "Informal" review of engineering package for replacement is being conducted. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/15/2020 | Jan 1 1900 8:00AM
07/29/2020 |  | Reportable Incident | SWP-05-374 | Stafford | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  | ["Level Sensor Operation"] | ["Level Sensor Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Intermittant alarms. Replaced failed timer float switch. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
10/21/2020 |  | Follow-Up | 179-15-0032-SP | Stafford | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [9 empty] | 5.000000 | [5 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
03/11/2020 |  | Routine, Scheduled |  | Page County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Lord Fairfax | SEAL, CHARLES K | 1934000144 | CHARLES | SEAL | 1.000000 |  | Septic Tank Only | Biomicrobics MicroFAST | Pump | Manifold | Drip Tubing | None |  | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | [18 empty] | [Comments]: Water level high in FAST. Root intrusion seen and may be the cause. Recommend removing top off of FAST and checking for obstruction | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/16/2020 | 03:15 PM
01/08/2020 |  | Routine, Scheduled | 113-18-074 | Madison County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | JENKINS, TROY C, JR | 1942001050 | TROY | JENKINS | 2.000000 | 1500 | None | None | None | Drip | Aggregate Bed | None | 2613.000000 | ["Control Operation"] | ["Control Operation"] |  |  |  | 7.220000 |  |  |  |  | 01/08/2020 | Effluent | 2.000000 |  |  | 1.300000 | 46.470000 |  | Attached to this report |  | [Pumpout Comments]: Was not pumped in Jan VENIS File Names: Sheetz.pdf | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/14/2020 | 12:17 PM
08/25/2020 |  | Routine/Scheduled | 06-160-0080 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Delta Environmental Products, DF Series |  | Pump | Drip | Drip Tubing | None | 70.000000 | ["None"] | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 08/25/2020 | 02:30 PM
09/16/2020 |  | Follow-Up |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Fixed the drainage in far left pod | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/14/2021 | 04:27 PM
02/17/2020 |  | Routine, Scheduled | 109-05-0054 | Bedford County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Central | WAUGH, IAIN C | 1942001512 | IAIN | WAUGH | 1.000000 | 1500 | Septic Tank Only | Puraflo | Pump | Distribution Box | Aggregate Trench | None |  | ["Attached Growth Medium"] | ["Attached Growth Medium"] | [18 empty] | [Comments]: Septic Tank " No Access" Recently Pumped Pump Tank - Pump Operational, Float switch and alarm Operational. In Puraflo boxes Peat in Goo/Great condition for age. Some root growth, recommend to remove soil around upper side of boxes, also Replacing riser on pump tank and installing 1 over septic tank | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/18/2020 | 01:40 PM
10/20/2020 |  | Follow-Up |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Peat replaced | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/27/2021 | 01:26 PM
07/01/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Concrete lid will need to be replaced in the near future. Lines might need to be flushed and balanced in the future. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/27/2021 | 01:26 PM
07/02/2020 |  | RoutineScheduled | 179-08-0017-SR | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Ace Contracting Services Inc | 1942001120 | Lawrence | Fellenz Jr. | 1.000000 |  | Puraflo | none | Gravity | Gravity |  | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 |  | 06/29/2021 | 10:39 PM
05/11/2020 | Alternative | RoutineScheduled | 166-09-331 | Northumberland | This AOSS is functioning as designed and in accord | Approved | EHD - Three Rivers | [13 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accord |  |  | 12:00 AM
03/03/2020 |  | Routine, Scheduled | {FIPSCode}-STS-26956 | Frederick County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Lord Fairfax | Hott, Joshua D. | 1942001301 | Joshua | Hott | 1.000000 | 1000 | Septic Tank Only | Puraflo | Pump | Distribution Box | Aggregate Trench | None |  | ["None"] | ["None"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/18/2020 | 03:40 PM
04/29/2020 |  | RoutineScheduled | SP-05-335 | King George | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Control Operation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | ["Attached Growth Medium" ,"Control Operation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | YES | [15 empty] | Will be sent separately | Inspected | Pump rate is a little low. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
09/25/2020 |  | Routine/Scheduled | 03-160-0298 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Delta Environmental Products, DF Series |  | Gravity | Distribution Box |  | None |  | ["None"] | ["Blower/Compressor/Aerator Operation","Sludge/Scum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 09/25/2020 | 04:45 PM
05/22/2020 |  | Routine/Scheduled | {FIPSCode}-STS-79879 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1500 | Orenco Advantex | None | Pump | Distribution Box | Aggregate Trench | None |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | [17 empty] | The Floats in the Processing Tank have exceeded life expectancy; the Advantex Treatment Media have exceeded life expectancy and the Lid did not have Support Struts present; the Discharge Pump is aged, and the Floats have exceeded life expectancy; the Control Panel has exceeded life expectancy; | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 06/09/2020 | 12:27 PM
08/03/2020 |  | Initial Visit | 041-STS-258153 | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesterfield | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | EZ Treat Sandfilter | None | Pump | None | Alternative Discharge | UV Light | 600.000000 |  | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | [17 empty] | Installation - Repair - Direct Discharge - VPDES Permit Installed new 1500g processing tank Installed EZ Treat synthetic sand filter Installed UV Disinfection & supplemental aeration Installed Pump Basin and discharge pump Installed 250 feet EZFlow trench to discharge point | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 08/07/2020 | Jan 1 1900 7:00AM
03/05/2020 |  | Routine, Scheduled |  | Prince George County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Crater | Madison Environmental LLC | 1934 000061 | Larry | Madison, Jr. |  |  | Norweco Singulair ATU |  | Pump |  |  |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/05/2020 | Jan 1 1900 11:00AM
06/15/2020 |  | RoutineScheduled | 179-13-0215-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Effluent Screens" ,"Recirculation Pump" ,"Distribution Pump Operation"] | YES | [15 empty] | Will be sent separately | Inspected | Cleaned clogged effluent filter. | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 |  | 04/09/2021 | 03:25 PM
02/11/2020 |  | Routine, Scheduled | 05-142-0517 | Hanover County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chickahominy | TIMBERLAKE, LOUIS RHEA | 1942001339 | LOUIS RHEA | TIMBERLAKE | 1.000000 |  | Puraflo | Septic Tank Only | Pump | None | Elevated Sand Mound | None | 648.000000 | ["Dispersal System Operation","Distribution Pump Operation","Effluent Screens","SludgeScum Accumulation"] | ["Dispersal System Operation","Distribution Pump Operation","Effluent Screens","SludgeScum Accumulation"] | [18 empty] | [Pumpout Comments]: Septic tank pumped in 2019, no pumping needed during 2020 inspection. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/16/2020 | Jan 1 1900 9:32PM
09/01/2020 |  | Routine/Scheduled | S 800-18-0128 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Western Tidewater | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | Biomicrobics MicroFAST | None | Pump | Distribution Box | Aggregate Bed | UV Light | 450.000000 |  | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | Musty | Clear | [15 empty] | Routine service conducted. Primary septic tank at normal operating level - effluent screen serviced. Aeration - normal operating level - blower unit serviced. Discharge Tank - normal operating level - pump, float sensors and controls operating properly. U.V. Disinfection - Bulb and quartz crystal serviced. Distribution box - normal level - no evidence of surfacing | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 09/03/2020 | Jan 1 1900 7:30AM
12/03/2020 |  | Initial Visit | 04-120-0328A | Chesterfield | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Chesterfield | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | PremierTech, EFX |  | Pump | Distribution Box | Aggregate Trench | None | 600.000000 | ["Attached Growth Medium"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | Musty | Clear | [15 empty] | Initial Visit - Homeowner reports installed 20 years ago - NO Maintenance! Primary septic tank - normal level - intact - effluent screen serviced. BioFilter - Fiberglass - structural failed - cannot be repaired - requires replacement - no surfacing or backup to residence reported - not able to remove all components for service due to collapse - Pump Basin - plastic - appears intact - pump, float sensors & controls operating - controls located under Porch! Surge / Distribution Box - concrete - intact - all laterals accepting effluent. System marked as BAD - But does not meet the definition of "Failure" as defined by regulations! | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 12/04/2020 | Jan 1 1900 7:30AM
11/24/2020 |  | RoutineScheduled |  | Augusta | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | NA | [7 empty] | 11/24/2020 |  | 23.000000 | [5 empty] | Will be sent separately | Inspected | Lab Sample Normal Installed new blower and new timer at time of service | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/26/2021 | 09:04 AM
05/19/2020 |  | Follow-Up | SR-02-2001 | Spotsylvania | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Biomicrobics MicroFAST | Biomicrobics MicroFAST | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Resealed all 3 pipe penetrations on drip tanks. Put new spin filter in headworks. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
12/08/2020 |  |  | 05-113-116 | Buchanan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Whitewater | [6 empty] | [] | [] | [17 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12/08/2020 | 12:00 AM
03/02/2020 |  | Routine, Scheduled |  | Loudoun County | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Paid | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 2.000000 |  | Biomicrobics MicroFAST | None | Gravity | Distribution Box | Aggregate Trench | [22 empty] | [Comments]: Septic tank needs pumped out | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 04/12/2020 | 02:21 PM
12/10/2020 |  | RoutineScheduled | 069140112 | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | None | Clear | 6.790000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12/21/2020 | 02:40 PM
05/13/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | SES MidAtlantic LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/15/2021 | 09:00 AM
06/04/2020 | Alternative | Routine/Scheduled | 159-07-229 | Middlesex | This AOSS should now return to normal function after having provided the above state routine maintenance | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1250 | Microfast | None | Pump | Distribution Box | Aggregate Trench | None | 450.000000 | ["Blower/Compressor/Aerator Operation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | Air Pump was found not operational, and was not properly mixing air in the Microfast Unit; the High Level Alarm Float in the Pump Tank was not operational; Homeowner has approved repairs 06/12/2020 - New blower installed - new high level float sensor installed. System restored to proper operating status. | This AOSS should now return to normal function after having provided the above state routine maintenance |  | 06/15/2020 | 10:00 AM
06/05/2020 |  | RoutineScheduled | {FIPSCode}-STS-72814 | Spotsylvania | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Distribution Pump Operation" ,"Level Sensor Operation" ,"Control Operation" ,"Auxiliary Filter"] | ["Level Sensor Operation" ,"Control Operation" ,"Distribution Pump Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | Completed annual inspection/service to serve as property sale inspection. Spin filter was dirty and starting to come apart, replaced it. Discharge redundant off float was stuck on, replaced it. Drip rate and flush rate are approximate as there is no flow meter. Takes about 1.5 minutes to pressurize the tubing. Discharge high level count at 53,795 and override count at 44,198. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
08/27/2020 |  | RoutineScheduled |  | Shenandoah | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity |  | Not Applicable |  | ["Control Operation" ,"BlowerCompressorAerator Operation"] | ["Control Operation" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/26/2021 | 09:04 AM
08/20/2020 |  | RoutineScheduled | 179-STS-87351 | Stafford | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Septic Works LLC | 1942001080 | michael | smith |  |  | Orenco Advantex | none | Gravity | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/25/2021 | 08:10 AM
11/09/2020 |  | RoutineScheduled | 177-17-0017-SP | Spotsylvania | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart |  |  | EZ Treat Sandfilter | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Attached Growth Medium" ,"Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | ["Control Operation" ,"Dispersal System Operation" ,"Attached Growth Medium" ,"Auxiliary Filter" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | YES | [15 empty] | Will be sent separately | Inspected | Ez Treat alarm horn and light burnt out. RSV needs 4" stub. Proposal to be sent to homeowner. Dogs have dug many holes in drain field. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
07/07/2020 |  | RoutineScheduled | 177-STS-87480 | Spotsylvania | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Level Sensor Operation"] | ["Level Sensor Operation"] | NA | [15 empty] | Will be sent separately | Inspected | 90-DAY INSPECTION | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/09/2021 | 03:25 PM
07/26/2020 | Alternative | Reportable Incident | 057-STS-105713 | Essex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 750 | None | None | Gravity | Distribution Box | Aggregate Trench | None | 450.000000 |  | ["Dispersal System Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | [17 empty] | System reported backing up into residence - COSS - Chesapeake Bay Pumpout - pumped 750g from primary septic tank - cleared blockage from Inlet baffle. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 07/27/2020 | 07:45 AM
05/20/2020 | Alternative | Reportable Incident | 133-STS-93715 | Northumberland | This AOSS should now return to normal function after having provided the above state routine maintenance | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | None | None | Gravity | Distribution Box | Aggregate Trench | None | 450.000000 | ["Dispersal System Operation"] | ["Dispersal System Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | [17 empty] | Septic tank pumped to facilitate replacement of inlet/outlet "T"'s, conveyance line, distribution box and header lines. Replaced failed / clogged distribution box with new. Replaced corroded cast iron "T"'s for both inlet and outlet in septic tank. Installed access riser on septic tank. Installed new conveyance line and header lines. Owner is rebuilding residence using existing footprint. No change in building size - 5 Bedroom residence as permitted with deeded restriction of occupancy of eight (8) persons. Onsite system as installed - 1000g concrete septic tank, gravity feeding to new distribution box and seven 60' x 2' laterals are functioning as best can be determined. | This AOSS should now return to normal function after having provided the above state routine maintenance |  | 05/26/2020 | 07:00 AM
05/18/2020 |  | Pump-Out Only |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | POWELLS PLUMBING, INC. | 1942001036 | Kurt | Holthaus | 1.000000 | 1250 | Microfast |  | Gravity | Distribution Box | Aggregate Trench |  |  | ["Sludge/Scum Accumulation"] | ["Sludge/Scum Accumulation"] | N/A | [17 empty] | Pumped Microfast system. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 06/19/2020 | 02:02 PM
09/04/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim |  |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/14/2021 | 04:27 PM
06/04/2020 |  | Routine/Scheduled | 093-16-0216 | Isle Of Wight | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | Serviced system. Checked the pump, panel, & floats (ok). Cleaned the filter in the Clearstream and cleaned the UV light bulb. Changed the diffuser in the Clearstream, changed the filter in the aerator, and changed mesh screen in the spinfilter. Replaced the circuit board for the UV. The aerator is full of ants (should be raised). The septic tank needs pumping. The timer is set to 4 minutes every 2 hours. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 06/04/2020 | Jan 1 1900 12:00PM
04/17/2020 |  | Routine, Scheduled | 08-163-0159 | New Kent County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chickahominy | Braxton, Corey Vance | 1942001039 | Corey | Braxton |  |  | Biomicrobics MicroFAST | None | Pump | Distribution Box | None | None |  |  | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation"] |  | None | 2.4 | 7.100000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/17/2020 | Jan 1 1900 9:33PM
11/13/2020 |  | RoutineScheduled | 07-184-5011 | Scott | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Effluent Screens"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Effluent Screens"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
05/15/2020 |  | RoutineScheduled | SD-06-78 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Soils, Inc. | 1940001392 | Markham | Smith | 2.000000 | 1500 | Peat filter PuroFlo (6pods) |  | Pump | Gravity | Trenches | Not Applicable | 65.600000 | [] | ["Attached Growth Medium","SludgeScum Accumulation","Septic Tank Baffles","Distribution Pump Operation","Control Operation"] | NA | [17 empty] | Floats corroded Septic tank 2in 8in Pump Chamber 2 sludge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 05/11/2020 | 01:35 PM
10/05/2020 |  | RoutineScheduled | 101-06-0296 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark | 2.000000 |  |  |  | Gravity | Pressure | Drip |  |  | [] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 04:35 AM
12/31/2020 |  | Routine/Scheduled | 05-137-00765 | Goochland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chickahominy | Miller's Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | Orenco Advantex |  | Pump | Distribution Box | Aggregate Trench | None | 600.000000 | ["Dispersal System Operation"] | ["Dispersal System Operation"] | N/A | [17 empty] | Replaced cracked distribution box with new concrete distribution box - header lines spliced and speed levels installed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/05/2021 | Jan 1 1900 7:45AM
06/09/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Pods are unable to be inspected due to big bushes. | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 |  | 04/14/2021 | 04:27 PM
12/21/2020 |  | Routine/Scheduled | 18-142-0290 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Old Dominion Onsite, Inc. | 1942001549 | Russell | Revis | [9 empty] | ["Distribution Pump Operation","Level Sensor (Float) Operation"] | ["Distribution Pump Operation","Level Sensor (Float) Operation"] | N/A | [17 empty] | Checked float and pump function, walked drain field, checked distribution box area where recent repair was made. System appears to be operating normally. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12/21/2020 | Jan 1 1900 11:25AM
06/25/2020 |  | Routine/Scheduled | 05-142-0345 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chickahominy | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. |  |  | Orenco Advantex |  | Pump | Distribution Box |  |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump","Sludge/Scum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump","Sludge/Scum Accumulation"] | N/A | [17 empty] | Removed roots from distribution box | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 06/25/2020 | Jan 1 1900 2:00AM
05/01/2020 |  | Routine/Scheduled |  | Southampton | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Whitewater ATU |  | Pump | Distribution Box |  | None |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  |  | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 05/01/2020 | Jan 1 1900 1:00PM
10/30/2020 |  | RoutineScheduled | 05-192-278 | Tazewell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Mound | Not Applicable | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","Effluent Screens"] | ["BlowerCompressorAerator Operation","Effluent Screens","Control Operation"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
04/24/2020 |  | RoutineScheduled | 154-02-0009 | Louisa | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 | Approved | EHD - Blue Ridge | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  | ["Distribution Pump Operation" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["Distribution Pump Operation" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | There are roots in the conveyance line leaving the aerobic treatment unit. We recommend ecavating by hand and repairing or replacing the pipe to remove these roots. The zone check valves are not holiding in the drip dispersal system and should be replaced. We also recommend reattaching the lowest zone piping that has pulled out from the K Rain Valve. | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 |  | 04/09/2021 | 03:25 PM
08/27/2020 |  | RoutineScheduled | 15-137-0168 | Goochland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | GeoEnvironmental Services, Inc. | 1942001010 | Peter | Mamunes | 2.000000 | 1850 | Multiflo |  | Pump | Pressure | Trenches | Not Applicable |  | ["Attached Growth Medium","Control Operation","BlowerCompressorAerator Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["SludgeScum Accumulation","Level Sensor Operation","Distribution Pump Operation","Dispersal System Operation","Control Operation","BlowerCompressorAerator Operation","Attached Growth Medium"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 10/12/2020 | Jan 1 1900 3:00PM
01/17/2020 |  | Routine, Scheduled | 033-07-0111-SP | Caroline County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Ware, Michele P | 1942001165 | Michele | Ware |  |  | Septic Tank Only | Septic Tank Only | None | None | None | None |  |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/20/2020 | 12:08 PM
05/11/2020 |  | Routine, Scheduled | 175-18-0316 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Biomicrobics MicroFAST |  |  |  |  | UV Light |  | ["Blower/Compressor/Aerator Operation","Disinfection"] | ["Blower/Compressor/Aerator Operation","Disinfection"] |  | Good | Good | [15 empty] | Spin filter cleaned. Pump Amps 10.17 ETM 152 h Cycles 1273 Water Meter Reading 90920 Septic Sludge 8" Scum 2" ATU Sludge 14" Scum 0 Pump Sludge 0 Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 05/11/2020 | 01:45 PM
05/13/2020 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 | Pending Payment | EHD - Loudoun | WasteMaster, Inc. | 1942001062 | Tim | Jenkins | 1.000000 |  | Delta Environmental Products, UC Series | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 |  | 06/21/2021 | 10:37 AM
06/26/2020 |  | Routine/Scheduled | 06-160-0005 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Delta Environmental Products, DF Series |  | Pump | Drip | Drip Tubing | None | 213.000000 | ["None"] | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 06/26/2020 | 09:00 AM
09/29/2020 | Alternative |  | 171-05-832 | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | None | Clear | 7.480000 |  |  |  |  | 09/29/2020 |  | 2.000000 |  |  | 1.400000 | [5 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 10/15/2020 | 11:15 AM
08/12/2020 | Alternative | Reportable Incident | 128-15-061 | Essex | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | obsidian onsite services |  | joel | pinnix | [9 empty] | [] | ["BlowerCompressorAerator Operation"] | [18 empty] | Replaced failed compressor and UV bulb. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  |  | 12:00 AM
10/15/2020 |  | RoutineScheduled | C 800-16-0267 | Suffolk | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Western Tidewater | Environmental Services of Virginia | 1942001182 | Steve | Haley | 3.000000 | 450 | 600NC3T |  | Pump | Pressure | Drip | UV |  | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | NA | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 10/15/2020 | Jan 1 1900 4:00PM
05/19/2020 |  | RoutineScheduled | SD-11-258 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Soils, Inc. | 1940001392 | Markham | Smith | 2.000000 | 1500 | PuroFlo (pods) |  | Pump | Gravity | Pad | Not Applicable | 45.000000 | [] | ["SludgeScum Accumulation","Septic Tank Baffles","Level Sensor Operation","Dispersal System Operation","Attached Growth Medium"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 07/16/2020 | 03:30 AM
09/09/2020 | Alternative | Routine/Scheduled | 157-09-0145 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | Serviced system. Checked the pump, panel, & floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. The pressure switch on the aerator is not hooked up. The septic tank needs additional risers on it so it can be properly inspected in the future. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 09/09/2020 | 12:00 PM
12/10/2020 |  | Follow-Up | 09-197-A4 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | Wise County Health Dept |  | Rodney | Neece | 1.000000 |  | ATU |  | Gravity | Gravity | Discharge | Chlorination |  |  |  |  | None | Clear | 6.200000 | 5.000000 |  | 0.000000 | Tablets are located inside the chambers. | [11 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12/10/2020 | 12:00 AM
12/09/2020 |  | RoutineScheduled |  | Augusta | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [7 empty] | 12/09/2020 |  | 16.000000 | [5 empty] | Will be sent separately | Inspected | Lab sample normal Adjusted timer settings to proper settings Replaced valve box lid | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/26/2021 | 09:04 AM
08/26/2020 |  | RoutineScheduled | 01-137-0430 | Goochland | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 | Approved | EHD - Chickahominy | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 2.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation"] | ["Control Operation"] | NA | [7 empty] | 08/26/2020 |  | 231.000000 |  |  | 120.000000 | 48.850000 |  | Will be sent separately | Inspected | Routine inspection and effluent sampling. In spite of recent additions to treatment, effluent continues to enter the drainfields at unacceptable waste strengths. Excessive grease and oil is believed to be the reason. Engineer will be contacted for a possible solution. Informal effluent sampling: D.O. measured .1 mg/L at 32.6* C in pump tank, and only .5 mg/L in recirc tank right next to new aerator. PH tested at 6.20, settleable solids at 5 mg/ 1000 mL. and ntu's at 114.6. Advantex sheets are packed with oily grease. Rinsed off tops to correct bridging. Daily discharge for the past 49 days has averaged 1,162.1 gals/day. | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 |  | 04/13/2021 | Jan 1 1900 11:22AM
12/01/2020 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump | Drip | Elevated Sand Mound | UV Light |  | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  | 3.64 | 7.920000 | 5.000000 |  |  |  | 12/16/2020 |  | 19.000000 |  | 4.000000 | [6 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 12/16/2020 | Jan 1 1900 2:00PM
10/09/2020 |  | Routine, Scheduled | 175-19-0166 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Orenco Advantex |  | Pump | Drip | Drip Tubing | None |  | ["Recirculation Pump"] | ["Recirculation Pump"] |  | Acceptable | Clear | [15 empty] | Spin filter cleaned. Pump Amps 4.56 ETM 145 hrs 9 mins Cycles 26229 Pump Amps 5.14 ETM 96 hrs 46 mins Cycles 626 Water Meter Reading 56500 Septic Sludge 4" Scum 0 Pump Sludge 0 Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 10/09/2020 | 06:15 PM
04/29/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | SES MidAtlantic LLC | 1942001203 | James | Green | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/15/2021 | 09:00 AM
06/05/2020 |  | RoutineScheduled | 69160302 | Frederick | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Lord Fairfax | Onsite Wastewater Services - May Supply | 1942001022 | Sara | Tusing |  |  | none | none | Pump | Gravity |  | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | INSECTION DS | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/28/2021 | 05:41 AM
03/04/2020 |  | Routine, Scheduled |  | Mathews County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Three Rivers | Farmer’s Septic Service, Inc. |  | Ross | Cole | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | [Comments]: Serviced system. Checked the pump, panel, & floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream, changed the filter in the aerator, and changed the mesh screen in the spinfilter. There is about 2’ of sludge in the bottom of the septic tank. The timer is set to 9 minutes every 1 hour. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/04/2020 | 12:00 PM
06/09/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/27/2021 | 01:26 PM
09/18/2020 |  | Routine/Scheduled | 04-160-0573 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Biomicrobics MicroFAST |  | Pump | Drip | Drip Tubing | None |  | ["None"] | ["Blower/Compressor/Aerator Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 09/11/2020 | 11:00 AM
08/26/2020 |  | Pump-Out Only |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | POWELLS PLUMBING, INC. | 1942001036 | Kurt | Holthaus | 1.000000 | 1000 | Puraflo |  | Pump | Distribution Box | Aggregate Trench |  |  | ["Sludge/Scum Accumulation"] | ["Sludge/Scum Accumulation"] | N/A | [17 empty] | Pumped septic. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 10/08/2020 | 03:57 PM
01/14/2020 |  | Routine, Scheduled |  | Prince William County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Puraflo |  |  |  |  | None |  | ["Effluent Screens"] | ["Effluent Screens"] | [18 empty] | [Comments]: Puraflo modules are ponding.Pump Amps 6.70 ETM 53172 Cycles 38034Septic Sludge 10" Scum 0.50Pump Sludge 2" Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/14/2020 | 10:46 AM
03/06/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green |  |  |  |  | Pump | Drip | Drip Tubing | None |  | ["Control Operation","Effluent Screens"] | ["Control Operation","Effluent Screens"] | [18 empty] | [Comments]: Spin filter cleaned.Pump Amps 11.50/12.96Water Meter Reading 136100Septic Sludge 8" Scum 0.25Pump Sludge 1" Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/06/2020 | Jan 1 1900 4:03PM
04/07/2020 |  | Routine, Scheduled |  | Northumberland County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Three Rivers | LANGFORD, CHARLES T | 1934000143 | CHARLES | LANGFORD | 1.000000 |  | Microfast | Septic Tank Only | None | Distribution Box | Gravel-Less Trench | None |  | ["Effluent Screens"] | ["Effluent Screens"] | [18 empty] | [Comments]: Septic tank needs pumping. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/14/2020 | 12:17 PM
07/22/2020 |  |  | 12-113-215 | Buchanan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. |  | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination |  | ["BlowerCompressorAerator Operation","Disinfection","Effluent Screens","Control Operation"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
10/12/2020 |  | RoutineScheduled | 181-04-0249 | Rockbridge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Hunter E. Ayres, General Contractor | 1942001166 | Hunter | Ayres | 1.000000 | 1500 | Biogator 300 |  |  | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","Effluent Screens"] | ["Auxiliary Filter","Effluent Screens"] | YES | [17 empty] | Filters checked and cleaned. Control panels functioning properly. No apparent leaks in system or drain field area. System did not need to be pumped. Lid properly secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 10/26/2020 | 09:00 PM
05/13/2020 |  | Reportable Incident | 550-STS-6406 | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance | Approved | EHD - Chesapeake | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | PremierTech, EFX |  | Pump | Distribution Box | Aggregate Bed | None | 600.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | None | Discolored | [15 empty] | Septic tank pumped on 05/04/2020 Treatment system peat removed 05/07/2020 Failed fiberglass EcoFlo STB-650 treatment system replaced with new Concrete STB-650 - HD Permit # 234-20-128 | This AOSS should now return to normal function after having provided the above state routine maintenance |  | 05/13/2020 | Jan 1 1900 2:00PM
11/25/2020 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Joe Blevins Equipment Rental, Inc | 2705013926 | Joel | Blevins | 1.000000 |  | Microfast |  | Pump | Gravity | Trenches | Not Applicable |  | ["None"] | ["None"] | NA | Musty | Clear | [5 empty] | 11/25/2020 | Sample Chamber | 71.000000 | [5 empty] | Attached to this report |  | The blower is strong and the ditches are dry. Cleaned the air filter/rusty, needs replaced. Lines have be damaged by landscaper, owner will have tank pump and wares replaced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12/23/2020 | Jan 1 1900 10:25AM
09/24/2020 |  | RoutineScheduled | SD-12-336 | Fauquier | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 2.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  | ["Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"SludgeScum Accumulation"] | ["Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Primary septic tank needs pumped out. All screws had been removed from all tank lids. Installed 2 screws per lid so that there was at least a minimum level of security. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
06/03/2020 |  | Routine/Scheduled |  | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [11 empty] | N/A | [7 empty] | 06/03/2020 |  | 5.000000 | [8 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 06/09/2020 | Jan 1 1900 9:30AM
05/01/2020 |  | RoutineScheduled | 107-07-0083 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Onsite Wastewater Services - May Supply | 1942001022 | Sara | Tusing | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 05/28/2021 | 05:41 AM
05/12/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | SES MidAtlantic LLC | 1942001203 | James | Green | 2.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/15/2021 | 09:00 AM
12/01/2020 |  | RoutineScheduled | 182-04-0393 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Hunter E. Ayres, General Contractor | 1942001166 | Hunter | Ayres | 1.000000 | 1000 | Best 1 |  | Pump | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","Effluent Screens"] | ["Auxiliary Filter","Effluent Screens"] | YES | [17 empty] | Filters checked and cleaned. Septic system did not need to be pumped. No apparent leaks in system or drain field area. Control panels functioning properly. Lids were properly secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12/28/2020 | 12:00 AM
12/07/2020 |  | RoutineScheduled | 069-18-0355 | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax |  |  | Michael | Edmonson | 1.000000 | 1500 | Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation","SludgeScum Accumulation","Level Sensor Operation"] | ["Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12/31/2020 | 10:00 AM
11/24/2020 |  | RoutineScheduled | 16-113-061 | Buchanan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Effluent Screens"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
07/27/2020 |  | RoutineScheduled | {FIPSCode}-STS-30595 | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 2705110225 | Larry | Royston | [9 empty] | ["None"] | ["None"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 07/28/2020 | 12:00 AM
08/11/2020 |  | Routine, Scheduled | 175-06-0561 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Puraflo |  |  |  |  | None |  | ["Effluent Screens"] | ["Effluent Screens"] | [18 empty] | Effluent filter handles are broken and cannot be cleaned properly. Puraflo peat modules-Good Pump Amps 12.90 ETM 205.13 hrs Cycles 9500 Septic Sludge 4" Scum 0.25 Pump Sludge 4" Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 08/11/2020 | 03:53 PM
04/27/2020 |  | RoutineScheduled | 196-10-175 | Westmoreland | This AOSS is functioning as designed and in accord | Approved | EHD - Three Rivers | [13 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accord |  |  | 12:00 AM
09/01/2020 |  | Routine/Scheduled | 2013-143-0053 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Henrico | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. |  |  | Bionest |  | Pump |  |  |  |  | ["Attached Growth Medium","Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump","Sludge/Scum Accumulation"] | ["Attached Growth Medium","Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump","Sludge/Scum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 09/01/2020 | 10:00 AM
02/04/2020 |  | Routine, Scheduled | 16-100-0457 | Accomack County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Eastern Shore | DUER, PETE C | 1942001051 | PETE | DUER | 1.000000 | 1000 | Septic Tank Only | Puraflo | Pump | None | None | None |  | ["None"] | ["None"] | [18 empty] | [Comments]: Aoss Inspection | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/07/2020 | 11:30 AM
06/09/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/14/2021 | 04:27 PM
04/23/2020 |  | RoutineScheduled | 179-07-0388-SR | Stafford | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | EcoPod | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"BlowerCompressorAerator Operation"] | ["Effluent Screens" ,"BlowerCompressorAerator Operation"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 |  | 04/09/2021 | 03:25 PM
07/29/2020 |  | Routine/Scheduled | 2005-126-066 | Dinwiddie | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Crater | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | Biomicrobics MicroFAST | None | Gravity | None | Alternative Discharge | Chlorine | 450.000000 |  | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | Musty | Clear | [15 empty] | Annual service conducted Primary septic tank in normal operating level BioMicrobics FAST - in normal operating level - blower unit serviced Direct discharge point clear of debris, signage present. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 07/30/2020 | Jan 1 1900 12:40PM
10/10/2020 |  | RoutineScheduled | SD-98-43 | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Wastemaster Inc |  | Timothy | Jenkins | 2.000000 |  | Recirculating Sandfilter |  | Pump | Gravity | Discharge | Chlorination |  | [] | [] |  | Musty | Clear | 6.900000 |  |  | 2.200000 | [12 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 10/26/2020 | 10:25 AM
12/15/2020 |  | Routine/Scheduled |  | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  |  |  | Elevated Sand Mound | UV Light |  | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  |  | 7.370000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 12/15/2020 | Jan 1 1900 8:00AM
08/27/2020 |  | Routine/Scheduled | 196-11-181 | Westmoreland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 5.000000 | 1300 | Puraflo |  | Pump | Distribution Box | Aggregate Bed |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 08/27/2020 | 05:00 AM
06/29/2020 |  | RoutineScheduled | 177-16-0101-SP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Distribution Pump Operation" ,"Dispersal System Operation" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 |  | 04/09/2021 | 03:25 PM
03/19/2020 |  | Routine, Scheduled | 42375 | Frederick County | This AOSS should now return to normal function after having provided the above stated routine maintenance. | Approved | EHD - Lord Fairfax | Ferguson, Jeremy | 1942001008 | Jeremy | Ferguson | 1.000000 | 1000 | Puraflo | Septic Tank Only | Pump | Manifold | Aggregate Trench | None |  | ["Distribution Pump Operation"] | ["Distribution Pump Operation"] | [18 empty] | [Comments]: Discharge pump was replaced. System is now operational and in compliance with health department regulations | This AOSS should now return to normal function after having provided the above stated routine maintenance. |  | 03/20/2020 | 02:31 PM
02/14/2020 |  | Routine, Scheduled | 069140166 | Frederick County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Lord Fairfax | POWELLS PLUMBING, INC. | 1942001036 | Kurt | Holthaus | 1.000000 | 1500 | Microfast |  | Pump | Drip | Drip Tubing |  | 450.000000 | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | [18 empty] | [Comments]: Annual Inspection - Serviced spin filter and blower. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/14/2020 | 12:58 PM
08/25/2020 |  | Routine/Scheduled | 03-160-0427 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Delta Environmental Products, DF Series |  | Pump | Distribution Box |  | None |  | ["None"] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 08/25/2020 | 02:30 PM
07/02/2020 |  | RoutineScheduled |  | Rockingham | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Dispersal System Operation" ,"SludgeScum Accumulation"] | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Dispersal System Operation" ,"SludgeScum Accumulation"] | NA | [7 empty] | 07/02/2020 |  | 137.000000 | [5 empty] | Will be sent separately | Inspected | Replaced Discharge Pump Pumped all tanks | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance |  | 04/26/2021 | 09:04 AM
10/23/2020 |  | RoutineScheduled |  | Rockingham | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Ecoflo | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/26/2021 | 09:04 AM
11/02/2020 |  | Routine, Scheduled | 175-08-0576 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Puraflo |  |  |  |  | None |  | ["Effluent Screens"] | ["Effluent Screens"] | [18 empty] | Spin filter cleaned. Pump 1 Amps 9.21 ETM 476 hrs Cycles 14990 Pump 2 Amps 8.55 ETM 6215 hrs Cycles 61080 Water Meter Reading 1120330 Septic Sludge 5" Scum 0 Pump Sludge 2"/3" Scum 0/0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 11/02/2020 | 09:31 AM
02/13/2020 |  | Routine, Scheduled | 107-08-0329 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | GRAY, RANDY L | 1942001335 | RANDY | GRAY | 1.000000 |  | Orenco Advantex | Septic Tank Only | None | None | None | None |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation"] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump"] | [18 empty] | [Pumpout Comments]: Tanks were pumped for repair. [Comments]: System took hit from lightning storm. Replaced all componets. all functioning as designed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 03/10/2020 | 09:25 AM
07/17/2020 |  | Routine, Scheduled | 2120-08-153 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Puraflo |  |  |  |  | UV Light |  | ["Effluent Screens"] | ["Effluent Screens"] |  | Good | Clear | 6.400000 | 7.700000 | [13 empty] | Pump Amps 15.13 ETM 208.56 hrs Cycles 14979 Septic Sludge 7" Scum 1" Pump Sludge 3" Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 07/17/2020 | 02:54 PM
10/20/2020 |  | RoutineScheduled | SD-05-187 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Soils, Inc. | 1942001004 | Markham | Smith | 2.000000 | 1500 | PuroFlo |  | Pump | Gravity | Trenches | Not Applicable | 65.400000 | [] | ["Septic Tank Baffles","SludgeScum Accumulation","Control Operation","Attached Growth Medium"] | YES | [16 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 10/23/2020 | 07:35 AM
05/20/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/27/2021 | 01:26 PM
12/06/2020 |  | RoutineScheduled | 139-05-0211 | Greene | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Alternative Systems Inspection Services, LLC | 1942001047 | Wesley | Basore | 1.000000 | 500 | Biomicrobics |  | Pump | Pressure | Drip | Not Applicable | 150.000000 | ["Control Operation","BlowerCompressorAerator Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 06:05 PM
08/26/2020 |  | Routine/Scheduled | 14-172-0307A | Powhatan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesterfield | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 15 | Delta Environmental Products, UC Series | None | Gravity | Distribution Box | Aggregate Trench | UV Light | 450.000000 |  | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | Musty | Clear | [15 empty] | Routine service conducted. Trash tank - normal operating level Aeration Tank - normal operating level - blower unit serviced. U.V. Disinfection - bulb and quartz crystal serviced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 08/28/2020 | Jan 1 1900 2:00PM
06/03/2020 |  | Routine/Scheduled |  | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [11 empty] | N/A | [7 empty] | 06/03/2020 |  | 8.000000 | [8 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 06/09/2020 | Jan 1 1900 9:30AM
12/01/2020 |  | Follow-Up | SD-14-87 | Culpeper | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [7 empty] | 12/01/2020 |  | 7.000000 | [5 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
06/12/2020 | Alternative | Follow-Up | 166-13-148 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers |  |  | joel | pinnix | [9 empty] | [] | [] | [18 empty] | Pump out of ATU and Pump Tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
03/09/2020 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Aquarobic Services | 1934000142 | Michael | Blake |  |  | none | none | Pump | Gravity | Mound | Not Applicable |  | ["Auxiliary Filter" ,"Control Operation" ,"SludgeScum Accumulation"] | ["Auxiliary Filter" ,"Control Operation" ,"SludgeScum Accumulation"] | NA | [15 empty] | Will be sent separately | Inspected | Assisted pumper with cleaning of tank. Pressure washed walls, then all sludge and debris removed. Single point of aeration found to be a broken diffuser; remaining diffusers had become rigid. Replaced all diffusers, leveled and secured new manifold with marine nylon rope. Seven additional shims were required to get manifold level (a critical step in achieving equal distribution of air). Filled tank with enough fresh water to verify aeration and flush discharge piping. Blower contactor chatter observed. Replaced the contactor as well as the motor starter. Replaced the air filter. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 07/01/2022 | 10:30 AM
04/02/2020 |  | Routine, Scheduled |  | Buchanan County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Cumberland Plateau | DEEL, DENNY M | 1942001097 | DENNY | DEEL |  |  | Norweco Singulair ATU | None | Gravity | None | Alternative Discharge | Chlorine | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens"] |  | Musty | Clear | [15 empty] | [Comments]: 5 blue crystals | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/08/2020 | Jan 1 1900 10:59AM
06/24/2020 |  | RoutineScheduled | 175-07-0055 | Prince William | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  | ["Effluent Screens" ,"Attached Growth Medium"] | ["Effluent Screens" ,"Attached Growth Medium"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 |  | 04/09/2021 | 03:25 PM
11/09/2020 |  | RoutineScheduled | SD-00-267 | Orange | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Attached Growth Medium" ,"Dispersal System Operation"] | ["Auxiliary Filter" ,"Attached Growth Medium"] | NA | [15 empty] | Will be sent separately | Inspected | We recommend replacing the control panel for the blower and clearing the trees off of the drainfield. | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 |  | 04/09/2021 | 03:25 PM
06/29/2020 |  | RoutineScheduled |  | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Catoctin Environmental |  | Cameron | Creighton | 2.000000 |  | Microfast |  | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
10/26/2020 |  | Routine/Scheduled | 191-05-0034 | Sussex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Crater | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. |  |  | Ecoflo |  | Pump |  |  |  |  | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 10/26/2020 | Jan 1 1900 12:00PM
03/20/2020 |  | Routine, Scheduled | 04-160-0250 | Montgomery County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1934000259 | Rodney | Rice | 1.000000 |  | Delta Environmental Products, DF Series |  | Pump | Distribution Box | Aggregate Trench | None |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/20/2020 | 01:45 PM
01/15/2020 |  | RoutineScheduled | 07-113-079 | Buchanan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | DEEL, DENNY M | 1942001097 | DENNY | DEEL |  |  | Norweco Singulair ATU | None | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens"] |  | Musty | Clear | [15 empty] | [Comments]: 5 Blue Crystal 10 Bio Max Added | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 02/05/2020 | Jan 1 1900 4:13PM
10/13/2020 |  | RoutineScheduled | 139-05-0708 | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | [6 empty] | PuraFlo |  | Pump | Gravity | Trenches |  |  | ["Attached Growth Medium","Septic Tank Baffles"] | ["Attached Growth Medium","Septic Tank Baffles"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 10/13/2020 | 12:00 AM
07/27/2020 |  | RoutineScheduled | 182-06-0526 | Rockingham | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Central Shenandoah | Onsite Wastewater Services - May Supply | 1942001022 | Sara | Tusing | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity |  | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | inspection by ds | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/28/2021 | 05:41 AM
02/21/2020 |  | Routine, Scheduled | 2001-143-0376 | Henrico County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Henrico | [7 empty] | Septic Tank Only | None | None | None | None | [22 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/11/2020 | 12:41 PM
09/11/2020 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintanence requirements | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Gravity | Gravity |  | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | A septic inspection was done on a main house and a guest house both go to the same drain field. The state requires that all conventional septic tanks must be pumped out EVERY 5 years and filed with the state and county. The main house has a clean out near the house. The pvc sewer line was camera snaked and was clear. The septic tank was pumped out and no visible cracks or leaks were found. The conveyance line was camera snaked and was clear. The 4 port splitter and both concrete d-boxes were dug up they were about 12" under the ground. All 10 header lines need jetted out full of solids. The guest house has a interior control panel. The sewer line was camera snaked and was clear. The septic tank was pumped out and inspected for any cracks or leaks none were seen. There is a riser on the septic tank. The pump tank, pump, floats and force main were inspected. At time of inspection system was not in working condition. | This AOSS is not functioning as designed or in accordance with the performance/maintanence requirements |  | 04/14/2021 | 04:27 PM
08/14/2020 |  | RoutineScheduled |  | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Soils, Inc. | 1940001392 | Markham | Smith | 2.000000 | 2000 | Mirofast 0.625 in a Hanover 1500 top seam tank |  | Pump | Pressure | Drip | Not Applicable |  | [] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Dispersal System Operation","Control Operation","Septic Tank Baffles","SludgeScum Accumulation","Distribution Pump Operation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 08/25/2020 | Jan 1 1900 3:40PM
05/14/2020 | Alternative | Reportable Incident | 136-15-0052 | Gloucester | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | Owner called due to the alarm being on. Serviced system. Checked the pump, panel, & floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. Installed a re-build kit on the aerator. The timer is set to 2 minutes every 2 hours. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 05/14/2020 | 12:00 PM
03/06/2020 |  | Follow-Up |  | Fairfax County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green | [9 empty] | ["Dispersal System Operation"] | ["Dispersal System Operation"] | [18 empty] | [Comments]: Installed new check valves, camlocks,& gate valves. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/06/2020 | Jan 1 1900 2:00PM
01/02/2020 |  | Routine, Scheduled |  | Albemarle County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Blue Ridge | CLARK, MICHAEL J | 1934000023 | MICHAEL | CLARK |  |  | Septic Tank Only | Septic Tank Only | None | None | None | None |  |  | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/14/2020 | 04:00 AM
09/21/2020 |  | RoutineScheduled |  | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 2705051738 | Joshua | Hott | 1.000000 | 1500 | Septic | Puraflo | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | YES | [7 empty] | 09/21/2020 | Pump Chamber | [6 empty] | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
04/29/2020 |  | Routine/Scheduled | 234-12-26 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesapeake | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1250 | Clearstream ATU | None | Pump | Distribution Box | Aggregate Trench | UV Light |  |  | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | The following repairs were completed: - Install riser on outlet of septic tank - Install new riser on aeration tank - Install new risers on inlet and outlet of pump tank - Install new float and complete conduit to panel from aeration tank - Install new air compressor and diffuser - Install new Orenco UV assembly, panel on post - Install water tight junction on pump tank and wiring to panel - Install new floats on float tree in pump tank - Repair air housing vents | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 05/20/2020 | Jan 1 1900 3:09PM
08/05/2020 |  | Routine/Scheduled |  | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Pump | Distribution Box |  | None |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Recirculation Pump","Sludge/Scum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Recirculation Pump","Sludge/Scum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 08/05/2020 | Jan 1 1900 2:00PM
08/27/2020 |  | RoutineScheduled |  | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 2705051738 | Joshua | Hott |  |  | Septic | Puraflo | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
07/17/2020 |  | RoutineScheduled |  | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 2705051738 | Joshua | Hott |  |  | Septic | Puraflo | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
05/04/2020 |  | RoutineScheduled |  | Caroline | This AOSS is functioning as designed and in accord | Pending Payment | EHD - Rappahannock | Drainfield Solutions |  | Michele | Ware | 2.000000 | [8 empty] | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation","Distribution Pump Operation"] | YES | [18 empty] | This AOSS is functioning as designed and in accord |  | 05/12/2020 | 12:00 AM
06/23/2020 |  | RoutineScheduled | 179-14-0207-SP | Stafford | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Attached Growth Medium"] | ["Recirculation Pump" ,"Attached Growth Medium"] | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/09/2021 | 03:25 PM
11/19/2020 |  | RoutineScheduled | E-05-111-0058 | Botetourt | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 4000 | Biomicrobics Fast |  | Pump | Pressure | Drip | Not Applicable |  | [] | [] | NA | [16 empty] | Inspected | Sludge levels-- 6" sludge in Lower Septic tank & Pump tank, floats and pump opperational. Fixed loose alarm wire. Play Ground parking septic Tanks 6-10" sludge, No pumping needed. Up top Hill Blower alarm good filter cleaned. Drip filter clean, pump opperational, alarm was disconnected and we left it diconnected, Up top sludge levels, fast tank 6" fast unit 10" pump tank -trace sludge, Good aeration. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 11/28/2020 | Jan 1 1900 9:30AM
06/29/2020 |  | RoutineScheduled | VAG408368 | Highland | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Central Shenandoah | Onsite Wastewater Services - May Supply | 1942001022 | Sara | Tusing | 1.000000 |  | none | none | Pump | Gravity |  | Chlorination |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | INSPECTION BY DS | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/28/2021 | 05:41 AM
12/15/2020 |  | Routine/Scheduled |  | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump | Drip | Elevated Sand Mound | UV Light |  | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  |  | 8.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 12/15/2020 | Jan 1 1900 8:00AM
03/24/2020 |  | Routine, Scheduled | 06-183-346 | Russell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | DEEL, DENNY M | 1942001097 | DENNY | DEEL |  |  | Norweco Singulair ATU | None | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens"] |  | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 03/30/2020 | Jan 1 1900 5:19PM
12/11/2020 |  | Routine/Scheduled | 15-142-0139 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Old Dominion Onsite, Inc. | 1942001549 | Russell | Revis | [9 empty] | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump"] | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump"] | N/A | [17 empty] | Cleaned manifold, effluent filter, and spin filter. Flushed drip field for 20 min. Inspected UV light, which was replaced in July. Effluent filter was very clogged, such that the water in septic tank was backing up. Discharge tank riser is still leaking after repair and needs more work. Components appear to be working normally. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12/11/2020 | Jan 1 1900 12:05PM
05/15/2020 |  | RoutineScheduled | 171-09-0179 | Pittsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Pittsylvania-Danville | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Ecoflo |  | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | NA | [16 empty] | Inspected | Sludge level-1/2" scum layer on top-3-4" sludge on bottom in Septic tank - Pump tank 6-7" sludge, Peat Moist no ponding, Roots were noted in all 4 quardants of the Ecoflo peat tank and we suggest to move bushes circling around the peat tank to minimze root intrusion into tank, tipping tray operational. Pump runs good. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 05/30/2020 | 09:30 AM
10/22/2020 | Alternative | Routine/Scheduled | 166-05-715 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | PremierTech, EFX |  | Pump | Distribution Box | Aggregate Trench | None | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | Musty | Clear | [15 empty] | Routine Service Primary Septic Tank - normal operating level - effluent screen serviced. Biofilter - Fiberglass - peatmoss in poor condition - raked / turned Pump Basin - plastic - pump, float sensors and controls operating properly Distribution box - plastic - intact - all laterals accepting effluent. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 10/23/2020 | 07:45 AM
06/02/2020 | Alternative | Routine/Scheduled | 150-17-0093 | King William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. |  |  | Biomicrobics MicroFAST |  | Pump |  |  |  |  | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 06/02/2020 | 10:30 AM
08/06/2020 |  | RoutineScheduled | 179-07-0238-SWP | Stafford | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Attached Growth Medium" ,"Control Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Level Sensor Operation"] | ["Attached Growth Medium" ,"Control Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | YES | [15 empty] | Will be sent separately | Inspected | System needs to be pumped out. Proposal emailed. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
07/07/2020 |  | RoutineScheduled | SD-03-11 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  |  |  | Pump | Pressure | Trenches | Not Applicable |  | ["None"] | ["None"] | NO | [17 empty] | Septic tank-6"sludge 3"scum/Pump tank-0"sludge/Puraflo media fluffed and in good condition cc1-123523/ETM-3029.99 Drainfield in good condition. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
04/29/2020 |  | RoutineScheduled | 17-184-102 | Scott | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | Septic Inc |  | Denny | Deel |  |  | Clearstream |  | Gravity |  | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens","Level Sensor Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens","Level Sensor Operation"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
12/22/2020 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump | Drip | Elevated Sand Mound | UV Light |  | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  |  | 7.400000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 12/22/2020 | Jan 1 1900 1:00PM
03/18/2020 |  | Routine, Scheduled | 107-10-0114 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | INBODEN, TERRY J | 1934000088 | TERRY | INBODEN |  | 13000 | Septic Tank Only | Septic Tank Only | None | None | None | None |  | ["None"] | ["None"] |  |  |  | 7.340000 | 5.650000 |  |  |  | 03/18/2020 |  | 8.000000 |  |  | 6.900000 |  |  |  |  | [Comments]: System functioning in accordance with regulations. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 04/14/2020 | 02:22 PM
01/30/2020 |  | Routine, Scheduled |  | Fluvanna County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Blue Ridge | CLARK, MICHAEL J | 1934000023 | MICHAEL | CLARK |  |  | Septic Tank Only | Septic Tank Only | None | None | None | None |  |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/09/2020 | 04:54 AM
09/30/2020 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump | Distribution Box | Aggregate Bed |  |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  | 6.22 | 7.730000 | 8.600000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 09/30/2020 | Jan 1 1900 3:00PM
12/10/2020 |  | Routine, Scheduled | 175-16-0006 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Microfast |  | Gravity |  |  | None |  | ["Blower/Compressor/Aerator Operation"] | ["Blower/Compressor/Aerator Operation"] |  | Acceptable | Clear | [15 empty] | Septic Sludge 12" Scum 9" ATU Sludge 15" Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 12/10/2020 | 02:16 PM
05/15/2020 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Aquarobic Services | 1934000142 | Michael | Blake |  |  | none | none | Pump | Gravity | Mound | Not Applicable |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | Routine inspection. Replaced air filter as maintenance. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 07/01/2022 | 10:30 AM
05/07/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Loudoun Enviromental | 1942001460 | Austin | Kirkpatrick | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NO | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/28/2021 | 10:17 AM
01/21/2020 |  | Routine, Scheduled | 175-05-0071 | Southampton County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Western Tidewater | R & K Septic, Inc. |  | John | Butt, Jr |  |  | Clearstream ATU |  | Pump | Distribution Box |  | None |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] |  |  | 8.06 | 6.860000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/21/2020 | Jan 1 1900 1:00PM
03/10/2020 |  | Routine, Scheduled |  | Albemarle County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Blue Ridge | ARNOLD, ARCHIE G | 1942001291 | ARCHIE | ARNOLD | 1.000000 | 1000 | Aqua Safe ATU | Septic Tank Only | Gravity | Distribution Box | Aggregate Trench | None | 300.000000 | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] |  | slightly Septic | light brown | [15 empty] | [Comments]: 3/10/2020 O&M: Added 6- 2oz of Bio-jet 7 plus to MLSS Fed MLSS, 32 oz. Sludge Away in Clarifier, replaced Air Filter performed typical maintenance. System working as indented. 6" Sludge in septic tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/24/2020 | 10:12 AM
10/05/2020 |  | Routine, Scheduled | 175-99-0361 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Delta Environmental Products, DF Series | Sandfilter, Non-recirculating |  |  |  | Chlorine |  | ["Blower/Compressor/Aerator Operation"] | ["Blower/Compressor/Aerator Operation"] |  | Acceptable | Clear | 7.900000 | 11.700000 | [13 empty] | Pump Amps 9.70 Cycles 2821 Pump Amps 7.04 Cycles 2715 Septic Sludge 4" Scum 0.25 ATU Sludge 2" Scum 4" Pump Sludge 1"/3" Scum 0/0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 10/05/2020 | 09:18 AM
08/12/2020 |  | RoutineScheduled | 175-18-0389 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Prince William | Dominion Septic, Inc | 1942001125 | Tom | Jackson |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | ["Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | NA | [7 empty] | 08/12/2020 | [7 empty] | Will be sent separately | Inspected | Routine inspection. Collected effluent sample for first BOD test. In the past 30 days, system pumped an average of 1 cycle per day for 3.6 minutes. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
12/08/2020 | Alternative | RoutineScheduled | 159-04-365 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Church View Septic Service Inc. | 1942001302 | Charles | Langford | 1.000000 | 1000 | ecoflo |  | Pump | Gravity | Pad | Not Applicable |  | ["Dispersal System Operation"] | [] | [18 empty] | The pete moss has reached its life expectancy and needs replacing in the near future. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12/08/2020 | 12:00 AM
12/07/2020 |  | RoutineScheduled | 109-02-0488 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 2000 | Biomicrobics Micro Fast |  | Pump | Pressure | Drip | Not Applicable |  | [] | [] | NA | [16 empty] | Inspected | Septic Tank 0" scum 12" sludge - Treatment unit, GOOD aeration! Pump Tank -12" fine sludge- Pump operational - Pump alarm operational - Cleaned Spin Filter Switched Drainfield valves.Pump Ct 96383 ETM 563616 - (1176 cycles -148.3 hrs since last inspection) | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12/29/2020 | 09:30 AM
08/14/2020 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Hoot |  | Pump | Drip | Elevated Sand Mound | UV Light |  | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  | 2.29 | 6.840000 | 5.700000 | [13 empty] | Replaced UV bulb | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 08/14/2020 | Jan 1 1900 2:00PM
04/21/2020 |  | Routine, Scheduled |  | Northumberland County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Three Rivers | Thomas W. Beasley Septic Contractor |  | Thomas | Beasley | 1.000000 | 1500 | Clearstream ATU |  | Pump | Drip | Drip Tubing |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [5 empty] | 40.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/21/2020 | 05:00 PM
06/04/2020 |  | Follow-Up |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | air vent was fixed | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/14/2021 | 04:27 PM
07/10/2020 |  | Routine, Scheduled | 175-14-0147 | Prince William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | EcoPod |  |  |  |  | None |  | ["Blower/Compressor/Aerator Operation"] |  |  | Some Odor | Tan | [15 empty] | Needs new compressor. Pump Amps 9.79 ETM 155.87 Cycles 2539 Septic Sludge 7" Scu4" ATU Sludge 12" Scum 0 Pump Sludge 1" Scum 0 | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 07/10/2020 | 09:55 AM
09/29/2020 |  | RoutineScheduled | 099-07-0062-ST | King George | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Attached Growth Medium" ,"Control Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Level Sensor Operation"] | ["Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Attached Growth Medium" ,"Effluent Screens" ,"Level Sensor Operation" ,"Control Operation" ,"Distribution Pump Operation"] | YES | [15 empty] | Will be sent separately | Inspected | Septic tank and pump tank inlet wedge lids contain roots and are leaking. Pump tank pipe is leaking. Proposal to be sent to homeowner. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
09/08/2020 |  | RoutineScheduled | 02-113-265 | Buchanan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. |  | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
08/26/2020 |  | Reportable Incident | 04-142-0384 | Hanover | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chickahominy | All In Septic Services | 1942001442 | Dennis | Mitchell | 2.000000 | 2500 | Advantex AX20 |  | Pump | Pressure | Drip | Not Applicable |  | [] | ["Auxiliary Filter","Attached Growth Medium","Control Operation","Effluent Screens","Recirculation Pump","SludgeScum Accumulation"] | YES | None | Cloudy | [14 empty] | Pumped Out |  | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 08/26/2020 | Jan 1 1900 2:00PM
11/02/2020 |  | Routine/Scheduled |  | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU | Clearstream ATU | Pump | Distribution Box |  | None |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  |  | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 11/02/2020 | Jan 1 1900 11:00AM
09/17/2020 |  | Routine, Scheduled | 175-12-0412 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Biomicrobics MicroFAST |  |  |  |  | None |  | ["Blower/Compressor/Aerator Operation"] | ["Blower/Compressor/Aerator Operation"] |  | Good | Clear | [15 empty] | Spin filter cleaned. Control panel needs to be remounted to house. Pump Amps 9.49 ETM 1117 hrs Cycles 12140 Water Meter Reading 496330 Septic Sludge 5" Scum 4" ATU Sludge 12" Scum 0 Pump Sludge 0 Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 09/17/2020 | 04:40 PM
11/03/2020 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 2705051738 | Joshua | Hott | 1.000000 | 1500 | Septic | puraflo | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [7 empty] | 11/03/2020 | Sample Chamber | [6 empty] | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 11/25/2020 | 12:00 AM
06/26/2020 |  | Follow-Up | 061-18-270 | Fauquier | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Pump tank was out of high level, but septic tank effluent was still at top of inlet tee. Microfast top will need to be removed and the media cleaned. | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
08/10/2020 |  | Follow-Up |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Lord Fairfax | Aquarobic Services | 1934000142 | Michael | Blake |  |  | none | none | Pump | Gravity | Mound | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation" ,"SludgeScum Accumulation" ,"Level Sensor Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Level Sensor Operation" ,"SludgeScum Accumulation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Concrete manway seal on inlet end of tank had failed, serving as a point of groundwater infiltration. Concrete riser removed, concrete tank top cleaned, and fiberglass manway put back in its place. Additional fiberglass manway set between inlet and outlet manways to provide an isolated housing (from tank moisture) for the blower. Loaner blower removed and new blower installed along with enhanced air filtration. Tank pumped out by Powell's Plumbing as first step to correct poor aeration. Tank pressure washed and all sludge and debris removed. Old style manifold with 4 diffusers and air-drops from ceiling were replaced with latest manifold and 6 diffusers. Additional ballast added to prevent manifold from floating. Rubber airline connected. Drip leg (or tailpiece) and sanitary tee added to inlet line. Added enough fresh water back to the tank to verify excellent aeration. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 07/01/2022 | 10:30 AM
08/29/2020 |  | Initial Visit | 107-02-0465 (LEGACY ALT. SYSTEM) | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Randy's Complete Water & Wastewater Services | 1942001335 | Randy | Gray | 1.000000 | 1000 | Pump up |  | Pump |  | Drip | Not Applicable | 100.000000 | ["None"] | ["None"] | NA | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 08/29/2020 | 03:00 PM
11/12/2020 |  | Routine, Scheduled | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | EcoPod |  |  |  |  | UV Light |  | ["Blower/Compressor/Aerator Operation","Disinfection","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation"] |  | Acceptable | Clear | [15 empty] | UV Light bad. ATU needs pumping. Pump Amps 8.96 ETM 104 hrs 16 mins Cycles 4467 Pump Amps 9.27 ETM 104 hrs 3 mins Cycles 4393 Septic Sludge 9" Scum 12" ATU Sludge 18" Scum 4" Pump Sludge 1" Scum 0 | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 11/12/2020 | Jan 1 1900 3:15PM
04/15/2020 |  | Reportable Incident | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance | Approved | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green | [9 empty] | ["None"] | ["None"] | [18 empty] | Replaced cracked concrete casing on pump chamber. | This AOSS should now return to normal function after having provided the above state routine maintenance |  | 04/15/2020 | Jan 1 1900 4:00PM
02/21/2020 |  | Routine, Scheduled |  | Loudoun County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | None | None | Pump | Manifold | [23 empty] | [Comments]: Sale inspection on a LPD alternative septic system. The septic control panel is a interior time dose. There are 3 pvc cleanouts. The sewer line was camera snaked . The septic tank has a plastic riser on the outlet side of the tanks and there is a filter that was cleaned. The manufacture recommends the filter be cleaned every 6 months. The septic tank was pumped out and the tank was inspected for any cracks or leaks none were found. The pump tank, pump, force main and floats were inspected. The drain field was probed and was dry. At time of inspection all components were in working condition. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/02/2020 | 04:43 AM
12/12/2020 |  | RoutineScheduled | 132-04-0218 | Fluvanna | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Alternative Systems Inspection Services, LLC | 1942001047 | Wesley | Basore | 1.000000 | 500 | Norweco 960 |  | Pump | Pressure | Mound | Not Applicable |  | ["Control Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation","Distribution Pump Operation"] | ["Control Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation","Distribution Pump Operation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12/18/2020 | 06:00 PM
06/02/2020 |  | RoutineScheduled | 069-16-0125 | Clarke | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 2705110225 | Larry | Royston | [9 empty] | ["None"] | ["None"] | YES | [16 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 08/15/2020 | 12:00 AM
04/15/2020 | Alternative | Routine/Scheduled | 136-17-0188 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | Serviced system. Checked the pump, panel, & floats (ok). Cleaned the filter and the diffuser in the Clearstream and cleaned the filter in the aerator | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 04/15/2020 | 12:00 PM
07/30/2020 |  | Routine/Scheduled | 19-120-0232R | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. |  |  | Clearstream ATU |  | Pump |  |  |  |  | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 07/30/2020 | Jan 1 1900 10:30AM
07/27/2020 |  | RoutineScheduled | 043170205 | Clarke | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Greenway Engineering | 1942001008 | Jeremy | Ferguson | 1.000000 | 1500 | Microfast | none | Pump | Pressure | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation","SludgeScum Accumulation","Control Operation"] | ["BlowerCompressorAerator Operation","SludgeScum Accumulation","Control Operation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 07/27/2020 | 02:25 PM
05/08/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Some of the lines are showing signs that they might need to be cleared in the near future. They are scheduled to be cleared preemptively in the next month or so. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/27/2021 | 01:26 PM
04/03/2020 |  | Routine, Scheduled |  | Loudoun County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | None | Pump | Distribution Box | Aggregate Trench | [23 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/12/2020 | 02:21 PM
08/07/2020 |  | RoutineScheduled | 14-177-1074 | Pulaski | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - New River | Southwest Soils, Inc. | 1942001494 | Stephen D. | Dalton | 1.000000 |  | Aqua Safe 500 Duo |  | Gravity | Gravity | Trenches | Not Applicable | 450.000000 | [] | ["BlowerCompressorAerator Operation","SludgeScum Accumulation","Control Operation"] |  | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 08/07/2020 | 01:30 PM
05/13/2020 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Eco Virginia | 1942001235 | William | Poindexter | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 |  | 06/03/2021 | 05:53 AM
11/05/2020 |  | RoutineScheduled | 90-184-003 | Scott |  |  | EHD - Lenowisco |  |  | John | Hyder |  |  | Norweco |  | Gravity |  |  | Chlorination | 450.000000 |  |  |  | Septic | Cloudy | 7.000000 | 0.000000 |  |  | chlorine residual 0 | [10 empty] | No laboratory testing done. Low dissolved oxygen level indicates aerator problems. Notified owner to have system checked by a licensed provider. |  |  |  | 12:00 AM
07/24/2020 |  | RoutineScheduled | 2015-143-0180 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | EZ Treat |  | Pump | Gravity | Trenches |  |  | ["Control Operation","Attached Growth Medium","Recirculation Pump","Distribution Pump Operation"] | ["Attached Growth Medium","Distribution Pump Operation","Recirculation Pump"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
07/24/2020 | Alternative | Reportable Incident | 073-STS-104684 | Gloucester | This AOSS should now return to normal function after having provided the above state routine maintenance | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | None | None | Gravity | Distribution Box | Aggregate Trench | None | 450.000000 |  | ["Dispersal System Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | [17 empty] | Pumped septic tank to facilitate repair. Install - Maintenance/Repair Replaced failing distribution box with new 6 port concrete Replaced conveyance line with 4" PVC Spliced new header lines to terracotta clay tile | This AOSS should now return to normal function after having provided the above state routine maintenance |  | 08/07/2020 | 07:30 AM
03/09/2020 |  | Routine, Scheduled |  | Prince William County | This AOSS should now return to normal function after having provided the above stated routine maintenance. | Paid | EHD - Prince William | SEAMON, CHARLIE L | 1942001108 | CHARLIE | SEAMON |  |  | Septic Tank Only | Microfast | Pump | Manifold | Drip Tubing | UV Light |  | ["BlowerCompressorAerator Operation","Disinfection","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection"] | [18 empty] | [Comments]: Performance Inspection: Microfast w/Salcor UV Light to 2 Zone American Drip. Septic-10"sludge 12"scum/Microfast-8"sludge/Pump tank-0"sludge. Recommend pump out and spray of the Septic/ Microfast Tank.Blower air filter cleaned. UV light burned out,needs replacement.Counts:Z1-2029/Z2-2028/Pump-4060 ETM-528h 2m/Peak-4/wm-039343.15 | This AOSS should now return to normal function after having provided the above stated routine maintenance. |  | 04/07/2020 | 11:12 AM
04/06/2020 |  | Routine/Scheduled | 085-STS-32915 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chickahominy | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | [11 empty] | N/A | [17 empty] | At the time of maintenance, the service expert confirmed that all components were functioning properly and the system was operational. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/06/2020 | Jan 1 1900 1:28PM
03/13/2020 |  | Routine, Scheduled | 13-100-0225 | Accomack County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Eastern Shore | DUER, PETE C | 1942001051 | PETE | DUER | 1.000000 | 1000 | Septic Tank Only | Delta Environmental Products, DF Series | Pump | None | None | None |  | ["None"] | ["None"] | [18 empty] | [Comments]: Aoss Inspection | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/20/2020 | 11:01 AM
11/30/2020 |  | RoutineScheduled | {FIPSCode}-STS-12463 | Warren | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Lord Fairfax | Onsite Wastewater Services - May Supply | 1942001627 | Drew | Shull | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | inspection by Ds | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/28/2021 | 05:41 AM
03/18/2020 |  | Routine, Scheduled | SP-05-399 | King George County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001350 | Mike | Cook | 1.000000 |  | Puraflo | None | Pump | Distribution Box | Aggregate Trench |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/01/2020 | 06:33 AM
04/08/2020 |  | RoutineScheduled | 069050653 | Frederick | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Lord Fairfax | Onsite Wastewater Services - May Supply | 1942001022 | Sara | Tusing | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Pressure | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/28/2021 | 05:41 AM
09/14/2020 |  | Routine/Scheduled | 08-163-0100 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chickahominy | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1500 | Orenco Advantex | None | Pump | Manifold | Aggregate Trench | None | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | None | Clear | [15 empty] | Routine Service Processing Tank - normal operating level - RSV, Recirc pump & effluent screen serviced. Treatment Module - media drapes & spray grid serviced. Discharge Tank - pump serviced - float sensors & controls operating properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 09/15/2020 | Jan 1 1900 2:00PM
07/01/2020 |  | Routine/Scheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Loudoun | POWELLS PLUMBING, INC. | 1942001036 | Kurt | Holthaus | 1.000000 | 1500 | Puraflo |  | Pump | Distribution Box | Aggregate Trench |  | 600.000000 | ["Effluent Screens"] | ["Effluent Screens"] | N/A | [17 empty] | Annual Inspection - Serviced effluent screen(s). | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 07/02/2020 | 12:25 PM
12/03/2020 |  | Routine/Scheduled |  | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Pump |  |  | None |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Recirculation Pump","Sludge/Scum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Recirculation Pump","Sludge/Scum Accumulation"] | N/A |  |  | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 12/03/2020 | Jan 1 1900 1:00PM
05/04/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Payment | EHD - Loudoun | Great Falls Septic Service, Inc | 1942001301 | Josh | Hott | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/27/2021 | 11:51 AM
06/23/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/14/2021 | 04:27 PM
08/18/2020 |  | RoutineScheduled | 061-17-493 | Fauquier | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Rappahannock-Rapidan | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Gravity | Trenches |  |  | ["SludgeScum Accumulation","BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [17 empty] | Septic-8"sludge 4"scum/ Microfast-14"sludge (Requires septic/microfast pumped out) Pump tank-0"sludge/blower air filter cleaned/Counts: Pump-531 ETM-58h 8m/Peak-0 (n/a) No breakout or spongy areas on the drainfield. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  |  | 12:00 AM
10/30/2020 |  | Reportable Incident | 15-142-0059 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Old Dominion Onsite, Inc. | 1942001549 | Russell | Revis | [11 empty] | N/A | [17 empty] | High recirc alarm is caused by leaking risers after rain events. Recommend digging up and sealing with bentonite. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 10/30/2020 | Jan 1 1900 3:55PM
03/02/2020 |  | Routine, Scheduled | 2008-143-0134 | Henrico County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Henrico | SHAW, WILLIAM A, JR. | 1934000449 | WILLIAM | SHAW |  |  | Septic Tank Only | Septic Tank Only | None | None | None | None |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/04/2020 | 11:31 AM
08/07/2020 |  | RoutineScheduled | 13-113-102 | Buchanan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
05/07/2020 |  | RoutineScheduled | 179-11-0157-SP | Stafford | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Attached Growth Medium" ,"Control Operation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Level Sensor Operation"] | ["SludgeScum Accumulation" ,"Control Operation" ,"Attached Growth Medium" ,"Effluent Screens" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | YES | [15 empty] | Will be sent separately | Inspected | BOD collected, replaced R.O. float in recirc, pump out of Advantex, pump tank and d-box needed, proposal to be sent to homeowner. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
07/13/2020 |  | RoutineScheduled | SWP-02-143 | King George | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Effluent Screens" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Effluent Screens" ,"Recirculation Pump"] | YES | [15 empty] | Will be sent separately | Inspected | The alarm light & horn are not working and should be replaced. The LB box for the recirculation pump is damaged and should be replaced. | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 |  | 04/09/2021 | 03:25 PM
03/04/2020 |  | Routine, Scheduled | 179-09-0148-SP | Stafford County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001350 | Mike | Cook |  |  | Orenco Advantex | None | Pump | Drip | Drip Tubing |  |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/18/2020 | 06:42 AM
01/27/2020 |  | Routine, Scheduled | 033-14-0090-SR | Caroline County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | EcoPod | None | Pump | Drip | Drip Tubing |  |  | ["Control Operation","Level Sensor Operation"] | ["Level Sensor Operation"] | [18 empty] | [Comments]: Timer float input showing "on" in Siemens processor. Timer float working, problem is with main mother board. Melted insulation on one wire attached to top of contactor and contactor noisy. Will return in a few days to make repairs. Collected effluent sample for 5-year BOD test. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/03/2020 | 05:52 AM
05/27/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/27/2021 | 01:26 PM
07/08/2020 | Alternative | Reportable Incident | 136-16-0005 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | Advanced Septic | None | Pump | Distribution Box | Aggregate Trench | None | 450.000000 |  | ["Dispersal System Operation"] | N/A | [17 empty] | Aquasafe ATU Replaced riser access to correct leakage / fracture Replaced fractured distribution box lid, re-sealed / parged distribution box and re-balanced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 07/09/2020 | 08:00 AM
04/04/2020 |  | Routine, Scheduled | 099-12-0100-SWP | King George County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Biomicrobics MicroFAST | None | Pump | Drip | Drip Tubing |  |  | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [18 empty] | [Comments]: Repaired broken drip line under planted bush and replaced timer float in discharge tank. Media did not appear clogged. Drip rate is higher than design but no wet spots found. Fast tank and pump tank must be pumped out and refilled. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/27/2020 | 04:14 AM
05/20/2020 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump | Drip | Elevated Sand Mound | UV Light |  | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  |  | 6.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 05/20/2020 | Jan 1 1900 12:30PM
02/21/2020 |  | Routine, Scheduled | 069050282 | Frederick County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Lord Fairfax | Ferguson, Jeremy | 1942001008 | Jeremy | Ferguson | 1.000000 | 1250 | Septic Tank Only | None | Pump | Manifold | Aggregate Trench | None |  |  | ["Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | [Comments]: Recommended to have septic tank pumped due to high level of scum. Other than that system is in compliance with approved plans and health department regulations | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/27/2020 | 08:58 AM
10/01/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | On October 1, 2020 the system appears to be functioning as designed. One lateral end valve box settled slightly. Recommend raising valve box to avoid possible damage. In the future it might be neccessary to flush and repressurize the lines. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/27/2021 | 01:26 PM
07/08/2020 |  | Routine/Scheduled | 00-172-0137A | Powhatan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. |  |  | Orenco Advantex |  | Pump |  |  |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump","Sludge/Scum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump","Sludge/Scum Accumulation"] | N/A | [17 empty] | Solids need pumping | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 07/08/2020 | Jan 1 1900 10:00AM
06/26/2020 |  |  | 043-03-283 | Clarke | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 2705110225 | Larry | Royston | [9 empty] | ["None"] | ["None"] | YES | [16 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 08/17/2020 | 12:00 AM
05/27/2020 |  | Follow-Up | VPDES-92-1 | Madison | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Rappahannock-Rapidan | Wastemaster |  | Timothy | Jenkins | 2.000000 |  | ATU |  | Gravity | Gravity | Trenches | Chlorination |  | [] | [] |  | None | [16 empty] | Installed 30 New Filters in Multiflo | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 05/27/2002 | 12:00 AM
01/23/2020 |  | Routine, Scheduled | 061-17-095 | Fauquier County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | Brown, Jason W | 1942001049 | Jason | Brown | 1.000000 | 1500 | Septic Tank Only | Septic Tank Only | Gravity | Distribution Box | Aggregate Trench | None |  |  |  |  | None | [16 empty] | VENIS File Names: O & M Log Jan 2020.odt | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/25/2020 | 02:24 PM
01/03/2020 |  | Routine, Scheduled | 177-17-0202-SP | Spotsylvania County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | None | Pump | Distribution Box | Aggregate Trench |  |  | ["Attached Growth Medium","Recirculation Pump"] | ["Attached Growth Medium","Recirculation Pump"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/04/2020 | 07:46 AM
06/19/2020 |  | RoutineScheduled |  | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  |  |  | Pump | Pressure | Drip | Not Applicable |  | ["SludgeScum Accumulation","Dispersal System Operation"] | ["Dispersal System Operation"] | NA | [17 empty] | Septic-7"sludge 3"scum/Microfast-10"sludge/Pump Tank-2"sludge.Recommend septic/Microfast pumped out in 6 months. Counts: Z1-1679/Z2-1680/Pump-3359 ETM-730h 2m/Peak-44 ETM-43h 14m/Water meter-0292155.95/Cleaned air filter/removed debris from return diaphragm. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
10/16/2020 |  | Follow-Up | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance | Approved | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green | [9 empty] | ["Distribution Pump Operation"] | ["Distribution Pump Operation"] | [18 empty] | Installed Z137 effluent pump. | This AOSS should now return to normal function after having provided the above state routine maintenance |  | 10/16/2020 | Jan 1 1900 4:00PM
11/06/2020 |  | RoutineScheduled | 06-192-226 | Tazewell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Effluent Screens"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
04/07/2020 |  | Routine, Scheduled | 061-16-250 | Fauquier County | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 5.000000 |  | Bio Barrier | Bio Barrier | Pump | Drip | Drip Tubing |  |  | ["Control Operation"] | ["Control Operation"] | [18 empty] | [Comments]: Biweekly inspection. In the past 19 days, an average of 2,972.6 gals/day at 320.9 gals/dose (avg.) was pumped for a total of 56,480 gals. No standing water seen in dripfield. All tanks at normal levels. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 04/27/2020 | 04:14 AM
10/29/2020 | Alternative | Routine/Scheduled | 151-15-0020 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 3.000000 | 3000 | EcoPod |  | Pump | Distribution Box | Aggregate Trench |  |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 10/29/2020 | 03:00 PM
06/04/2020 |  | Routine/Scheduled | 093-17-0078 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | Serviced system. Checked the pump, panel, & floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. The timer is set to 3 minutes every 2 hours. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 06/04/2020 | Jan 1 1900 12:00PM
07/20/2020 |  | Routine/Scheduled | 2017-143-0021 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Old Dominion Onsite, Inc. | 1942001503 | Jason | Hackler | 1.000000 | 1250 | Orenco Advantex |  | Pump | Distribution Box | Gravel-Less Trench | UV Light |  | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump","Sludge/Scum Accumulation"] | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump","Sludge/Scum Accumulation"] | N/A | [17 empty] | Cleaned effluent filter, changed UV bulb, flushed manifold. Changed off time from 15 to 13. Averaged 3.2 overrides per day. System appears to be operating normally. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 07/20/2020 | 12:12 PM
05/15/2020 |  | RoutineScheduled | SD-05-71 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Soils INC. | 1940001392 | Markham | Smith | 2.000000 | 1500 | Peat Filter, Bord ns Mona Puraflo |  | Pump | Gravity | Trenches | Not Applicable | 57.700000 | ["SludgeScum Accumulation","Level Sensor Operation","Distribution Pump Operation","Control Operation"] | [] | YES | Septic | Discolored |  |  |  |  | Pump Chamber 2sum 1 sludge | 05/15/2020 | [8 empty] | Inspected | all units are functioning | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 05/21/2020 | 04:50 AM
05/14/2020 |  | Follow-Up |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | SES MidAtlantic LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Sealed riser on pump tank. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/15/2021 | 09:00 AM
02/17/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Fairfax | Hott, Joshua D. | 1942001301 | Joshua | Hott |  |  | Septic Tank Only | Septic Tank Only | None | None | None | None | [22 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/25/2020 | Jan 1 1900 4:12PM
12/02/2020 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump | Drip | Elevated Sand Mound | UV Light |  | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  | 5.17 | 7.200000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 12/02/2020 | Jan 1 1900 10:00AM
02/26/2020 |  | Routine, Scheduled | MS 62A Lot 11B | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesapeake | R & K Septic, Inc. |  | John | Butt, Jr |  |  | Orenco Advantex |  | Pump | Distribution Box |  | None |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] |  |  | 17.75 | 7.180000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/26/2020 | Jan 1 1900 9:00AM
11/06/2020 |  | RoutineScheduled | 187-19-014 | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Greenway Engineering | 1942001008 | Jeremy | Ferguson | 1.000000 | 1000 | Multi Flo | None | Gravity | Gravity | Trenches | Not Applicable |  | ["Control Operation","Dispersal System Operation"] | ["Control Operation","Dispersal System Operation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 11/06/2020 | 02:00 PM
06/03/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Pad | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Pod #3 lid is cracked | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/14/2021 | 04:27 PM
08/14/2020 |  | Routine, Scheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Puraflo |  |  |  |  | None |  | ["Effluent Screens"] | ["Effluent Screens"] | [18 empty] | Pump 1 Amps 14.55 ETM 109 hrs 33 mins Cycles 13777 Pump 2 Amps 14.77 ETM 105 hrs 03 mins Cycles 10698 Septic Sludge 13" Scum 0 Pump Sludge 2" Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 08/14/2020 | Jan 1 1900 10:37AM
06/18/2020 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump | Drip | Elevated Sand Mound | UV Light |  | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  |  | 7.740000 | 4.400000 | [13 empty] | Replaced UV bulb, aerator and alarm buzzer | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 06/18/2020 | Jan 1 1900 2:00PM
05/21/2020 |  | RoutineScheduled |  | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | [9 empty] | ["Level Sensor Operation"] | ["Level Sensor Operation"] | [18 empty] | Septic/ATU had 10"sludge,6"scum Cleaned air filter for blower. Pump tank had1" sludge. Pump #1-432 ETM#1- 14h 32m Pump#2-412 ETM#2-13h 52m Peak-8 H/L-9 Replaced off level float | This AOSS should now return to normal function after having provided the above state routine maintenance. |  |  | 12:00 AM
06/10/2020 |  | Routine/Scheduled | 03-163-0085 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chickahominy | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1500 | Orenco Advantex |  | Pump | Distribution Box | Aggregate Trench | None | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | Musty | Clear | [15 empty] | Routine scheduled Routine scheduled service - Processing tank pumped as recommended from inspection / service of 2019. All components removed, serviced, refilled with fresh water, and placed back into operation. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 06/12/2020 | Jan 1 1900 8:00AM
11/05/2020 | Alternative | RoutineScheduled | SD-87-183 | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | Musty |  | 6.880000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 11/11/2020 | 02:40 PM
02/13/2020 |  | Routine, Scheduled |  | Loudoun County | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Paid | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | EcoPod | None | Pump | Distribution Box | Aggregate Trench | [22 empty] | [Comments]: All tanks need pumped out | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 03/02/2020 | 04:43 AM
06/05/2020 |  | Routine, Scheduled | 179-14-0367-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | EZ Treat Sandfilter |  |  |  |  | None |  | ["Dispersal System Operation","Effluent Screens"] | ["Dispersal System Operation","Effluent Screens"] |  | Good | Clear | [15 empty] | Pump Amps 11.54 ETM 639.41 Cycles 1533 Pump Amps 5.48 Septic Sludge 8" Scum 6" Pump Sludge 1" Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 06/05/2020 | 12:35 PM
08/08/2020 |  | RoutineScheduled | 175-09-0136 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Wastemaster Inc |  | Timothy | Jenkins | 2.000000 |  | ATU | Spray Irrigation | Pump | Gravity |  | UV |  | [] | [] |  | Musty | Clear | 7.500000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 09/03/2020 | 01:20 PM
11/13/2020 |  | Initial Visit | 179-STS-88017 | Stafford | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Septic Works LLC | 1942001080 | michael | smith | 1.000000 |  | EZ Treat Sandfilter | none | Gravity | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/25/2021 | 08:10 AM
04/06/2020 |  | Routine, Scheduled | 04-172-0018A | Powhatan County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesterfield | Mamunes, Peter S. | 1942001010 | Peter | Mamunes | 2.000000 | 2000 | Ecoflo | Puraflo | Pump | Manifold | None | None | 450.000000 | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | [Comments]: Sludge = .5" Scum = 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/21/2020 | Jan 1 1900 10:51AM
07/27/2020 |  | RoutineScheduled | 101-04-0767 | Albemarle | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Blue Ridge | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Ecoflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation" ,"Level Sensor Operation"] | ["Level Sensor Operation" ,"Distribution Pump Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Increase tether length on the on/off float about 1.5" to reduce wear and tear on pump. Peat has compacted about 10" below center support and had pockets of water that went away with raking. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
01/10/2020 |  | Routine, Scheduled |  | Prince William County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Prince William | Dominion Septic, Inc | 1942001125 | Tom | Jackson |  |  | EZ Treat Sandfilter | None | Pump | Distribution Box | Gravel-Less Trench |  |  | ["Control Operation","Recirculation Pump"] | ["Control Operation","Recirculation Pump"] | [18 empty] | [Comments]: Effluent not as visually clear as expected. Reduced recirc off time from 15 min to 13.5 min. Recommend adding water treatment system in house to reduce pH and level of sulfates. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/15/2020 | 10:52 AM
05/27/2020 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintanence requirements | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Gravity | Gravity |  | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Sale inspection on a conventional gravity septic system. The sewer line is cast iron and was camera snaked and was open. The septic tank was pumped out and inspected. It does have a plastic riser on the inlet side of the tank. The cast iron section of the conveyance line is which is about 10 feet is swelled shut the camera was not able to make it thru. Once we were on the other side of the case iron line we were able to camera snake to the d-box. The d-box was dug up it was about 24" under the ground. It was in good condition. The 7 header lines were camera snaked they were all clear. The drain field was probed and was dry. At time of inspection septic system was not in working condition. | This AOSS is not functioning as designed or in accordance with the performance/maintanence requirements |  | 04/14/2021 | 04:27 PM
08/10/2020 |  | RoutineScheduled |  | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 2705051738 | Joshua | Hott |  |  | Septic | Puraflo | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
10/26/2020 | Alternative | Routine/Scheduled | 151-03-096 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1250 | PremierTech, EFX |  | Gravity | None | Aggregate Bed | None | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | Musty | Clear | [15 empty] | Routine service Primary septic tank - normal operating level - effluent screen serviced. Pump Basin - normal operating level - pump, float sensors & controls operating properly. BioFilter - Peatmoss in good condition - raked / turned | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 10/27/2020 | 08:00 AM
11/03/2020 |  | RoutineScheduled | {FIPSCode}-STS-18050 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Wastemaster Inc |  | Timothy | Jenkins |  |  | ATU |  |  |  | Discharge | Chlorination |  | [] | [] |  | Musty | Clear | 7.400000 |  |  | 1.900000 | [12 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 11/20/2020 | 12:05 PM
01/06/2020 |  | Routine, Scheduled | 234-14-258 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesapeake | R & K Septic, Inc. |  | John | Butt, Jr |  |  | Clearstream ATU |  | Pump | Distribution Box | Aggregate Bed | None |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] |  |  |  | 8.660000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/06/2020 | Jan 1 1900 9:15AM
04/28/2020 |  | RoutineScheduled | 107-16-0126 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Pump | Pressure | Drip | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 06/02/2021 | 12:00 AM
12/09/2020 |  |  | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Joe Blevins Equipment Rental, Inc | 2705013926 | Joel | Blevins | 2.000000 | 1500 | Microfast |  | Pump | Gravity | Trenches | Not Applicable |  | ["None"] | ["None"] | NA | Musty | Cloudy | [15 empty] | 8 inches of sludge in treatment tank. No need to pump the tank. Blower is strong and the ditches are dry. Cleaned the air filter. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12/23/2020 | 12:00 AM
10/01/2020 |  | Routine/Scheduled |  | Frederick | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Review | EHD - Lord Fairfax | POWELLS PLUMBING, INC. | 1942001036 | Kurt | Holthaus | 1.000000 | 1000 | Ecoflo |  | Pump | Drip | Drip Tubing |  | 600.000000 | ["Attached Growth Medium","Control Operation","Effluent Screens"] | ["Effluent Screens"] | N/A | [17 empty] | Annual Inspection -Remove brush from drainfield and riser openings. Two risers need to be replaced. Replace media due to ponding. Serviced spin filter and effluent filter. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. |  | 12/30/2020 | 12:56 PM
10/07/2020 |  | RoutineScheduled | 175-02-0228 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic Tank | Pump Tank for Puraflo | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","Other"] | ["Attached Growth Medium","Other"] | NO | [17 empty] | Septic tank-6"sludge 1"scum/ pump tank-0"sludge/ replaced both interior and exterior alarm buzzers/ all puraflo modules retaining water, drain needs to be unclogged and more gravel added at the drain. Repair was done on 10/15/2020/ No breakout or spongy areas on the drainfield. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  |  | 12:00 AM
01/16/2020 |  | Routine, Scheduled | 179-18-0199-VU | Stafford County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | None | Pump | Distribution Box | Aggregate Trench |  |  | ["Attached Growth Medium","Effluent Screens","Recirculation Pump"] | ["Attached Growth Medium","Effluent Screens","Recirculation Pump"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/04/2020 | 07:46 AM
11/30/2020 |  | Reportable Incident | 147-11-0052 | James City | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Peninsula | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1500 | Norweco Singulair ATU | None | Pump | Drip | Drip Tubing | UV Light | 450.000000 |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | Pungent | Discolored | [15 empty] | Initial visit with this homeowner. - Alarm Call Response Trash Tank - high level Aeration Tank - high level - Aspirator failed - requires replacement. Clarifier - high level - effluent screen serviced. UV - Salcor - Failed - Bulb / headworks not functioning. Pump Tank - High level - pump serviced, float sensors and controls operating Drip Headworks - drip screen clogged 100% - replaced screen - flushed drip field - System pumped itself out of high level condition once drip screen replaced. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 12/01/2020 | Jan 1 1900 8:30AM
01/28/2020 |  | Routine, Scheduled | 15-163-0054 | New Kent County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chickahominy | Mamunes, Peter S. | 1942001010 | Peter | Mamunes | 1.000000 | 1000 | EcoPod | None | Pump | Distribution Box | Aggregate Trench | None | 450.000000 | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","SludgeScum Accumulation"] | [18 empty] | [Comments]: ST sludge = 4" | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/18/2020 | Jan 1 1900 1:13PM
05/13/2020 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Eco Virginia | 1942001235 | William | Poindexter | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"SludgeScum Accumulation"] | ["Effluent Screens" ,"SludgeScum Accumulation"] | YES | [15 empty] | Will be sent separately | Inspected | Cleaned filter Septic tank pumped | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 |  | 06/03/2021 | 05:53 AM
05/26/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/27/2021 | 01:26 PM
06/18/2020 | Alternative | Routine/Scheduled | 151-06-0283 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | PremierTech, EFX |  | Pump | None | Aggregate Bed | None | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | Musty | Clear | [15 empty] | At the time of maintenance, the technician noted that all tanks were found at normal level. When inspecting the peat chamber, he found that the peat raked out and was in good condition. The technician reported that upon completion all components were functioning properly and the system was operational. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 06/19/2020 | 08:00 AM
06/17/2020 |  | RoutineScheduled | 181-09-0163 | Rockbridge | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Central Shenandoah | Onsite Wastewater Services - May Supply | 1942001022 | Sara | Tusing | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | inspection by DS | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/28/2021 | 05:41 AM
03/12/2020 |  | Routine, Scheduled |  | Manassas | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Paid | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Orenco Advantex |  | Pump |  |  | None |  | ["Distribution Pump Operation","Effluent Screens"] | ["Effluent Screens"] |  | Good | Good | [15 empty] | [Comments]: Discharge pump is bad.Pump Amps 11.60/16.20Septic Sludge 14" Scum 1"ATU Sludge 12" Scum 0Pump Sludge 3" Scum 0 | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 03/12/2020 | 02:45 PM
05/13/2020 |  | RoutineScheduled | 179-07-0018-SWP | Stafford | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  | ["Distribution Pump Operation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Control Operation" ,"Attached Growth Medium" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | ["Effluent Screens" ,"Level Sensor Operation" ,"Septic Tank Baffles" ,"Control Operation" ,"Attached Growth Medium" ,"Distribution Pump Operation" ,"SludgeScum Accumulation"] | YES | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
02/25/2020 |  | Routine, Scheduled | 15-142-0177 | Hanover County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chickahominy | SHAW, WILLIAM A, JR. | 1934000449 | WILLIAM | SHAW |  |  | Septic Tank Only | Septic Tank Only | None | None | None | None |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/28/2020 | Jan 1 1900 11:25AM
04/27/2020 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Eco Virginia | 1942001235 | William | Poindexter | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 |  | 06/03/2021 | 05:53 AM
11/20/2020 |  | Routine/Scheduled | 02-163-0038 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chickahominy | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1500 | Orenco Advantex | None | Pump | Drip | Drip Tubing | None | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | None | Clear | [15 empty] | Routine Service Processing Tank - normal operating level - RSV, Recirc Pump & Effluent screen serviced. Treatment Module - Media Drapes & spray grid serviced. Pump Tank - normal operating level - discharge pump serviced - float sensors and controls operating properly. Drip headworks serviced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 11/23/2020 | Jan 1 1900 7:15AM
03/02/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS should now return to normal function after having provided the above stated routine maintenance. | Paid | EHD - Fairfax | SEAMON, CHARLIE L | 1942001108 | CHARLIE | SEAMON |  |  | Septic Tank Only | Microfast | Pump | Distribution Box | Aggregate Trench | None |  | ["BlowerCompressorAerator Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation"] | [10 empty] | 13.000000 | [5 empty] | Attached to this report |  | [Comments]: Performance Inspection And BOD Sample: Microfast to Drainfield. Septic/Microfast Tank requires pump out and sprayed due to paint on the media. Pump tank-0"sludge. Blower air filter cleaned. P1 cnts-24 ETM-0h 26m/ P2 cnts-23 ETM-0h 55m. No breakout or spongy areas at the drainfield but noted 6 trees near the boxes and lines-recommend removal. | This AOSS should now return to normal function after having provided the above stated routine maintenance. |  | 04/01/2020 | Jan 1 1900 9:07AM
02/20/2020 |  | Routine, Scheduled | 171-09-0307 | Pittsylvania County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Pittsylvania-Danville | COLLINS, MELVIN J | 1942001044 | MELVIN | COLLINS | 1.000000 | 1500 | Ecoflo | None | Pump | Distribution Box | Aggregate Bed | None | 450.000000 | ["Auxiliary Filter"] | ["Auxiliary Filter"] | [18 empty] | [Comments]: tipping tray fixed, filter cleaned | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/21/2020 | 07:49 AM
12/10/2020 |  | RoutineScheduled | 07-113-071 | Buchanan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | WHITEWATER |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Effluent Screens"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
07/22/2020 |  | RoutineScheduled | SD-13-176 | Fauquier | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Recommended pump out of septic tank, owner to make arrangements. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
02/03/2020 |  | Routine, Scheduled | 37905 | Clarke | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Lord Fairfax | Hott, Joshua D. | 1942001301 | Joshua | Hott | 1.000000 | 1500 | Septic Tank Only | Puraflo | Pump | Distribution Box | Aggregate Trench | None |  | ["Effluent Screens"] | ["Effluent Screens"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/18/2020 | 03:44 PM
01/06/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Fairfax | BLEVINS, JOEL R, SR | 1934000415 | JOEL | BLEVINS |  |  | Puraflo | Septic Tank Only | None | None | None | None |  | ["None"] | ["None"] | [18 empty] | [Comments]: Peat looks good, there is no settlement and no ponding. The inlet tee is clear. Ditches are dry and cleaned the filter. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/07/2020 | Jan 1 1900 10:58AM
09/14/2020 |  | RoutineScheduled | 177-18-0231-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Recirculation Pump" ,"Attached Growth Medium"] | ["Effluent Screens" ,"Recirculation Pump" ,"Attached Growth Medium"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 |  | 04/09/2021 | 03:25 PM
10/27/2020 |  | RoutineScheduled | 061-STS-21344 | Fauquier | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | ["Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | NA | [7 empty] | 10/27/2020 | [7 empty] | Will be sent separately | Inspected | First inspection and first BOD sample collected. Notes written in panel shows either AOSE or design engineer opted to set up pump cycles for 360 gals average daily flow, no peak setting. Dripfield is overgrown with very tall weeds. Needs cut and then reseeded. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
01/21/2020 |  | RoutineScheduled | 03-125-095 | Dickenson | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Dispersal System Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Disinfection","Dispersal System Operation","Control Operation"] | YES | Musty | Clear | [15 empty] | 5 Chlorine 7 Dechlorine | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 01/21/2020 | 12:00 AM
08/01/2020 |  | RoutineScheduled | 171-16-0002 | Pittsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Pittsylvania-Danville | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1000 | Advantex |  | Gravity | Gravity | Trenches |  |  | ["None"] | ["None"] | [18 empty] | 8" of solids in septic tank. Flushed treatment unit manifold. Cleaned septic tank filter. Tested floats, pump and alarm. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 10/13/2020 | 07:00 PM
05/07/2020 |  | Follow-Up | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance | Approved | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green | [9 empty] | ["Dispersal System Operation"] | ["Dispersal System Operation"] | [18 empty] | Installed new water meter. | This AOSS should now return to normal function after having provided the above state routine maintenance |  | 05/07/2020 | Jan 1 1900 4:00PM
04/23/2020 | Alternative | RoutineScheduled | 150-06-339 | King William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | GeoEnvironmental Services, Inc | 1942001010 | Peter | Mamunes | 1.000000 | 1250 | Microfast |  | Pump | Pressure | Trenches | Not Applicable | 450.000000 | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["SludgeScum Accumulation","Level Sensor Operation","Distribution Pump Operation","Dispersal System Operation","Control Operation","BlowerCompressorAerator Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 06/22/2020 | 03:00 PM
10/07/2020 |  | RoutineScheduled | 12-152-A1 | Lee | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Effluent Screens"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
03/12/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Puraflo |  | Pump |  |  | None |  | ["Effluent Screens"] | ["Effluent Screens"] |  | Good | [16 empty] | [Comments]: Pump 1 Amps 17.12 ETM 52922h Cycles 11344Pump 2 Amps 12.72 ETM 52694h Cycles 11302Septic Sludge 6" Scum 1"Pump Sludge 2" Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/12/2020 | Jan 1 1900 1:15PM
07/22/2020 |  | RoutineScheduled | -STS-92277 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Wastemaster Inc |  | Timothy | Jenkins | 2.000000 |  | ATU |  | Pump | Gravity | Discharge | UV |  | ["SludgeScum Accumulation"] | [] |  | Musty | Clear | 7.600000 |  | 24.000000 | [12 empty] | Recommend pumping of system | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 07/22/2020 | 03:50 PM
10/15/2020 |  | Routine/Scheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | POWELLS PLUMBING, INC. | 1942001036 | Kurt | Holthaus | 1.000000 | 1250 | Sandfilter, Recirculating |  | Pump | Distribution Box | Aggregate Trench |  | 450.000000 | ["None"] | ["None"] | N/A | [17 empty] | Annual Inspection - No repairs or service needed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 10/16/2020 | 10:58 PM
05/15/2020 |  | Routine/Scheduled | -STS-43171 | Roanoke | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Alleghany-Roanoke | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Puraflo |  | Gravity | Distribution Box |  | None |  |  | ["Control Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 05/15/2020 | Jan 1 1900 10:30AM
06/24/2020 |  | Routine/Scheduled | 2001-143-0062 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Henrico | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | Clearstream |  | Gravity | None | Alternative Discharge | Chlorine | 450.000000 |  | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Effluent Screens","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | Musty | Clear | [15 empty] | Routine service conducted. Septic tank in normal operating level - effluent screen serviced. ATU in normal operating level - aeration compressor serviced. Gravity discharge through tablet chlorinator and tablet de-chlorinator - owner maintains / replenishes tablets. Discharge point clear | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 06/25/2020 | 03:00 PM
11/16/2020 |  | Initial Visit | 124-STS-2379 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Central Shenandoah | [6 empty] | Advantex |  | Pump | Pressure | Drip |  |  | ["Attached Growth Medium","Auxiliary Filter","Septic Tank Baffles"] | ["Attached Growth Medium","Auxiliary Filter","Septic Tank Baffles"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 11/16/2020 | 12:00 AM
09/23/2020 |  | RoutineScheduled | 182-08-0092 | Rockingham | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Central Shenandoah | Onsite Wastewater Services - May Supply | 1942001022 | Sara | Tusing | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Pressure | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Inspection DKS Homeowner replaced timer and timer panel and float. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/28/2021 | 05:41 AM
05/12/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | A bod/tss sample was taken and sent to the lab waiting for results | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/14/2021 | 04:27 PM
08/05/2020 |  | RoutineScheduled | 069090160 | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Combs Wastewater Management LLC | 1942001353 | Amy | Combs | 2.000000 | 1500 |  |  | Pump | Gravity | Trenches | Not Applicable | 300.000000 | [] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12/28/2020 | 12:00 AM
03/11/2020 |  | Routine, Scheduled |  | Louisa County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Blue Ridge | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | None | Pump | Distribution Box | Aggregate Trench |  |  | ["Attached Growth Medium","None","Recirculation Pump"] | ["Attached Growth Medium","None","Recirculation Pump"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/06/2020 | 02:45 PM
08/28/2020 |  | Follow-Up |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Distribution boxes were covered - by others. Riser was repaired - by others. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/27/2021 | 01:26 PM
12/22/2020 |  | Routine/Scheduled | 175-07-0357 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Delta Environmental Products, DF Series |  |  |  |  | Not Applicable |  | ["Blower/Compressor/Aerator Operation"] | ["Blower/Compressor/Aerator Operation"] | N/A | None | Clear | [15 empty] | Septic Sludge 6" Scum 4" ATU Sludge 6" Scum 2" Pump Sludge 0 Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 12/22/2020 | 04:00 PM
09/08/2020 |  | RoutineScheduled | 061-17-326 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
01/28/2020 |  | Routine, Scheduled | {FIPSCode}-STS-24899 | Shenandoah | This AOSS should now return to normal function after having provided the above stated routine maintenance. | Approved | EHD - Lord Fairfax | SEAL, CHARLES K | 1934000144 | CHARLES | SEAL | 1.000000 |  |  | Puraflo | Pump | Distribution Box | Aggregate Trench | None |  | ["Attached Growth Medium","Septic Tank Baffles"] | ["Attached Growth Medium","Septic Tank Baffles"] | [18 empty] | [Comments]: Last pod repaired | This AOSS should now return to normal function after having provided the above stated routine maintenance. |  | 03/11/2020 | 03:39 PM
10/01/2020 | Alternative | Routine/Scheduled | 159-06-0368 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1500 | Orenco Advantex |  | Pump | Distribution Box | Aggregate Trench | None | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | None | Clear | [15 empty] | Routine Service Processing Tank - normal operating level - RSV, recirc pump, Effluent screen serviced. Treatment Module - media drapes & spray grid serviced. Pump Tank - low level - timer enable float sensor / redundant OFF float sensor requires replacement - controls operate properly. SurgeBox/DBox - normal operating level - minor root intrusion removed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 10/09/2020 | 08:00 AM
11/23/2020 | Alternative | Routine/Scheduled | 136-00-072 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | Clearstream | None | Pump | Distribution Box | Aggregate Trench | None | 450.000000 |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | Musty | Clear | [15 empty] | Routine Service Primary Septic Tank - normal level - effluent screen serviced. Aeration Tank - normal level - compressor serviced. Pump Tank - normal level - pump, float sensors & controls operating. Distribution box - concrete - intact - all laterals accepting effluent. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 11/24/2020 | 08:00 AM
06/17/2020 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintanence requirements | Pending Review | EHD - Loudoun | Eco Virginia | 1942001235 | William | Poindexter | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected | Peat is ponding | This AOSS is not functioning as designed or in accordance with the performance/maintanence requirements |  | 06/03/2021 | 05:53 AM
09/18/2020 |  | RoutineScheduled |  | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | McKim Construction | 1942001330 | Michelle | McKim | 2.000000 |  |  |  | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 11/13/2020 | 12:00 AM
04/29/2020 |  | RoutineScheduled | 07-184-5011 | Scott | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | Septic Inc |  | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
12/18/2020 |  | RoutineScheduled | 175-03-0245 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Prince William | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Control Operation" ,"Attached Growth Medium" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Level Sensor Operation"] | ["Attached Growth Medium" ,"Control Operation" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Recirculation Pump"] | YES | [15 empty] | Will be sent separately | Inspected | Advantex 2 compartment tank requires a pump out and refilled to proper water level. (Pumper will need to pull apart unit or use a 2 hose on the recirc side.) Heavy worms in pod, we treated. Pump tank; bottom concrete riser joint has a heavy stain. Low water use. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
03/25/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Fairfax | MCKIM, STEPHEN E | 1934000043 | STEPHEN | MCKIM |  |  | Septic Tank Only | Septic Tank Only | None | None | None | None | [21 empty] | [Comments]: Installed 1 splitter box and 2 d-boxes. Installed new A300 filter in the septic tank. Fairfax Health inspected and passed the install. The area was backfilled, seeded and strawed. At this time the septic system is in working condition | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/27/2020 | Jan 1 1900 3:00PM
11/20/2020 |  | RoutineScheduled | SD-08-219 | Fauquier | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Attached Growth Medium" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Level Sensor Operation"] | ["Distribution Pump Operation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Attached Growth Medium" ,"Control Operation"] | YES | [15 empty] | Will be sent separately | Inspected | Few roots on septic tank wedge lid; no alarms from rain. Cleaned out sample box. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
05/29/2020 |  | RoutineScheduled |  | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 2705051738 | Joshua | Hott | 1.000000 | 2000 | Septic | Puraflo | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
05/15/2020 |  | Reportable Incident |  | Fairfax | This AOSS is not functioning as designed or in acc | Approved | EHD - Fairfax | Soils, Inc | 1940001392 | Markham | Smith | 1.000000 | 1500 |  |  | Pump | Pressure | Drip | UV |  | [] | [] | [18 empty] | This system has experienced numerous issues since start-up on 11/9/2019 including 17 alarms and 25 peak overrides. The homeowner acknowledged that the O&M Operator was not notified of any of the alarm events. There have been 3 instances of sewage backing up into the house. There has been an excessive amount of water entering the tanks from the house as well as inflow to the tanks during rain events. It appears this activity has hydrologically overloaded the drip field, damaging it beyond repair. It also appears the homeowner cleared the reserve field incorrectly. Soils Inc. viewed the site before and after the clearing was completed. Soils Inc. interviewed the homeowner and learned that heavy equipment was used to clear the reserve and that the stumps were ground improperly. Therefore, we believe the reserve is unusable. | This AOSS is not functioning as designed or in acc |  | 05/15/2020 | 12:00 AM
10/01/2020 | Alternative | Routine/Scheduled | 073-STS-99978 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | None | None | Gravity | Distribution Box | Aggregate Trench | None | 450.000000 |  | ["Dispersal System Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | [17 empty] | Pumpout for real estate inspection Real Estate Inspection - COSS Primary Septic Tank - normal operating level - no access riser present - lid depth buried at 16". Distribution Box intact - 4 laterals present - all laterals accepting effluent. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 10/09/2020 | 08:00 AM
07/29/2020 |  | RoutineScheduled | 061-18-175 | Fauquier | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Clearstream | none | Gravity | Gravity | Trenches | Not Applicable |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | Effluent is not as clear as expected. Suspect low pH in well water is limiting treatment. Advised owners to have professional water analysis done. Cleaned air filter. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
04/21/2020 |  | Routine, Scheduled |  | Northumberland County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Three Rivers | Thomas W. Beasley Septic Contractor |  | Thomas | Beasley | 2.000000 | 2500 | Microfast |  | Pump | Distribution Box | Aggregate Trench |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [5 empty] | 60.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/21/2020 | 05:00 PM
10/02/2020 |  | RoutineScheduled | SWP-04-326 | Spotsylvania | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Attached Growth Medium"] | ["Attached Growth Medium" ,"Recirculation Pump"] | NA | [15 empty] | Will be sent separately | Inspected | The riser lid on the Septic Tank does not have the correct lid. We recommend repairing the broken riser & installing an Orenco riser & lid. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/09/2021 | 03:25 PM
09/01/2020 |  | RoutineScheduled | N/A | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Wastemaster Inc |  | Timothy | Jenkins | 2.000000 |  | ATU |  | Pump | Gravity | Discharge | Chlorination |  | [] | [] |  | Musty | Clear | 7.300000 |  | 35.000000 | 1.900000 | [12 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 09/10/2020 | 03:40 PM
03/11/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Fairfax | Aquarobic Services | 1934000142 | Michael | Blake |  |  | None | None | Pump |  |  |  |  | ["Auxiliary Filter","Dispersal System Operation","Distribution Pump Operation"] | ["Auxiliary Filter","Dispersal System Operation","Distribution Pump Operation"] |  | YES | YES | [15 empty] | [Comments]: Cleaned air pre-filter. Filterbed vent pipes broken at hubs, presumably from deer. Pump discharge piping broken causing effluent to surface on side of filterbed. Repaired filterbed piping and transitioned to sch 40 for vents. Discharge re-routed to reduce exposure to cold and foot traffic. Ran pump 10 minutes to verify repair. Evidence of groundwater infiltration at concrete riser joints. Surfaces power brushed clean and dried. Cement glue applied and hydraulic cement used to seal all joints. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/31/2020 | Jan 1 1900 7:24AM
05/12/2020 |  |  | 03-125-300 | Dickenson | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 05/12/2020 |  | 11.200000 |  |  | 1.100000 |  |  | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 05/12/2020 | 12:00 AM
04/22/2020 |  | Routine, Scheduled |  | Petersburg | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Crater | Madison Environmental LLC | 1934 000061 | Larry | Madison, Jr. |  |  | Clearstream ATU |  | Pump |  |  |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/22/2020 | Jan 1 1900 2:30AM
12/09/2020 |  | RoutineScheduled |  | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Auxiliary Filter" ,"Control Operation"] | ["Auxiliary Filter" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 |  | 04/26/2021 | 09:04 AM
12/11/2020 |  | Routine/Scheduled | 161-STS-43037 | Roanoke | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Rejected | EHD - Alleghany-Roanoke | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Orenco Advantex |  | Pump | Drip | Drip Tubing | None |  | ["Dispersal System Operation"] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | [18 empty] | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 12/11/2020 | Jan 1 1900 3:00PM
11/13/2020 |  | RoutineScheduled | 124-STS-2379 | Hanover | This AOSS should now return to normal function after having provided the above state routine maintenance. | Rejected | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Elgin | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | YES | [17 empty] | We replaced the alarm float on 11/13/20 as well | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 01/04/2021 | 12:00 AM
04/20/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | SES MidAtlantic LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Effluent Screens"] | ["Auxiliary Filter" ,"Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/15/2021 | 09:00 AM
02/20/2020 |  | Routine, Scheduled |  | Loudoun County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Loudoun | POWELLS PLUMBING, INC. | 1942001036 | Kurt | Holthaus | 1.000000 | 1250 |  |  | Pump | Manifold | Aggregate Trench |  | 600.000000 | ["Effluent Screens"] | ["Effluent Screens"] | [18 empty] | [Comments]: Annual Inspection - Serviced effluent screen(s). | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/20/2020 | 09:56 AM
11/02/2020 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump | Drip | Elevated Sand Mound | UV Light |  | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  | 10.73 | 6.780000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 11/02/2020 | Jan 1 1900 8:30AM
09/23/2020 |  |  |  | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/Microfast | Pump | Pump | Pressure | Trenches |  |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [17 empty] | Septic-10"sludge 6"scum/Microfast-8"sludge /Pump Tank-0"sludge/ Blower air filter cleaned. Counts: Pump 1-224 ETM-10h 56m/ Pump 2-204 ETM-9h 58m/ Peak-8/High-7/ Recommend grass on the drainfield be mowed. System does not require a pump out. System working as designed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
12/05/2020 |  | RoutineScheduled | # 139-12-002 | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | dovel enterprises |  | jerry | dovel | 1.000000 | 1000 |  |  | Pump | Pressure |  | Not Applicable |  | [] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12/03/2020 | 12:00 AM
11/21/2020 |  | Routine/Scheduled | 196-14-060 | Westmoreland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 2.000000 | [8 empty] | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 11/20/2020 | 05:00 PM
05/13/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Upon arrival, the blower was turned off and alarming. It was turned back on and functioned as designed. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/27/2021 | 01:26 PM
12/15/2020 |  | Reportable Incident |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES MidAtlantic LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Repaired broken control wiring. | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 |  | 04/15/2021 | 09:00 AM
12/08/2020 | Alternative | RoutineScheduled | 115-14-0300 | Campbell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Septic Tank | Advantex AX20 | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Distribution Pump Operation","Effluent Screens"] | NA | Musty | [15 empty] | Inspected | Sludge level-5" Sludge in Septic tank. 4" Sludge in Recirc tank, Clear Effluent on top. Add more mulch to cover the system(will help frost protection). Pump functional tested 12-11.8 on run Amps, alarm functional, Cleaned Biofilter, Brushed Manifold, Cleaned RSV, and Flushed system. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12/28/2020 | 05:30 PM
06/18/2020 |  | RoutineScheduled | 175-05-0108 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Prince William | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation"] | ["Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | On site for annual inspection. System in high level. Replaced bulb in atu panel. Atu had a pretty thick blanket of sludge, broken up with shovel. Tank may need pumped next year. Treated effluent in pump tank looked much better than prior to atu repair. Used fiber optic camera to verify small, steady stream of water coming from the house. Owner dye tested toilets and found one to be problematic. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
01/29/2020 |  | Routine, Scheduled |  | Mathews County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Three Rivers | MEAGHER, WILLIAM J | 1942001190 | WILLIAM | MEAGHER | 1.000000 | 1000 | Septic Tank Only | Ecoflo | Pump | Distribution Box | Aggregate Bed | None | [22 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/05/2020 | 10:10 AM
10/15/2020 |  | Routine/Scheduled | 2019-143-0070 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Henrico | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. |  |  | Clearstream ATU |  | Pump |  |  |  |  | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | Grab Bod sample | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 10/15/2020 | 10:00 AM
04/09/2020 |  | Routine, Scheduled | 159-17-0021 | Middlesex County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers | LANGFORD, CHARLES T | 1934000143 | CHARLES | LANGFORD | 1.000000 | 1000 | Aqua Safe ATU | Septic Tank Only | Pump | None | None | None |  | ["Control Operation","Effluent Screens"] | ["Control Operation","Effluent Screens"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/14/2020 | 04:27 PM
07/15/2020 |  | Reportable Incident | 124-STS-2379 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Chickahominy | Old Dominion Onsite, Inc. | 1942001549 | Russell | Revis | [9 empty] | ["Blower/Compressor/Aerator Operation","Dispersal System Operation","Level Sensor (Float) Operation"] | ["Blower/Compressor/Aerator Operation","Dispersal System Operation","Level Sensor (Float) Operation"] | N/A | [17 empty] | Received call for aerator alarm. Aerator was working but alarming due to high level. Breaker for main control panel had been cut off for unrelated repair and was not turned back on. Upon turning the breaker on, system returned to normal function. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 07/15/2020 | Jan 1 1900 12:00PM
11/20/2020 | Alternative | Initial Visit | 166-06-346 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001063 | K.R. Trapper | Davis | 2.000000 | 2000 | Biomicrobics MicroFAST | None | Pump | Drip | Drip Tubing | None | 450.000000 |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | Musty | Clear | [15 empty] | Initial Visit Primary Septic Tank - Cottage - normal operating level Pump Basin - Cottage - normal operating level - pump, float sensor and controls operating properly. Primary Septic Tank - Main Residence - normal operating level. Aeration Tank - normal operating level - compressor serviced. Pump Tank - normal operating level - pump serviced - float sensors and controls operating properly. Automatic Headworks - solenoids operating - drip screen serviced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 11/23/2020 | 08:45 AM
07/31/2020 |  | Routine/Scheduled | 04-142-0160 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chickahominy | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1500 | Orenco Advantex | None | Pump | Distribution Box | Aggregate Trench | None | 600.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | None | Clear | [15 empty] | Routine service conducted. Processing tank - at normal operating level - RSV, Effluent Screen and Recirculation pump serviced. Advantex module - media drapes and spray grid serviced. Pump Tank - at normal operating level - discharge pump serviced. Float sensors and controls operating properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 08/06/2020 | Jan 1 1900 8:30AM
06/05/2020 |  | RoutineScheduled | 99-142-0285 | Hanover | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Rejected | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Puraflo | [6 empty] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [18 empty] | Peat moss needs to be changed. There were large amounts of grease in the main line that our tech removed. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. |  | 09/17/2020 | 12:00 AM
06/30/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 2.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/27/2021 | 01:26 PM
10/27/2020 | Alternative | Reportable Incident | 159-04-276 | Middlesex | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 6000 | Advanced Septic |  | Pump | None | Alternative Discharge | Chlorine | 7000.000000 |  | ["Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | [17 empty] | Treatment system being abandoned and removed. Pumped treatment system empty - treatment system being removed - restaurant closed - unknown what alternative solutions have been proposed - unknown what treatment to be utilized for existing marina operations and/or restaurant operations. Service Agreement with Millers no longer in effect! | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 10/29/2020 | 10:00 AM
06/25/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | SES MidAtlantic LLC | 1942001203 | James | Green |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Attached Growth Medium"] | ["Effluent Screens" ,"Attached Growth Medium"] | YES | [15 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/15/2021 | 09:00 AM
04/20/2020 |  | RoutineScheduled | 44724 | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | ["None"] | ["None"] |  | None | Clear | 7.260000 |  |  |  |  | 04/20/2020 |  | 16.000000 | [8 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 06/30/2020 | 12:00 AM
05/26/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Payment | EHD - Loudoun | Great Falls Septic Service, Inc | 1942001301 | Josh | Hott | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/27/2021 | 11:51 AM
05/15/2020 |  | RoutineScheduled | 182-04-0612 | Rockingham | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Central Shenandoah | Onsite Wastewater Services - May Supply | 1942001022 | Sara | Tusing | 1.000000 |  | none | none | Pump | Pressure | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | INSPECTION BY DS | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/28/2021 | 05:41 AM
05/27/2020 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump | Distribution Box |  | None |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  | 2.58 | 6.550000 | 12.400000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 05/27/2020 | Jan 1 1900 1:45PM
12/12/2020 |  | Follow-Up |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | SES MidAtlantic LLC | 1942001203 | James | Green | 1.000000 |  | Delta Environmental Products, DF Series | none | Gravity | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation"] | ["Dispersal System Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Installed new zoner & compressor. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/15/2021 | 09:00 AM
05/18/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | sEPTIC AND ATU NEED PUMPED OUT ALSO THE AIRBLOWER IS NOT WORKING AND NEEDS TO BE REPLACED | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 |  | 04/14/2021 | 04:27 PM
10/08/2020 |  | Reportable Incident | 2017-143-0102 | Henrico | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Henrico | Old Dominion Onsite, Inc. | 1942001698 | Robert | Nicholas | [9 empty] | ["Blower/Compressor/Aerator Operation"] | ["Blower/Compressor/Aerator Operation"] | N/A | [17 empty] | Replaced aerator. System has returned to proper function. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 10/12/2020 | 12:05 PM
01/28/2020 |  | Routine, Scheduled | 033-17-0163-SP | Caroline County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Ware, Michele P | 1942001165 | Michele | Ware |  |  | Septic Tank Only | Septic Tank Only | None | None | None | None |  |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/28/2020 | 03:07 PM
09/26/2020 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintanence requirements | Pending Payment | EHD - Loudoun | WasteMaster, Inc. | 1942001062 | Tim | Jenkins | 1.000000 |  | none | none | Gravity | Gravity |  | Not Applicable |  | ["BlowerCompressorAerator Operation"] |  | NA | [15 empty] | Will be sent separately | Inspected | MultiFlo overflowing. Multiflo aerator not functioning. Unable to access dechlor applicator due to weeds. Unable to access discharge pipe due to weeds. | This AOSS is not functioning as designed or in accordance with the performance/maintanence requirements |  | 06/21/2021 | 10:37 AM
12/15/2020 |  | Follow-Up | 175-17-0287 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green | [9 empty] | ["Dispersal System Operation"] | ["Dispersal System Operation"] | [18 empty] | Replaced zoner. | This AOSS should now return to normal function after having provided the above state routine maintenance |  | 12/15/2020 | 04:00 PM
06/30/2020 |  |  | 113-19-018 | Madison | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Rappahannock-Rapidan | Randy's Complete Water & Wastewater Services | 1942001335 | Randy | Gray | 2.000000 | Gal | biomicrobics 2.0 | biomicrobics 3.0 | Pump | Pressure | Drip | Not Applicable |  | ["None"] | ["None"] | NA | Musty | Clear | 5.500000 | 5.800000 |  |  |  | 06/30/2020 | Pump Chamber | 23.000000 |  |  | 4.500000 | 29.000000 |  | Attached to this report | Exempt |  | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. |  |  | 08:45 PM
07/03/2020 |  | RoutineScheduled | {FIPSCode}-STS-66779 | Stafford | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Control Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | ["Control Operation" ,"Distribution Pump Operation" ,"Attached Growth Medium" ,"Effluent Screens" ,"Level Sensor Operation" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | YES | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
01/29/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Fairfax | Hott, Joshua D. | 1942001301 | Joshua | Hott | 1.000000 | 2500 | Septic Tank Only | Microfast | Pump | Distribution Box | Aggregate Trench | None |  | ["None"] | ["None"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/06/2020 | Jan 1 1900 1:03PM
09/02/2020 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 2705051738 | Joshua | Hott |  |  | Septic Tank | Puraflo | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [18 empty] | Need to replace peat moss. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. |  |  | 12:00 AM
12/11/2020 |  | Routine/Scheduled |  | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  |  |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  |  | 8.530000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 12/11/2020 | Jan 1 1900 8:30AM
01/23/2020 |  | Routine, Scheduled | SD-05-356 | Fauquier County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | MCKIM, STEPHEN E | 1934000043 | STEPHEN | MCKIM |  |  | Septic Tank Only | Septic Tank Only | None | None | None | None |  |  | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [18 empty] | [Comments]: Peat fiber was replaced by another company and we have re inspected system | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/23/2020 | 02:36 PM
07/07/2020 |  | RoutineScheduled | 182-87-0049 (LEGACY SEPTIC) | Rockingham | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Central Shenandoah | Onsite Wastewater Services - May Supply | 1942001022 | Sara | Tusing | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Pressure | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | INSPECTION BY DS | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/28/2021 | 05:41 AM
08/19/2020 |  | RoutineScheduled | {FIPSCode}-STS-1948 | Dickenson | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Effluent Screens"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
04/08/2020 | Conventional | Reportable Incident Component Maintenance | 073-STS-103625 | Gloucester | This AOSS should now return to normal function after having provided the above state routine maintenance Other conventional maintenance performed | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | None | None | Gravity | Distribution Box | Aggregate Trench | None | 600.000000 |  | ["Dispersal System Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | [17 empty] | Septic pumped for repair / replacement of distribution box. Installed new distribution box and spliced to conveyance and header lines. | This AOSS should now return to normal function after having provided the above state routine maintenance | Other conventional maintenance performed | 04/27/2020 | 09:00 AM
10/01/2020 |  | RoutineScheduled | 177-17-0054-SWP | Spotsylvania | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Attached Growth Medium"] | ["Attached Growth Medium" ,"Recirculation Pump"] | NA | [15 empty] | Will be sent separately | Inspected | The Orenco riser lid is cracked but secure. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/09/2021 | 03:25 PM
02/03/2020 |  | Routine, Scheduled |  | Albemarle County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Blue Ridge | ARNOLD, ARCHIE G | 1942001291 | ARCHIE | ARNOLD | 1.000000 | 1000 | Aqua Safe ATU | Septic Tank Only | Pump | Drip | Drip Tubing | None | 100.000000 | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Effluent Screens","SludgeScum Accumulation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Effluent Screens","SludgeScum Accumulation"] |  | musty | murky | [15 empty] | [Comments]: O&M: Replace air filter,flush drip lines, clean disk filter replaced air filter. performed typical maintenance. System working as intended. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/06/2020 | 01:18 PM
04/09/2020 |  | Routine, Scheduled | SD-08-49 | Culpeper County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | JENKINS, TIMOTHY R | 1942001062 | TIMOTHY | JENKINS |  |  | Aero-flo ATU | None | None | Drip | Alternative Discharge | Chlorine |  | ["None"] | ["None"] | [18 empty] | [Comments]: No Discharge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/22/2020 | 02:05 AM
02/26/2020 |  | Routine, Scheduled | 234-13-8 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesapeake | R & K Septic, Inc. |  | John | Butt, Jr |  |  | Clearstream ATU |  | Pump | Drip | Elevated Sand Mound | UV Light |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] |  |  | 3.83 | 7.940000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/26/2020 | Jan 1 1900 9:30AM
06/12/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Gravity | Gravity | Pad | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/14/2021 | 04:27 PM
08/14/2020 |  | RoutineScheduled | 179-15-0169-SP | Stafford | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Effluent Screens" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Effluent Screens" ,"Recirculation Pump"] | YES | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/09/2021 | 03:25 PM
11/07/2020 |  | Initial Visit | 069160194 | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Combs Wastewater Management LLC | 1942001353 | Amy | Combs | 2.000000 | 1000 |  |  | Pump | Gravity | Drip | Not Applicable | 450.000000 | [] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 01/08/2021 | 12:00 AM
06/05/2020 |  | Routine/Scheduled | 05-118-0013 | Charles City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chickahominy | Miller's Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1500 | Orenco Advantex | None | Pump | Distribution Box | Aggregate Trench | None |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | [17 empty] | In the Septic Tank, the RSV Ball was found stuck up causing the Tank to fall below normal level; | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 06/16/2020 | Jan 1 1900 3:56PM
06/10/2020 |  | Follow-Up | 171-07-0408 | Pittsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Pittsylvania-Danville | Acres of Virginia, Inc. | 1942001044 | Melvin | Collins | 1.000000 | 1500 | Ecoflo | none | Pump | Pressure | Trenches | Not Applicable | 450.000000 | ["None"] | ["None"] | NA | [17 empty] | Replaced tipping tray | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 06/11/2020 | 12:25 PM
12/09/2020 |  | Follow-Up | 06-197-A2 | Wise | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | Wise Health Dept |  | Rodney | Neece | 1.000000 |  | ATU |  | Gravity | Gravity | Discharge | Chlorination | [10 empty] | Still no tablets in chambers. | [11 empty] | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12/10/2020 | 12:00 AM
08/07/2020 |  | RoutineScheduled | 2016-143-0172 | Henrico | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Henrico | Onsite Maintenance Team | 1942001039 | Corey | Braxton | 3.000000 | 1200 | Clear stream 600 DC3 |  | Pump | Pressure | Drip |  | 200.000000 | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation"] | NA | Musty | Clear | 7.500000 | 4.000000 | [14 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 08/07/2020 | 12:00 AM
12/21/2020 |  | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Lord Fairfax | Aquarobic Services | 1934000142 | Michael | Blake |  |  | none | none | Pump | Gravity | Mound | Not Applicable |  | ["Distribution Pump Operation" ,"Level Sensor Operation" ,"Control Operation" ,"Auxiliary Filter"] | ["Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | Owner reported sporadic high level alarms. Wet stains on walls support this claim. Pump, panel and floats working correctly at this time and no groundwater infiltration was observed. Suspect alarms were due to excessive water use. Air pre-filter cleaned. Debris/hair clumps removed from timer enabler float switch. Owner to install filter for washing machine discharge. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 07/01/2022 | 10:30 AM
08/03/2020 | Alternative | Routine/Scheduled | 151-05-361 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1500 | Orenco Advantex | None | Pump | Manifold | Aggregate Trench | None | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | None | Clear | [15 empty] | Annual service conducted. Processing tank - at normal level - RSV, Effluent Screen and recirc. pump serviced. AdvanTex Module - bridging noted on media drapes - drapes flushed, but require power washing / possible replacement - spray grid serviced. Discharge tank in normal operating level - discharge pump serviced, float sensors and controls operating properly. Absorption field - exercised manifold valve - walkover indicates no signs of surfacing. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 08/06/2020 | 09:50 AM
11/20/2020 |  | Routine/Scheduled | 196-04-538 | Westmoreland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 3.000000 | 2500 | Ecoflo |  | Pump | Distribution Box | Aggregate Bed |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 11/20/2020 | 05:00 PM
05/08/2020 |  | Routine, Scheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Biomicrobics MicroFAST |  |  |  |  | None |  | ["Blower/Compressor/Aerator Operation"] | ["Blower/Compressor/Aerator Operation"] |  | Good | Tan | [15 empty] | Pump 1 Amps 9.71 ETM 188 hrs Cycles 38777 Pump 2 Amps 10.27 ETM 180 hrs Cycles 39791 Water Meter Reading 1967140 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 05/08/2020 | Jan 1 1900 1:29PM
07/18/2020 |  | RoutineScheduled | SP-05-532 | Stafford | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump" ,"Attached Growth Medium"] | ["Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump" ,"Attached Growth Medium"] | YES | [15 empty] | Will be sent separately | Inspected | Responded to alarm call and did full service on system. | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 |  | 04/09/2021 | 03:25 PM
06/24/2020 |  | Routine, Scheduled | 175-15-0213 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Puraflo |  |  |  |  | None |  | ["Effluent Screens","Level Sensor (Float) Operation"] | ["Effluent Screens","Level Sensor (Float) Operation"] | [18 empty] | Pump Amps 12.26 ETM 209.33 Cycles 23477 Septic Sludge 10 " Scum 1" Pump Sludge 2" Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 06/24/2020 | 10:10 AM
03/26/2020 |  | Routine, Scheduled |  | Loudoun County | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Paid | EHD - Loudoun | Mckim Construction | 1934000043 | Steve | Mckim | 1.000000 |  | None | None | Pump | Distribution Box | Aggregate Trench | [22 empty] | [Comments]: septic/atu need pumped out | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 04/12/2020 | 02:21 PM
04/20/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | SES MidAtlantic LLC | 1942001203 | James | Green | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/15/2021 | 09:00 AM
02/10/2020 |  | Reportable Incident | 234-17-441 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesapeake | Farmer's Septic Service, Inc. |  | Ross | Cole | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | [Comments]: Owner called due to the last rain - got an alarm. Serviced system. Checked the pump, panel, & floats (ok). Cleaned the filter in the Clearstream, cleaned the disc filter, and cleaned the UV light bulb. Changed the diffuser in the Clearstream and changed the filter in the aerator. The septic tank needs additional risers on it so it can be properly inspected in the future. The timer is set to 8 minutes every 2 hours. Did not take initial samples. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/10/2020 | Jan 1 1900 12:00PM
09/11/2020 |  | Routine/Scheduled |  | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump | Drip | Elevated Sand Mound | UV Light |  | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  |  | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 09/11/2020 | Jan 1 1900 10:30AM
04/17/2020 | Alternative | Routine/Scheduled | 166-04-461 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001063 | K.R. Trapper | Davis | [10 empty] | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | At the time of maintenance, the service expert found that tall tanks were at normal level. Tested the pump and all floats and confirmed that they were functioning as they should. A new globe valve was installed during this visit. The service expert tested the valve and determined that the dispersal field is now getting water as it should. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/17/2020 | 11:06 AM
10/30/2020 |  | RoutineScheduled | 10-163-0026 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Clearstream | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12/04/2020 | 12:00 AM
08/21/2020 |  | Routine/Scheduled | 04-120-0320AR | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. |  |  | Orenco Advantex |  | Pump |  |  |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 08/21/2020 | Jan 1 1900 12:30PM
09/30/2020 |  | Follow-Up | 069050286 | Frederick | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Lord Fairfax | Dehavens backhoe | 1942001541 | Michael | Edmonson | 1.000000 | 1250 | microfast |  | Pump | Pressure | Drip | Not Applicable |  | ["Control Operation","Auxiliary Filter","Level Sensor Operation"] | ["Control Operation","Auxiliary Filter","Level Sensor Operation"] | NA | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 10/05/2020 | 01:00 AM
06/22/2020 |  | Routine/Scheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | POWELLS PLUMBING, INC. | 1942001036 | Kurt | Holthaus | 1.000000 | 1500 | Microfast |  | Pump | Drip | Drip Tubing |  | 450.000000 | ["Blower/Compressor/Aerator Operation"] | ["Blower/Compressor/Aerator Operation"] | N/A | [17 empty] | Annual Inspection - Serviced spin filter and blower. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 06/26/2020 | 02:16 PM
02/07/2020 |  | Routine, Scheduled | 800-11-0074 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Western Tidewater | R & K Septic, Inc. |  | John | Butt, Jr |  |  | Clearstream ATU | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] |  |  |  | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/07/2020 | Jan 1 1900 10:00AM
08/08/2020 |  | RoutineScheduled | 175-14-0303 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Wastemaster Inc |  | Timothy | Jenkins | 2.000000 |  | Recirculating Sand Filter |  | Pump | Gravity | Discharge | UV |  | [] | [] |  | Musty | Clear | 7.100000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 09/03/2020 | 02:00 PM
11/18/2020 |  | RoutineScheduled | 099-06-0079-ST | King George | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"Control Operation" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Attached Growth Medium"] | ["Distribution Pump Operation" ,"Level Sensor Operation" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Control Operation" ,"Dispersal System Operation" ,"Attached Growth Medium"] | NA | [15 empty] | Will be sent separately | Inspected | Roots in rope hole of pod 1 I dug it out on both sides monitor next year. Outlet pipe on septic tank settling hard to get filter monitor next year. Stringy grass roots on septic tank inlet wedge lid. no indication of infiltration customer never gets alarms in heavy rains. Peat looks in very good condition for being 13 years old! | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
11/28/2020 |  | RoutineScheduled | 196-05-532 | Westmoreland | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Three Rivers | Wastemaster Inc |  | Timothy | Jenkins | 2.000000 |  | ATU |  | Pump | Pressure |  |  |  | [] | [] | [5 empty] | 23.000000 | [12 empty] | UV Nonfunctional | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. |  | 12/09/2020 | 03:25 PM
01/16/2020 |  | Routine, Scheduled | 182-04-0113 | Rockingham County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Central Shenandoah |  |  |  |  | 1.000000 |  |  | Biomicrobics MicroFAST | Pump | Manifold | Drip Tubing | None |  | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/21/2020 | 30-12-1899 07:33 PM
01/17/2020 |  | Routine, Scheduled | 159-05-185 | Middlesex County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers | LANGFORD, CHARLES T | 1934000143 | CHARLES | LANGFORD | 1.000000 | 1000 | Clearstream | Septic Tank Only | None | None | None | None |  | ["Control Operation"] | [19 empty] | [Comments]: AUDIBLE ALARM NOT WORKING VISUAL ALARM FUNCTIONING ROOT INTRUSION IN TANKS | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/19/2020 | 09:46 AM
01/02/2020 |  | Routine, Scheduled | 159-11-020 | Middlesex County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers | LANGFORD, CHARLES T | 1934000143 | CHARLES | LANGFORD |  |  | Clearstream | Septic Tank Only | None | None | None | UV Light |  | ["Disinfection"] | ["Disinfection"] | [18 empty] | [Comments]: NEW SALCOR UNIT INSTALLED | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/03/2020 | 12:16 PM
01/06/2020 |  | Routine, Scheduled | 109-14-0197 | Bedford County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Central | WAUGH, IAIN C | 1942001512 | IAIN | WAUGH | 1.000000 | 1500 | Septic Tank Only | Orenco Advantex | Pump | Distribution Box | Aggregate Trench | None |  | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Effluent Screens","Recirculation Pump"] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Effluent Screens","Recirculation Pump"] | [18 empty] | [Pumpout Comments]: Not Needed at this time but if heavy oil layer continues to build, it may need pumping more frequently then normal. Your septic tank is just below full the FOG layer will break down Especially if F.O.G. (Fats oil and grease) are not allowed in the septic system. Recommend to wipe grease out from pans. [Comments]: Septic Tank 2-4" Scum 7-12" Sludge- Try reduce F.O.G. use in Drains, Large Oil and Grease layer in Septic Tank, Recirc zone 8" Sludge- Discharge zone 8" Sludge, Cleaned Bio Filter, Srpay pattern weak in Recirc tank- Cleaned Sprayer assembly, Scrubbed and flushed manifold. Sprayed off Media Filters to reduce buildup. Pulled Pump. See Below | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/06/2020 | 10:25 PM
06/09/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | The septic tank lid was too damaged to remove safely. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/27/2021 | 01:26 PM
08/20/2020 |  | RoutineScheduled | 196-07-180 | Westmoreland | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Pad | Not Applicable |  | ["Attached Growth Medium" ,"Effluent Screens" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Effluent Screens" ,"Recirculation Pump"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 |  | 04/09/2021 | 03:25 PM
05/13/2020 |  | RoutineScheduled | 182-12-0115 | Rockingham | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Central Shenandoah | Onsite Wastewater Services - May Supply | 1942001022 | Sara | Tusing | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Pressure | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/28/2021 | 05:41 AM
07/01/2020 |  | RoutineScheduled |  | Shenandoah | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation" ,"Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Dispersal System Operation" ,"Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | [7 empty] | 07/01/2020 |  | 21.000000 | [5 empty] | Will be sent separately | Inspected | Lab Sample Normal Repaired valve boxes | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/26/2021 | 09:04 AM
10/07/2020 |  | RoutineScheduled | 35441 | Clarke | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Rejected | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 2405110225 | Larry | Royston | [9 empty] | ["Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["None"] | NO | [16 empty] | Inspected |  | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. |  | 01/19/2021 | 12:00 AM
10/08/2020 |  | RoutineScheduled | 00-197-A11 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | Wise County Health Dept. |  | Rodney | Neece | 1.000000 |  | ATU |  | Gravity | Gravity | Discharge | Chlorination |  |  |  |  | None | Clear | 6.500000 | 8.000000 |  |  | Chlorine Effluent (0) | [11 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 10/08/2020 | Jan 1 1900 2:20PM
07/14/2020 | Alternative | Routine/Scheduled | 157-89-328 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | None | None | Pump | Manifold | Elevated Sand Mound | None | 450.000000 |  | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | [17 empty] | Pump tank pumped empty to allow confined space entry to reparge. Routine service conducted. Replaced riser access on septic tank, pump tank and sealed / parged pump tank. Mound walked - no areas of wetness / surfacing noted. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 07/16/2020 | 12:15 PM
02/18/2020 |  | Routine, Scheduled | 08-142-0095 | Hanover County | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Chickahominy | Old Dominion Onsite, Inc. |  | Jason | Hackler | 1.000000 | 1500 | Biomicrobics MicroFAST |  | Pump | Distribution Box | Aggregate Trench | None |  | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation"] | [18 empty] | [Comments]: Cleaned air filter. No power on the control panel. Water level high in discharge tank. Need power restored for control side of panel. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 02/18/2020 | Jan 1 1900 10:28AM
07/16/2020 |  | RoutineScheduled |  | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 3.000000 |  | Septic Tank | Pump Tank (Puraflo) Pump Tank(Discharge) | Pump | Pressure | Trenches | Not Applicable |  | ["Level Sensor Operation","Attached Growth Medium"] | ["Attached Growth Medium","Level Sensor Operation"] | [8 empty] | 07/16/2020 | Sample Chamber | 13.000000 | [5 empty] | Attached to this report |  | Septic Tank-6"sludge 0"scum/ Puraflo Pump Tank-0"sludge/Discharge Pump Tank-2"sludge/ Counts: cc1-2320 ETM-8768.58/ cc2-2300 ETM-8056.85/ Replaced override float. No pump out needed at this time. Drainfield is good. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  |  | 12:00 AM
10/27/2020 |  | RoutineScheduled |  | Augusta | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/26/2021 | 09:04 AM
01/15/2020 |  | Reportable Incident |  | Prince William County | This AOSS should now return to normal function after having provided the above stated routine maintenance. | Paid | EHD - Prince William | SEAMON, CHARLIE L | 1942001108 | CHARLIE | SEAMON |  |  | Septic Tank Only | Delta Environmental Products, DF Series | Pump | Distribution Box | Aggregate Trench | None |  | ["Distribution Pump Operation"] | ["Distribution Pump Operation"] | [18 empty] | [Comments]: Service call only: Found faulty Zoeller N 140 Pump and replaced. Pump counts 8468/ ETM 447.82 | This AOSS should now return to normal function after having provided the above stated routine maintenance. |  | 02/17/2020 | 07:30 AM
12/02/2020 | Alternative | Routine/Scheduled | 166-97-304 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | Puraflo |  | Pump | None | Aggregate Bed | None | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | Musty | Clear | [15 empty] | Routine service Primary Septic Tank - normal level - effluent screen serviced. Pump Tank - normal level - pump, float sensors & controls operating. PuraFlo - FOUR Module - peatmoss in good condition - raked / turned. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 12/03/2020 | 08:00 AM
01/21/2020 |  | Routine, Scheduled | 2013-143-0116 | Henrico County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Henrico | [13 empty] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump"] | [18 empty] | [Comments]: Flushed drip field and filter. Cleaned effluent filter. Checked float and pump operation. System appears to be functioning well. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/21/2020 | 11:05 AM
03/27/2020 |  | Routine, Scheduled | 179-12-0128-SWP | Stafford County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Orenco Advantex | None | Pump | Drip | Drip Tubing |  |  | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | [18 empty] | [Comments]: May need check valve. Vacuumed scum out of recirc vault. Drip rate has dropped, could try bleaching system to get flow to increase. Proposal to be sent to homeowner. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/01/2020 | 06:33 AM
12/20/2020 |  |  | SD-04-741 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC |  | Jason | Brown | 1.000000 | 1000 | Septic | Puraflo | Gravity | Pressure | Trenches | Not Applicable |  | [] | [] | YES | Musty | Cloudy | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12/28/2020 | 03:20 PM
11/19/2020 |  | RoutineScheduled | 175-13-0188 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Prince William | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | EcoPod | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"BlowerCompressorAerator Operation" ,"Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | ["Attached Growth Medium" ,"BlowerCompressorAerator Operation" ,"Control Operation" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Treatment tank (both sides) and pump tank needs pumped out. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
08/31/2020 |  | Follow-Up |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Pod 3 and 4 drain lines were blown out and unclogged | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/14/2021 | 04:27 PM
05/11/2020 |  | Routine/Scheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | POWELLS PLUMBING, INC. | 1942001036 | Kurt | Holthaus | 1.000000 | 1250 | Microfast |  | Pump | Drip | Drip Tubing |  | 450.000000 |  |  | N/A | [17 empty] | Annual Inspection - Serviced spin filter. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 05/13/2020 | 11:49 AM
12/03/2020 |  | RoutineScheduled | 09-100-0209 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Bundick Well & Pump | 1942001051 | Peter | Duer | 1.000000 | 1250 | Septic Tank | Bio-COIR ATS-6 | Pump | Pressure | Pad | Not Applicable | 650.000000 | ["Attached Growth Medium"] | ["Attached Growth Medium"] | YES | [16 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12/04/2020 | 07:40 AM
11/30/2020 |  | RoutineScheduled | 179-09-0154-SR | Stafford | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Level Sensor Operation" ,"Control Operation" ,"Recirculation Pump" ,"SludgeScum Accumulation"] | ["Level Sensor Operation" ,"Recirculation Pump" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | On site for annual inspection and to investigate alarm. Panel's electronic log indicated "filter clog". Cleaned very dirty biotube filter and pump intake. Tank needs pumping. Owner called and scheduled a pump-out. Advised him to refill tank with enough fresh water to turn on the bottom float switch. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
07/29/2020 |  | Reportable Incident |  | Isle Of Wight | This AOSS should now return to normal function after having provided the above state routine maintenance | Pending Payment | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Puraflo |  | Pump |  |  |  |  | ["Control Operation","Dispersal System Operation","Distribution Pump Operation"] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation"] | N/A | [17 empty] | Replaced pump | This AOSS should now return to normal function after having provided the above state routine maintenance |  | 07/29/2020 | Jan 1 1900 4:00PM
04/18/2020 |  | RoutineScheduled | 109-18-0489 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1000 | Advantex |  | Gravity | Gravity | Trenches |  |  | ["None"] | ["None"] | [18 empty] | 6" of solids in septic tank. Flushed treatment unit spray manifold. Cleaned septic tank filter. Tested floats, pump and alarm. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 09/17/2020 | 07:03 PM
04/17/2020 |  | Routine, Scheduled | 107-07-0649 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | AYRES, KENNETH Edgar | 1942001128 | KENNETH | AYRES | 1.000000 | 1500 | Septic Tank Only | Biomicrobics MicroFAST | Pump | Drip | Drip Tubing | None |  | ["Attached Growth Medium","Auxiliary Filter"] | ["Attached Growth Medium","Auxiliary Filter"] | [18 empty] | [Pumpout Comments]: SYSTEM PUMPED BY ROTOR ROOTER INSPECTOR PRESENT DURING PUMPING OF BOTH TANKS. [Comments]: SYSTEM PUMPED DUE TO EXCESSIVE GROWTH ON THE MEDIA FILTER. MEDIA FILTER AND SPIN FILTER BOTH CLEANED. SEPTIC TANK AND PUMP TANK WERE BOTH PUMPED AND CLEANED. CONTROL OPERATIONS FUNCTIONING AS DESIGNED. NO VISIBLE LEAKS IN DRIP FIELD. LIDS SECURED. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 04/25/2020 | 04:55 PM
11/04/2020 |  |  | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001301 | Joshua | Hott | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
10/05/2020 | Alternative | Routine/Scheduled | 157-04-207 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1500 | Orenco Advantex |  | Pump | Distribution Box | Gravel-Less Trench | None | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | None | Clear | [15 empty] | Routine Service Processing Tank - normal operating level - RSV, Recirc Pump & effluent screen serviced. Treatment Module - media drapes & spray grid serviced. Pump Tank - pump serviced - float sensors and controls operating properly. Distribution Box - Plastic - several orange seals ruptured - distribution box in normal level - all laterals accepting effluent - recommend replacement of plastic D-Box with Concrete. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 10/12/2020 | 08:30 AM
01/23/2020 |  | Routine, Scheduled | 033-19-0026-SP | Caroline County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Ware, Michele P | 1942001165 | Michele | Ware |  |  | Septic Tank Only | Septic Tank Only | None | None | None | None |  |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | [16 empty] | Attached to this report |  | VENIS File Names: BOD Results.pdf | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/30/2020 | 12:15 PM
09/08/2020 |  | RoutineScheduled | 033-STS-87265 | Caroline | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | 90-Day Inspection | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/09/2021 | 03:25 PM
08/07/2020 |  | Reportable Incident | 087-STS-6332 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Henrico | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 5.000000 | 10000 | None | None | Pump | Distribution Box | Aggregate Trench | None | 5000.000000 | ["Septic Tank Baffles","Sludge/Scum Accumulation"] | ["Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | [17 empty] | Septic tanks pumped empty for storage to facilitate repairs. Primary and Secondary septic tank collapse - verbal permission from Henrico County Health Department to replace / install new. 2 - 2000g traffic rated tanks installed - risers installed to grade. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 08/10/2020 | 11:30 AM
06/15/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/27/2021 | 01:26 PM
02/28/2020 |  | Routine, Scheduled |  | Loudoun County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | None | Pump | Distribution Box | Aggregate Trench | [23 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/12/2020 | 02:21 PM
05/18/2020 |  | Routine/Scheduled | 06-120-0611A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesterfield | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | Ecoflo | None | Pump | Distribution Box | Aggregate Trench | None |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | The Filter in the Septic Tank is outdated (we recommend its replacement during your next scheduled pumping service) and the area around the Outlet Pipe has deteriorated; in the Ecoflo Biofilter Module, there are several patches that are bulging/failing, and a section has buckled; there was slight bulging noted in the Pump Chamber; the Surge Box has deteriorated; the Distribution Box Lid was found cracked, and was not inspected per Homeowner request. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 06/04/2020 | Jan 1 1900 1:01PM
04/25/2020 | Alternative | RoutineScheduled | 128-05-133 | Essex | This AOSS is functioning as designed and in accord | Approved | EHD - Three Rivers | Wastemaster |  | Tim | Jenkins | 2.000000 |  |  |  | Pump |  | Subsurface |  |  | [] | [] | [8 empty] | 04/25/2020 | [10 empty] | This AOSS is functioning as designed and in accord |  |  | 12:00 AM
05/29/2020 |  | Reportable Incident |  | Frederick | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Lord Fairfax | POWELLS PLUMBING, INC. | 1942001036 | Kurt | Holthaus | 1.000000 | 1000 | Multiflo FTB |  | Pump | Distribution Box | Aggregate Trench |  |  | ["Blower/Compressor/Aerator Operation"] | ["Blower/Compressor/Aerator Operation"] | N/A | [17 empty] | Replaced customer supplied aerator for Multiflo. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 06/24/2020 | 01:53 PM
08/12/2020 | Alternative | RoutineScheduled | 151-04-159 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Church View Septic Service Inc. | 1942001302 | Charles | Langford | 1.000000 | 1000 | Ecoflo |  | Gravity | Pressure | Trenches | Not Applicable |  | ["Other"] | ["Other"] | [17 empty] | Pumped Out | Ground water was infiltrating in around outlet pipe during heavy rains. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 08/12/2020 | 12:00 AM
09/22/2020 |  | Reportable Incident | 199-05-0028 | York | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Peninsula | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1500 | Orenco Advantex |  | Pump | Distribution Box | Aggregate Bed | None | 450.000000 |  |  | N/A | [17 empty] | System alarming high level - storm damage to access riser allowing flooding by surface / ground water. 09/24/2020 - Damaged riser repaired - | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 10/05/2020 | Jan 1 1900 10:00AM
02/12/2020 |  | Routine, Scheduled |  | Louisa County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Blue Ridge | CLARK, MICHAEL J | 1934000023 | MICHAEL | CLARK |  |  | Septic Tank Only | Septic Tank Only | None | None | None | None |  |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/24/2020 | 05:06 AM
11/20/2020 |  | RoutineScheduled |  | Page | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Level Sensor Operation" ,"Auxiliary Filter"] | ["Control Operation" ,"Level Sensor Operation" ,"Auxiliary Filter"] | NA | [7 empty] | 11/20/2020 |  | 80.000000 | [5 empty] | Will be sent separately | Inspected | Repaired electrical from panel to system for alarm float | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance |  | 04/26/2021 | 09:04 AM
03/23/2020 |  | Routine, Scheduled |  | Page County | This AOSS should now return to normal function after having provided the above stated routine maintenance. | Paid | EHD - Lord Fairfax | Cubbage, Harrison Lee, II | 1942001021 | Harrison | Cubbage | 1.000000 | 1500 | Septic Tank Only | Orenco Advantex | Pump | Drip | Drip Tubing | None |  | ["Auxiliary Filter","Control Operation","Level Sensor Operation"] | ["Auxiliary Filter","Control Operation","Level Sensor Operation"] |  | Musty | Clear | [5 empty] | 03/23/2020 | Pump Tank | 10.000000 | [5 empty] | Attached to this report |  | [Lab Comments]: Lab Sample Normal [Comments]: Replaced Cracked filter and pressure gauge Corrected float assembly Recirc Pump- Off 19.7min On .3min ETM-1729.6Hr Cycle COunt-39901 Discharge Pump- Off 2hrs On 10min ETM-764.5Hr Cycle COunt-64718 VENIS File Names: 1266 Batman Rd 3-23-20.pdf | This AOSS should now return to normal function after having provided the above stated routine maintenance. |  | 04/06/2020 | 02:05 PM
06/23/2020 |  | Routine/Scheduled | 10-160-0197 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Orenco Advantex |  | Pump | Distribution Box |  | None |  | ["None"] | ["Control Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Recirculation Pump","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 06/23/2020 | 08:00 AM
06/02/2020 |  | RoutineScheduled |  | Augusta | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter"] | ["Control Operation" ,"Auxiliary Filter"] | NA | [7 empty] | 06/02/2020 |  | 22.000000 | [5 empty] | Will be sent separately | Inspected | Lab sample normal | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/26/2021 | 09:04 AM
01/29/2020 |  | Routine, Scheduled | 177-06-0192 | Spotsylvania County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Ware, Michele P | 1942001165 | Michele | Ware |  |  | Septic Tank Only | Septic Tank Only | None | None | None | None |  |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | [18 empty] | [Comments]: Sludge:4" | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/30/2020 | 05:24 PM
06/08/2020 | Alternative | Routine/Scheduled | 136-12-0287 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001063 | K.R. Trapper | Davis | [11 empty] | N/A | [17 empty] | At the time of maintenance, the service expert found that all tanks were at normal level. He did note that the float within the treatment tank contained some water in it. Due to these finding, he recommends having this float replaced. He also noted that the air line does not have a union. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 06/09/2020 | 01:28 PM
10/02/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | A inspection on an alternative septic system. The state requires that all alternative septic systems must be inspected EVERY year and filed with the state and the county. The septic control panels are interior one demand the other is a timed dose. There is 1 pvc cleanout near house. The septic tank was pumped out and the filter was cleaned. The filter manufacture recommends that the filter be cleaned every 6 months. Both pump tanks, pump, floats and force mains were inspected All 5 purflo pods were opened. The peat fiber looked good on top. We dug down to the bottom of each pod to look for any standing water and all were dry. The 15 port concrete d-box was ground level and opened up. The d-box is broken and will need to be replaced. The drain field was probed and was dry. At time of inspection system was not in working condition. | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 |  | 04/14/2021 | 04:27 PM
02/03/2020 |  | Reportable Incident | 177-12-0288-SP | Spotsylvania County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Orenco Advantex | None | Pump | Distribution Box |  |  |  | ["Control Operation","Level Sensor Operation"] | ["Control Operation","Level Sensor Operation"] | [18 empty] | [Comments]: Septic tank and grease trap pumped out last week and grease clog cleared last week (by others). Chief requested follow-up visit. Neither tank had refilled yet, so recirc pump had created low level condition when pumping part of each dose back to the septic tank for nitrogen reduction. Normally the effluent then flows right back into the recirc tank and maintains the minimum level. Spinners were moving slowly and tops of sheets were dirty/greasy. Rinsed all that off until spinners were working correctly. Discharge tank was also in low level, but due to a "failed on" timer float. This allowed extra cycles to be run and created a lot of low level alarms in the previous weeks. Low level count now at 280 and high level count at 67. Minor infiltration observed in septic tank at lower riser joint. Recommend addition of riser and lid to inlet end of tank to facilitate inspections and pump-outs. Used fiber optic camera to inspect sewer line that feeds grease trap tank. Belly just prior to tank holding some water and fairly good glob of grease encountered close to building. Pipe may need jetting if clogging occurs again. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/11/2020 | 01:54 PM
10/08/2020 |  | Reportable Incident |  | Isle Of Wight | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Payment | EHD - Western Tidewater | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 2000 | None | None | Pump | Distribution Box | Aggregate Trench | None |  | ["Dispersal System Operation","Distribution Pump Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] |  | N/A | [17 empty] | Pump tank has collapsed - septic tank full to overflowing - pumped by Goodman's Septic Service ... Commercial establishment - pending permit information documents. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 10/13/2020 | Jan 1 1900 8:00AM
10/10/2020 |  | RoutineScheduled | SD-89-488 | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Wastemaster Inc |  | Timothy | Jenkins | 1.000000 |  | ATU | BK2000 |  | Gravity | Discharge | Chlorination |  | ["SludgeScum Accumulation"] | [] |  | Musty | Clear | 6.600000 |  | 22.000000 | 2.200000 | [11 empty] | Pumping Recommended | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 10/26/2020 | 09:50 AM
06/22/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/14/2021 | 04:27 PM
11/03/2020 | Alternative | Routine/Scheduled | 119-STS-93365 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 10000 | None | None | Gravity | Distribution Box | Aggregate Trench | None | 450.000000 |  | ["Dispersal System Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | [17 empty] | 180 day post install inspection. Septic Tank - normal operating level - effluent screen serviced. Distribution box intact - all laterals accepting effluent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 11/04/2020 | 08:00 AM
09/17/2020 |  | Routine, Scheduled | 175-93-0115 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green |  |  |  |  | Pump | Drip | Drip Tubing | None |  | ["Effluent Screens"] | ["Effluent Screens"] | [18 empty] | Spin filter cleaned. Pump Amps 9.24 ETM 260 hrs Cycles 1520 Water Meter Reading 71700 Septic Sludge 3" Scum 0 Pump Sludge 2" Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 09/17/2020 | 09:10 AM
02/18/2020 |  | Routine, Scheduled | 136-11-0141 | Gloucester County | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Three Rivers | Farmer’s Septic Service, Inc. |  | Ross | Cole | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | [Comments]: Serviced system. Checked the pump, panel, & floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. The Salcor UV is not working. There is a hole in the 2" pipe - need to cut off and put a coupling in it, also H20 is blowing on the UV. Need to replace the UV panel, bulb, cord, and tube. The septic tank needs additional risers on it so it can be properly inspected in the future. The timer is set to 6 minutes every 2 hours. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 02/18/2020 | 12:00 PM
10/06/2020 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [11 empty] | N/A | [9 empty] | 2.000000 |  | 1.000000 | [6 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 10/12/2020 | Jan 1 1900 8:30AM
12/29/2020 |  | Routine, Scheduled | 175-19-0143 | Prince William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Biomicrobics MicroFAST |  |  |  |  | UV Light |  | ["Blower/Compressor/Aerator Operation","Disinfection"] | ["Blower/Compressor/Aerator Operation"] |  | Acceptable | Clear | [15 empty] | UV Bulb & chord needs replacing. Spin filter cleaned. Pump Amps11.98 ETM 89 hrs Cycles 911 Water Meter Reading 58500 Septic Sludge 3" Scum 6" ATU Sludge 5" Scum 0 Pump Sludge 0 Scum 0 | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 12/29/2020 | 01:38 PM
05/27/2020 |  | RoutineScheduled | 107-98-0273 (LEGACY ALT. SYSTEM) | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Inboden Environmental Services, Inc | 1942001083 | Terry | Inboden | [8 empty] | 1680.000000 | ["None"] | ["None"] | [18 empty] | No Alarms | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 06/25/2020 | 12:00 AM
08/04/2020 |  | RoutineScheduled |  | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 2705051738 | Joshua | Hott |  |  | Septic | Puraflo | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
12/07/2020 |  | Routine/Scheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | POWELLS PLUMBING, INC. | 1942001036 | Kurt | Holthaus | 1.000000 | 1060 | Orenco Advantex |  | Pump | Drip | Drip Tubing |  | 450.000000 | ["Effluent Screens"] | ["Effluent Screens"] | N/A | [17 empty] | Annual Inspection - Serviced effluent screen(s). | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12/29/2020 | 02:33 PM
11/24/2020 |  |  | 09-142-0149 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Clearstream | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 01/04/2021 | 12:00 AM
02/24/2020 |  | Routine, Scheduled | 45701 | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Lord Fairfax | Cubbage, Harrison Lee, II | 1942001021 | Harrison | Cubbage | 1.000000 | 1500 |  | Biomicrobics MicroFAST | Pump | Drip | Drip Tubing | None |  | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation"] |  | Musty | Clear | [15 empty] | [Comments]: Pump Settings: Off 2hrs On 6min Sludge/Scum Accumulations: Comp.1- 13"/1" Comp.2- 12"/0" Pump Tank-4"/0" | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/01/2020 | 01:00 PM
04/29/2020 | Alternative | Routine/Scheduled | 128-05-127 | Essex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001063 | K.R. Trapper | Davis | [11 empty] | N/A | [17 empty] | At the time of maintenance, the service expert found that the alarm float within the recirulation tank was no longer functioning and in need of replacement. The bad float was replaced during this visit. The pressure gauge within the headworks box was also not functioning and replaced on site. Also noted that there was ponding on the media sheets, preventing water from being fully treated. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/28/2029 | 02:38 PM
05/27/2020 |  | RoutineScheduled |  | Shenandoah | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 | 1500 | Septic Tank | Bio-Microbics | Pump |  | Drip | Not Applicable |  | ["Distribution Pump Operation","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | YES | Musty | Clear | [16 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 05/27/2020 | 12:00 AM
03/10/2020 |  | Follow-Up |  | Loudoun County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | None | Pump | Distribution Box | [23 empty] | [Comments]: Peat fiber replaced in all pods | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/12/2020 | 02:21 PM
05/18/2020 |  | Reportable Incident | C 800-15-0225 | Suffolk | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | Owner called due to the red light being on for a couple of weeks. Serviced system. Checked the pump, panel, & floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream, changed the filter in the aerator, changed the mesh screen in the spinfilter, and replaced the pressure switch on the aerator. The aerator should be raised - full of ants. The UV is not working - not wired up correctly - wired up directly to the breaker panel at the house - needs to be wired up through the control panel. There is visible wetness on the drainfield - rain - need to keep an eye on it. The timer is set to 6 minutes every 2 hours. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. |  | 05/18/2020 | Jan 1 1900 12:00PM
12/10/2020 |  | Routine/Scheduled | 14-142-0192 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Old Dominion Onsite, Inc. | 1942001549 | Russell | Revis | [9 empty] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump"] | N/A | [17 empty] | Cleaned effluent filter, flushed manifold. Checked float and pump operation. System appears to be operating normally. Upon opening septic tank risers I noticed some "flushable" wet wipes in scum layer. These do not break down and can cause blockages in filters and pumps, which leads to premature failure. These items should not be allowed to enter the septic tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12/10/2020 | Jan 1 1900 2:25PM
05/29/2020 |  | Routine, Scheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Biomicrobics MicroFAST |  |  |  |  | None |  | ["Blower/Compressor/Aerator Operation"] | ["Blower/Compressor/Aerator Operation"] |  | Good | Clear | [15 empty] | Pump 1 Amps 7.61 ETM 170.32 Cycles 5812 Pump 2 Amps 7.51 ETM 177.29 Cycles 5633 Pump 1 Amps 14.15/ 14.96 Septic Sludge 4" Scum 2" ATU Sludge 2" Scum 0 Pump Sludge 2" Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 05/29/2020 | Jan 1 1900 10:30AM
03/24/2020 |  | Routine, Scheduled | 179-06-0029-SWT | Stafford County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Biomicrobics MicroFAST | None | Pump | Drip | Drip Tubing |  |  | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/06/2020 | 02:46 PM
05/06/2020 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Joe Blevins Equipment Rental, Inc | 2705013926 | Joel | Blevins | 2.000000 | 1500 | Microfast |  | Pump | Gravity | Trenches | Not Applicable |  | ["Other"] | ["Other"] | NA | Musty | Clear | [5 empty] | 05/06/2020 | Pump Chamber | 14.000000 | [5 empty] | Attached to this report |  | Compressor is strong and cleaned air filter. No sludge build up in tank. Ditches are dry. No dial-flow in distribution box. We install new ones. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | Jan 1 1900 12:20PM
02/12/2020 |  | Routine, Scheduled | 179-08-0039-SP | Stafford County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001350 | Mike | Cook | 1.000000 |  | Puraflo | None | Pump | Distribution Box | Aggregate Trench |  |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/13/2020 | 08:33 AM
11/02/2020 |  | RoutineScheduled | 107-07-0287 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Onsite Wastewater Services - May Supply | 1942001627 | Drew | Shull | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 05/28/2021 | 05:41 AM
05/30/2020 |  | RoutineScheduled | 2084-03-153 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | WasteMaster |  | Timothy | Jenkins | 2.000000 |  | PuraFlo |  | Pump | Gravity | Discharge |  |  | [] | [] |  | Musty | Clear | 7.800000 |  |  | 2.200000 | [12 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 01:25 PM
03/13/2020 |  | Routine, Scheduled |  | Page County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Lord Fairfax | SEAL, CHARLES K | 1934000144 | CHARLES | SEAL | 1.000000 |  | Septic Tank Only | Puraflo | Pump | Distribution Box | Aggregate Trench | None |  | ["Attached Growth Medium","Septic Tank Baffles"] | ["Attached Growth Medium","Septic Tank Baffles"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/16/2020 | 11:17 AM
02/26/2020 |  | Follow-Up | 179-18-0297-SWP | Stafford County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001350 | Mike | Cook | 1.000000 |  | Biomicrobics MicroFAST | None | Pump | Distribution Box | [15 empty] | 20.000000 | [8 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/06/2020 | 08:57 AM
11/03/2020 |  | RoutineScheduled | 177-14-0058-SWP | Spotsylvania | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | EcoPod | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"BlowerCompressorAerator Operation"] | ["Attached Growth Medium" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced defective blower. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/09/2021 | 03:25 PM
07/23/2020 |  | Reportable Incident |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  |  |  | ["Blower/Compressor/Aerator Operation","Control Operation"] | ["Blower/Compressor/Aerator Operation","Control Operation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 07/23/2020 | Jan 1 1900 10:30AM
03/26/2020 |  | Follow-Up | 179-14-0222-SR | Stafford County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson |  |  | Orenco Advantex | None | Pump | Distribution Box |  | UV Light | [13 empty] | 26.000000 |  | 1600.000000 | [6 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/27/2020 | 04:14 AM
03/04/2020 |  | Routine, Scheduled |  | Loudoun County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | None | Pump | Distribution Box | Aggregate Trench | [23 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/12/2020 | 02:21 PM
03/25/2020 |  | Routine, Scheduled | 181-07-0175 | Rockbridge County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Central Shenandoah | [7 empty] | Septic Tank Only | None | None | None | None |  | ["None"] | ["None"] | [18 empty] | [Comments]: Filters checked and cleaned. Control panels functioning properly. System did not need to be pumped. No apparent leaks in system or drain field area. Lids properly secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/27/2020 | 30-12-1899 10:43 AM
01/14/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Fairfax | SEAMON, CHARLIE L | 1942001108 | CHARLIE | SEAMON |  |  | Septic Tank Only | Microfast | Pump | Distribution Box | Aggregate Trench | None |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | [10 empty] | 13.000000 | [5 empty] | Attached to this report |  | [Comments]: Performance Inspection And BOD Sample:Microfast to Drainfield.Septic-8"sludge 6"scum/Microfast-10"sludge (Will need pump out in about 6 months) Pump tank-0"sludge. P1 cnts-910 ETM-42h 59m P2-cnts-900 ETM-42h 11m/Peak-13 High-11/ Blower air filter cleaned.Pumps Goulds WE0511h 52gpm. No breakout or spongy areas on the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/25/2020 | Jan 1 1900 1:41PM
10/15/2020 |  | Routine, Scheduled | 175-04-0728 | Prince William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Puraflo |  |  |  |  | None |  | ["Dispersal System Operation","Distribution Pump Operation","Effluent Screens"] | ["Effluent Screens"] | [18 empty] | System was in alarm. One Puraflo unit has turned to mud .Puraflo's not getting equal flow. Needs alarm float. Septic Sludge 12" Scum 1" Pump Sludge 2" Scum 0 | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 10/15/2020 | 09:05 AM
03/04/2020 |  | Routine, Scheduled | 03-165-0214 | Northampton County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Eastern Shore | DUER, PETE C | 1942001051 | PETE | DUER | 1.000000 | 1250 | Septic Tank Only | Puraflo | Pump | None | None | None |  | ["None"] | ["None"] | [18 empty] | [Comments]: Aoss Inspection. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/27/2020 | 02:04 PM
02/29/2020 |  | Routine, Scheduled |  | Rockingham County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Central Shenandoah | DOVEL, JERRY A | 1942001116 | JERRY | DOVEL | 1.000000 |  | EZ Treat Sandfilter | Septic Tank Only | None | None | None | None | [22 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/07/2020 | 07:12 PM
04/14/2020 |  | Routine, Scheduled | 175-06-0127 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Delta Environmental Products, DF Series |  |  |  |  | None |  | ["Blower/Compressor/Aerator Operation"] | ["Blower/Compressor/Aerator Operation"] |  | Good | Clear | [15 empty] | Spin filter cleaned. Pump Amps7.69 Cycles 20375 Water Meter Reading 773980 Septic Sludge 4" Scum 1" ATU Sludge 0 Scum 3" Pump Sludge 5" Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/14/2020 | 01:11 PM
07/29/2020 |  |  | 06-100-0354 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Bundick Well & Pump | 1942001051 | Peter | Duer | 1.000000 | 1250 | Septic Tank | Purflo | Pump | Pressure | Pad | Not Applicable |  | ["None"] | ["None"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 08/18/2020 | 12:20 PM
05/20/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/27/2021 | 01:26 PM
02/05/2020 |  | Routine, Scheduled | 171-04-0303 | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Lord Fairfax | Cubbage, Harrison Lee, II | 1942001021 | Harrison | Cubbage | 1.000000 | 1000 |  | Puraflo | Pump | Distribution Box | Aggregate Trench | None |  | ["Attached Growth Medium","Auxiliary Filter","Control Operation"] | ["Attached Growth Medium","Auxiliary Filter","Control Operation"] |  | Musty | Clear | [15 empty] | [Comments]: Raked Puraflo Modules Pump Settings: Off 5hrs On 4min Sludge/Scum Accumulations: Septic Tank-10"/0" Pump tank-6"/0" | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/11/2020 | 02:12 PM
06/24/2020 |  | Routine, Scheduled | -STS-20173 | Manassas | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Aquarobic Mini Plant | Sandfilter, Non-recirculating |  |  |  | Chlorine |  | ["Blower/Compressor/Aerator Operation","Disinfection"] | ["Blower/Compressor/Aerator Operation","Disinfection"] |  | Good | Clear | 6.470000 | 3.230000 | [13 empty] | Pump Amps 8.73 Cycles 36805 Septic Sludge 10" Scum 2" ATU Sludge 1" Scum 0 Pump Sludge 2" Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 06/24/2020 | 11:53 AM
02/03/2020 |  | Routine, Scheduled | {FIPSCode}-STS-2390 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesapeake | R & K Septic, Inc. |  | John | Butt, Jr |  |  | Orenco Advantex |  | Pump | Distribution Box |  | None |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | [18 empty] | [Comments]: Moved junction box in tank, ran new conduit & wire. Replaced middle float & vent cap. Installed float tree. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/03/2020 | Jan 1 1900 8:00AM
11/10/2020 |  | RoutineScheduled | 06-197-A10 | Wise | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | EHD - Lenowisco | Wise County Health Dept. |  | Christopher | Cantrell | 1.000000 |  | Jet |  | Gravity | Gravity |  | Chlorination | 450.000000 |  |  |  | Musty | Clear | 6.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 11/16/2020 | 12:00 AM
09/22/2020 | Alternative | RoutineScheduled | 171-15-030 | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | ["Control Operation"] | [] |  | None |  | 6.980000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 10/15/2020 | 08:20 AM
04/06/2020 |  | Routine, Scheduled |  | Fluvanna County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Blue Ridge | CLARK, MICHAEL J | 1934000023 | MICHAEL | CLARK |  |  | Septic Tank Only | Septic Tank Only | None | None | None | None |  |  | ["Attached Growth Medium","Auxiliary Filter","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/12/2020 | 04:49 AM
11/17/2020 |  | RoutineScheduled | 179-14-0321-SR | Stafford | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Septic Tank Baffles" ,"SludgeScum Accumulation" ,"BlowerCompressorAerator Operation" ,"Control Operation" ,"Attached Growth Medium" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | ["Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"Control Operation" ,"Attached Growth Medium" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Cleaned ATU, few roots at pump tank wedge lid and septic tank riser, no alarms from infiltration. Septic/ATU tank needs to be pumped out. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
10/01/2020 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump | Drip | Elevated Sand Mound | UV Light |  | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | Replaced aerator, uv bulb, uv cord | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 10/01/2020 | Jan 1 1900 4:00PM
02/03/2020 |  | Follow-Up |  | Prince William County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Prince William | SEAMON, CHARLIE L | 1942001108 | CHARLIE | SEAMON |  |  | Septic Tank Only | Microfast | Pump | Manifold | Drip Tubing | None |  | ["Attached Growth Medium","Dispersal System Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Dispersal System Operation","SludgeScum Accumulation"] | [18 empty] | [Comments]: Follow up on performance report done on 1/8/2020. Septic/ATU Tank was pumped and also media was cleaned by SeptiClean. Other repairs: Cracked zoner replaced by others. System now functioning as designed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/04/2020 | 10:37 AM
05/05/2020 |  | RoutineScheduled | 12-173-089 | Prince Edward | This AOSS is functioning as designed and in accord | Approved | EHD - Piedmont | Taylor's Septic Service | 1942001028 | Penny | Taylor | 1.000000 | 1500 |  | Norweco Singulair | pump | distribution Box | graveless trench |  | 450.000000 | ["BlowerCompressorAerator Operation","Effluent Screens"] | ["BlowerCompressorAerator Operation","Effluent Screens"] | true | Low | clear | [16 empty] | This AOSS is functioning as designed and in accord |  | 05/05/2020 | Jan 1 1900 10:00AM
03/12/2020 |  | Routine, Scheduled | 109-09-0237 | Bedford County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Central | WAUGH, IAIN C | 1942001512 | IAIN | WAUGH | 1.000000 | 1000 | Septic Tank Only | Whitewater ATU | Pump | Drip | Drip Tubing | None |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | [18 empty] | [Pumpout Comments]: Not needed at this time [Comments]: Septic Tank 4" Scum 6" Sludge Treament tank 2" scum 6" sludge - Good Aeration Pump Tank 6" sludge Alarm tested good on pump panel, Alarm tested good on blower panel, Pump operational, Pump float operation, alarm float operatonal, Blower motor replace in September in great condition | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/12/2020 | 11:34 PM
05/27/2020 |  | RoutineScheduled |  | Shenandoah | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter" ,"Control Operation" ,"Dispersal System Operation"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter" ,"Control Operation" ,"Dispersal System Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Repaired pressure gauage at time of service May need pumping in 2020. Let us know if you would like us to do this during next inspection | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance |  | 04/26/2021 | 09:04 AM
02/24/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Delta Environmental Products, DF Series |  | Pump | Drip | Drip Tubing | None |  | ["BlowerCompressorAerator Operation","Effluent Screens"] | ["BlowerCompressorAerator Operation","Effluent Screens"] |  | Good | Clear | [15 empty] | [Comments]: Spin filter cleaned.Pump Amps 4.20Water Meter Reading 165155Septic Sludge 12" Scum 0.50ATU Sludge 0 Scum 0Pump Sludge 1" Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/24/2020 | Jan 1 1900 11:10AM
04/20/2020 |  | Routine/Scheduled | 01-172-0353A | Powhatan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesterfield | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | [11 empty] | N/A | [17 empty] | At the time of maintenance, the service expert found that all tanks were at normal level. Tested and confirmed that all floats and pump were functioning properly. He was unable to locate the distribution box during this visit but our office has requested a copy of the septic permit from the County to assist in locating it during the next visit. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/20/2020 | Jan 1 1900 2:40PM
04/28/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | SES MidAtlantic LLC | 1942001203 | James | Green | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/15/2021 | 09:00 AM
07/14/2020 |  | RoutineScheduled | 124-STS-2379 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Rappahannock-Rapidan | Soils, Inc. | 1940001392 | Markham | Smith | 1.000000 | 1500 | Mirofast 0.75 in a Hanover 1500 top seam tank |  | Gravity | Gravity | Trenches | Not Applicable |  | [] | ["BlowerCompressorAerator Operation","Dispersal System Operation","SludgeScum Accumulation","Attached Growth Medium"] | NA | [17 empty] | The tank was pumped again by great falls. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 07/27/2020 | 03:45 PM
09/15/2020 |  | Routine/Scheduled | 06-172-0156AR | Powhatan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. |  |  | Orenco Advantex |  | Pump | Drip |  |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 09/15/2020 | Jan 1 1900 10:30AM
06/08/2020 |  | RoutineScheduled | 179-15-0109-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NO | [15 empty] | Will be sent separately | Inspected | 90-Day Inspection. We were not able to service the effluent filter in the Septic Tank. We will contact the installer to ask him to extend it into the tank. The UV light is not working properly. We were not able to troubeshoot with the manufacturer becasue their compturs where down. We are planning a follow-up trip. | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 |  | 04/09/2021 | 03:25 PM
09/05/2020 |  | RoutineScheduled | 2118-06-153 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Wastemaster Inc |  | Timothy | Jenkins | 2.000000 |  | PuraFlo |  | Pump | Gravity | Discharge | Chlorination |  | [] | [] | YES | Musty | Clear | 7.100000 |  |  | 2.200000 | [12 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 09/11/2020 | 12:05 PM
10/01/2020 | Alternative | Reportable Incident | 157-03-168 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | PremierTech, EFX |  | Pump | None | Aggregate Bed | None | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | Musty | Clear | [15 empty] | System pumped to effect repairs Repair Primary Septic Tank - pumped empty to effect repair Plastic Pump Basin removed - new Infiltrator 500g plastic pump tank installed per HDID 157-20-0093 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 10/09/2020 | 08:45 AM
09/05/2020 |  | Follow-Up |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 | Pending Payment | EHD - Loudoun | WasteMaster, Inc. | 1942001062 | Tim | Jenkins |  |  | Multiflo FTB | none | Gravity | Gravity |  | Chlorination |  |  | ["BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | In to replace MF Aerator. Electrical junction box full of greasy foam. Electrical wiring has failed. MF PVC piping broken in 2 locations. | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 |  | 06/21/2021 | 10:37 AM
12/09/2020 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintanence requirements | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Gravity | Gravity |  | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | a septic inspection was done on a conventional gravity septic system. The state requires that all conventional tanks must be pumped out every 5 years and filed with the state and count. There is 1 pvc clean out near the house. The sewer line was camera snaked and was clear. The concrete septic tank was dug up it was 12" under the ground. The inlet and outlet T's are pvc. The septic tank was pumped out and the tank was inspected for any leaks or cracks none were found. The conveyance line was camera snaked and was clear. The 6 port concrete surge was dug up it was 14" under the ground. The box needs to be replace. The conveyance line from surge to d-box was camera snaked and was clear. The 6 port concrete d-box was 2 1/2 feet under the ground. The box is deuterated and will need to be replace. There are 5 header lines. The drain field bottom line is hydraulically overloaded and effluent is on the surface. At this time the septic system is not in working condition. Home owner needs to contact a soil engineer. | This AOSS is not functioning as designed or in accordance with the performance/maintanence requirements |  | 04/14/2021 | 04:27 PM
06/15/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Payment | EHD - Loudoun | Great Falls Septic Service, Inc | 1942001301 | Josh | Hott | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/27/2021 | 11:51 AM
09/18/2020 |  | RoutineScheduled |  | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | McKim Construction | 1942001330 | Michelle | McKim |  |  |  |  | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 11/13/2020 | Jan 1 1900 10:20AM
02/24/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Biomicrobics MicroFAST |  | Gravity | Distribution Box |  | None |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] |  | Good | Clear | [5 empty] | 02/24/2020 |  | 20.000000 | [7 empty] | [Comments]: Septic Sludge 5" Scum 10"ATU Sludge 10" Scum 9" | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/24/2020 | Jan 1 1900 12:40PM
08/21/2020 |  | RoutineScheduled | {FIPSCode}-STS-10137 | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Greenway Engineering | 1942001008 | Jeremy | Ferguson | 1.000000 | 1000 | Puraflo | none | Pump | Pressure | Drip | Not Applicable |  | ["Attached Growth Medium","SludgeScum Accumulation"] | ["Attached Growth Medium","SludgeScum Accumulation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 09/03/2020 | 02:10 PM
05/09/2020 |  | RoutineScheduled | 109-18-0071 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1500 | Advantex |  | Pump | Pressure | Drip |  |  | ["None"] | ["None"] | [18 empty] | 4" of solids in septic tank. Flushed treatment unit spray manifold. Cleaned drip manifold filter. 22 psi on drip field. Cleaned septic tank filter. Flushed drip field. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 09/17/2020 | 07:03 PM
12/07/2020 | Alternative | RoutineScheduled | 35802 | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | None | Clear | 8.080000 |  |  |  |  | 12/07/2020 |  | 7.000000 |  |  | 7.700000 | [5 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12/21/2020 | 03:10 PM
09/24/2020 |  | Routine/Scheduled | 196-15-0026 | Westmoreland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 3.000000 | 3000 | EcoPod |  | Pump | Drip | Drip Tubing |  |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | [17 empty] | Evidence that to much water is being used than system is designed for. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 09/24/2020 | 05:00 PM
08/19/2020 |  | Routine/Scheduled | 800-STS-14487 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Western Tidewater | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 9000 | Advanced Septic | None | Pump | Distribution Box | Aggregate Trench | None | 4500.000000 |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Recirculation Pump","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | Musty | Clear |  | 5.400000 |  |  |  | 08/19/2020 | Clarifier Outfall | [8 empty] | Laboratory samples for BOD5 and TSS obtained. Monthly service conducted as per VDH Consent Order. Primary septic tank / flow equalization tank in moderately high level, but not yet activating high level alarm float sensor - possible increase in water usage - Recirculation weir noted to have more return than normal - appears that a section has "corroded" and fallen into the septic tank. ATU Functioning - compressor # 2 & 4 serviced. Clarifier outfall serviced to remove blockage material. Discharge tank in normal operating level. All pumps, float sensors and controls functioning properly. Facility is heavily overgrown - NOTE that last two weeks have had extraordinary heavy rain events and grass unable to be cut due to how wet it is. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 08/21/2020 | Jan 1 1900 8:00AM
12/31/2020 |  | Reportable Incident | 154-14-0083 | Louisa | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Blue Ridge | All In Septic Services | 1942001442 | Dennis | Mitchell | 11.000000 | 10,000 | Whitewater | Whitewater | Pump | Pressure | Drip | Not Applicable |  | [] | ["BlowerCompressorAerator Operation","Dispersal System Operation","Effluent Screens"] | YES | None | Clear | [14 empty] | Pumped Out |  | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 01/01/2021 | 07:03 PM
12/22/2020 |  | RoutineScheduled | 179-12-0203-SWP | Stafford | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Dispersal System Operation" ,"Level Sensor Operation" ,"Control Operation"] | ["Control Operation" ,"Dispersal System Operation" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Level Sensor Operation" ,"Recirculation Pump"] | NA | [15 empty] | Will be sent separately | Inspected | Roots in D-Box I removed them. They were not going into the header lines monitor next year. D-Box is out of level had to remove dial-a-flows on 2 upper lines to get equal flow in all trenches. Panel shows very low water usage on dis charge pump. Outstanding proposal to run camera down inlet pipe potential break due to settling. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
10/07/2020 |  | RoutineScheduled | 16-197-084 | Wise | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Effluent Screens"] | ["BlowerCompressorAerator Operation","Control Operation","Effluent Screens","Disinfection"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
11/06/2020 |  | RoutineScheduled | {FIPSCode}-STS-23329 | Scott |  |  | EHD - Lenowisco |  |  | John | Hyder |  |  | Norweco |  | Gravity |  |  | Chlorination |  |  |  |  | None | Clear | 7.000000 | 4.000000 |  |  | chlorine residual 0 | [10 empty] | No laboratory tests performed. Routine field inspection. |  |  |  | 12:00 AM
08/21/2020 |  | RoutineScheduled | 171-09-0115 | Pittsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Pittsylvania-Danville | Virginia Septic Service LLC | 1942001512 | iain | Waugh | 1.000000 | 1500 | Ecoflo |  | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens","Attached Growth Medium"] | ["Effluent Screens","Attached Growth Medium"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 08/21/2020 | 12:00 AM
08/12/2020 |  | RoutineScheduled |  | Warren | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Dispersal System Operation" ,"SludgeScum Accumulation"] | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Dispersal System Operation" ,"SludgeScum Accumulation"] | NA | [15 empty] | Will be sent separately | Inspected | All tanks pumped Zone valve replaced | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance |  | 04/26/2021 | 09:04 AM
06/01/2020 |  | Routine/Scheduled | 11-120-0127A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. |  |  | Norweco Singulair ATU |  | Pump |  |  |  |  | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 06/01/2020 | Jan 1 1900 1:30AM
04/08/2020 |  | Follow-Up |  | Loudoun County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | Biomicrobics MicroFAST | None | Gravity | Drip | Drip Tubing | [22 empty] | [Comments]: Fixed the air blower and was able with lye to break up the grease and other that was clogging up the microfast unit. At this time system is in working condition. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/12/2020 | 02:21 PM
04/29/2020 |  | RoutineScheduled | SWP-04-739 | Spotsylvania | This AOSS is functioning as designed and in accord | Approved | EHD - Rappahannock | Wastemaster |  | Tim | Jenkins | 2.000000 |  |  |  | Pump |  | Subsurface |  |  | [] | [] | [8 empty] | 04/29/2020 | [9 empty] | Cleaned Pump, Floats, Headworks filter and flushed all field lines. | This AOSS is functioning as designed and in accord |  |  | 12:00 AM
03/23/2020 |  | Routine, Scheduled |  | Louisa County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Blue Ridge | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Orenco Advantex | None | Pump | Distribution Box | Aggregate Trench |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | [18 empty] | [Comments]: One hinge on AX20 pod lid is not attached. Had to run wire & conduit to pump tank (corroded UF wire). Installer used bare ground for conductor. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/01/2020 | 06:33 AM
08/11/2020 | Alternative | Initial Visit | 136-12-0016 | Gloucester | This AOSS should now return to normal function after having provided the above state routine maintenance | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | Delta Environmental Products, UC Series |  | Pump | Distribution Box | Aggregate Trench | None | 450.000000 |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | Pungent | Discolored | [15 empty] | Site visited for Alarm event Previous visit found blower unit had failed Septic tank in normal operating level Aeration tank in normal operating level - blower unit replaced with new Discharge tank in normal operating level. | This AOSS should now return to normal function after having provided the above state routine maintenance |  | 08/12/2020 | 10:30 AM
07/13/2020 |  | RoutineScheduled | 099-06-0272-SP | King George | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Attached Growth Medium" ,"Auxiliary Filter" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump"] | ["Auxiliary Filter" ,"Attached Growth Medium" ,"Effluent Screens" ,"Recirculation Pump" ,"Distribution Pump Operation"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 |  | 04/09/2021 | 03:25 PM
08/20/2020 | Alternative | Reportable Incident | 159-09-105 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | None | None | Gravity | Distribution Box | Aggregate Trench | None | 450.000000 |  | ["Dispersal System Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | [17 empty] | Maintenance New building sewer installed from residence to septic tank Riser access installed on septic tank Added cleanout access to conveyance line | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 08/27/2020 | 08:00 AM
07/07/2020 |  | RoutineScheduled | SD-12-389 | Fauquier | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Rappahannock-Rapidan | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/Ecopod | Pump Tank | Pump | Pressure | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation","SludgeScum Accumulation"] | [] | NA | [17 empty] | Septic/Ecopod-6"sludge 2"scum/14"sludge Ecopod requires pump out. Pump tank-4"sludge. Blower at high amps requires replacement. Hand-36/High-28/Override-38/Pump start-14148/Pump run-1811/water meter-064101 | This AOSS should now return to normal function after having provided the above state routine maintenance. |  |  | 12:00 AM
08/27/2020 | Alternative | RoutineScheduled | 151-10-070 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services |  | joel | pinnix | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
11/18/2020 |  | RoutineScheduled |  | Warren | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Puraflo | none | Pump | Gravity |  | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter"] | ["Control Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | Breakers were tripped to panel was able to correct | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance |  | 04/26/2021 | 09:04 AM
10/14/2020 |  | RoutineScheduled | 179-STS-90549 | Stafford | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Effluent Screens"] | ["Attached Growth Medium" ,"Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected | The peat in the Puraflo Modules has lost its texture and is holding water. Peat replacement or the installation of a different treatment unit is recommended. | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 |  | 04/09/2021 | 03:25 PM
01/15/2020 |  | Routine, Scheduled | 2005-143-0326 | Henrico County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Henrico |  |  |  |  | 1.000000 | 1500 |  | None | Pump | Drip | Drip Tubing | None | 600.000000 | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | [18 empty] | [Comments]: sludge = 16" scum = 4" | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/17/2020 | 02:20 PM
02/26/2020 |  | RoutineScheduled | 14-100-0417 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Bundick Well & Pump | 1942001051 | Peter | Duer | 1.000000 | 1250 | Septic Tank | Delta Eco Pod E-50N | Pump | Pressure | Trenches | UV | 450.000000 | ["Disinfection"] | ["Disinfection"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 06/02/2020 | 12:00 PM
03/06/2020 |  | Routine, Scheduled |  | Prince William County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Delta Environmental Products, DF Series |  |  |  |  | None |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] |  | Good | Good | [15 empty] | [Comments]: Pump Amps 7.05 ETM 123h 20m Cycles 1559Septic Sludge 6" Scum 7"ATU Sludge 14" Scum 0Pump Sludge 0.50 Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/06/2020 | 08:59 AM
01/06/2020 |  | Routine, Scheduled | 179-19-0008-SWP | Stafford County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Michael Smith | 1942001080 | michael | smith | 1.000000 |  | Orenco Advantex | None | Gravity | [16 empty] | 11.000000 | [8 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/05/2020 | 03:37 PM
07/09/2020 |  | RoutineScheduled | 019-STS-24199 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1000 | Advantex AX20RT |  | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | NA | [16 empty] | Inspected | Newly Installed advantex AX20RT | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 07/10/2020 | 09:30 AM
12/30/2020 |  | RoutineScheduled | SP-05-253 | Caroline | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Rappahannock | Wastemaster Inc |  | Timothy | Jenkins | 2.000000 |  | Advantex |  | Pump | Gravity | Drip |  |  | [] | [] | [18 empty] | In for alarm. Found flex PVC pip in tank broken. Made repair. Perfromed annual clean and inspection of system. System operating properly at this time. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 01/14/2021 | 10:00 AM
06/17/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/14/2021 | 04:27 PM
06/04/2020 |  | Reportable Incident | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance | Approved | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green | [9 empty] | ["Distribution Pump Operation"] | ["Distribution Pump Operation"] | [18 empty] | Installed Z 140 effluent pump. | This AOSS should now return to normal function after having provided the above state routine maintenance |  | 06/04/2020 | Jan 1 1900 4:00PM
11/12/2020 |  | Follow-Up | 179-11-0236-SWP | Stafford | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | EZ Treat Sandfilter | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Replaced non-functioning horn and pressure gauge that was rotten. Homeowner notified us that they had the pump out done on November 4th. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
11/03/2020 |  | RoutineScheduled | 175-10-0305 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Wastemaster Inc |  | Timothy | Jenkins | 2.000000 |  | Recirculating Sand Filter | Effluent Filter | Pump | Gravity | Discharge | Chlorination |  | [] | [] |  | Musty | Clear | 6.900000 |  |  | 2.200000 | [12 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 11/20/2020 | 02:00 PM
10/27/2020 |  | RoutineScheduled | {FIPSCode}-STS-58945 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Wastemaster Inc |  | Timothy | Jenkins | 2.000000 |  | Recirculating Sand Filter |  | Pump | Gravity | Discharge | Chlorination |  | [] | [] | [18 empty] | No discharge from wetlands | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 11/16/2020 | 02:30 PM
08/13/2020 |  | Routine, Scheduled | 175-17-0069 | Prince William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Biomicrobics MicroFAST |  | Pump | Drip | Drip Tubing | UV Light |  | ["Blower/Compressor/Aerator Operation","Disinfection"] | ["Blower/Compressor/Aerator Operation"] |  | Good | Good | [15 empty] | UV Bulb & cord bad. Spin filter cleaned. Pump Amps 10.21 ETM 220 hrs Cycles 1688 Water Meter Reading 22860 Septic Sludge 10" Scum 12" ATU Sludge 14" Scum 0 Pump Sludge 2" Scum 0 | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 08/13/2020 | 01:30 PM
04/02/2020 |  | Routine, Scheduled | 033-12-0113-SP | Caroline County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Orenco Advantex | None | Pump | Drip | Drip Tubing |  |  | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | [18 empty] | [Comments]: Few roots in septic tank wedge lid. Replaced control panel due to tree fall. Replaced bottom 2 floats in discharge. Could not locate ARV’s. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/27/2020 | 04:14 AM
05/26/2020 |  | Routine, Scheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Delta Environmental Products, DF Series |  |  |  |  | None |  | ["Effluent Screens"] | ["Effluent Screens"] |  | Good | Clear | [5 empty] | 05/26/2020 | Pump tank | 25.000000 | [7 empty] | Pump 1 Amps 12.83 ETM 203121 Cycles 4535 Pump 2 Amps 10.93 ETM 200245 Cycles 43889 Septic Sludge 1" Scum 0 ATU Sludge 10" Scum 2" Pump Sludge 2" Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 05/26/2020 | Jan 1 1900 10:25AM
07/24/2020 |  | Follow-Up |  | Frederick | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Lord Fairfax | POWELLS PLUMBING, INC. | 1942001036 | Kurt | Holthaus | 1.000000 | 1500 | Microfast |  | Pump | Drip | Drip Tubing |  |  | ["Control Operation"] | ["Control Operation"] | N/A | [17 empty] | Replaced MVP logo controller in Orenco control box. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 07/31/2020 | 02:33 PM
12/02/2020 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic Tank | Pump Tank | Pump | Pressure | Mound | Not Applicable |  | ["None"] | ["None"] | NO | [17 empty] | Septic tank-3"sludge 0"scum/ Pump Tank-0"sludge. No pump out needed at this time. No breakout or spongy areas on the Wisconsin Mound. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
11/25/2020 | Alternative | RoutineScheduled | 150-06-116 | King William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | GeoEnvironmental Services, Inc. | 1942001010 | Peter | Mamunes | 1.000000 | 1250 | Microfast |  | Pump | Pressure | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Level Sensor Operation","SludgeScum Accumulation","Distribution Pump Operation","Dispersal System Operation","Control Operation","BlowerCompressorAerator Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12/15/2020 | 10:45 AM
12/07/2020 |  | RoutineScheduled | 196-12-151 | Westmoreland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
09/04/2020 |  | Routine/Scheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | POWELLS PLUMBING, INC. | 1942001036 | Kurt | Holthaus | 1.000000 | 1000 | Puraflo |  | Pump | Distribution Box | Aggregate Trench |  | 450.000000 | ["Effluent Screens"] | ["Effluent Screens"] | N/A | [17 empty] | Annual Inspection - Serviced effluent screen(s). | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 09/10/2020 | 10:57 AM
07/28/2020 |  | RoutineScheduled | SP-04-384 | Stafford | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Control Operation" ,"Attached Growth Medium" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Level Sensor Operation"] | ["Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Attached Growth Medium" ,"Control Operation" ,"Distribution Pump Operation"] | YES | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
11/16/2020 |  | RoutineScheduled | 107-08-0114 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Onsite Wastewater Services - May Supply | 1942001627 | Drew | Shull | 1.000000 |  | Orenco Advantex | none | Pump | Gravity |  | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | inspection by Ds | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 05/28/2021 | 05:41 AM
12/08/2020 |  | Routine/Scheduled | 2015-143-0160 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Henrico | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | Orenco Advantex |  | Pump | Distribution Box | Aggregate Trench | None | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | None | Clear | [15 empty] | Routine Service Primary Septic tank - normal level - effluent screen serviced. AX RT Processing Tank - recirc pump serviced - media drapes & spray grid serviced. AX RT Pump Tank - discharge pump serviced, float sensors and controls operating properly. Distribution box - intact - all laterals accepting effluent. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 12/09/2020 | 10:15 AM
07/03/2020 |  | RoutineScheduled | SWP-05-130 | Stafford | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Control Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | ["Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Distribution Pump Operation" ,"Control Operation" ,"Attached Growth Medium" ,"Effluent Screens" ,"Level Sensor Operation"] | YES | [15 empty] | Will be sent separately | Inspected | Pump out of septic tank needed, recommend pump out of pump tank as well. Septic tank; few roots at inlet wedge lid. Pump tank; leak @ outlet pipe and wedge lid. Septic tank needs new concrete lid. Proposal to be sent to homeowner. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
09/05/2020 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Eco Virginia | 1942001235 | William | Poindexter | 1.000000 |  | Biomicrobics MicroFAST | Biomicrobics MicroFAST | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 |  | 06/03/2021 | 05:53 AM
07/09/2020 |  | RoutineScheduled | {FIPSCode}-STS-9358 | Russell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. |  | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Effluent Screens","Control Operation"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
03/13/2020 |  | Routine, Scheduled | 177-06-0260-SWP | Spotsylvania County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | None | None | Pump | Distribution Box | Aggregate Bed |  |  | ["Distribution Pump Operation","Effluent Screens"] | ["Dispersal System Operation","Effluent Screens"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/06/2020 | 02:45 PM
07/22/2020 |  | Routine/Scheduled | 03-120-0322A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesterfield | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | Orenco Advantex | None | Gravity | Distribution Box | Aggregate Trench | None | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | None | Clear | [15 empty] | Routine service conducted. Septic tank in normal level - no access riser present Processing tank in normal level - RSV, Effluent Screen & Recirc. pump serviced. AdvanTex Module - media washed, distribution grid serviced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 07/23/2020 | Jan 1 1900 8:00AM
04/28/2020 |  | RoutineScheduled | 139-07-031 | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | SEAL’S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal | 1.000000 |  | septic tank only | MicroFast | Pump | Pressure | Drip | Not Applicable |  | ["Dispersal System Operation","Auxiliary Filter","BlowerCompressorAerator Operation"] | ["Dispersal System Operation","Auxiliary Filter","BlowerCompressorAerator Operation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 04/28/2020 | 12:00 AM
06/01/2020 |  | RoutineScheduled | 187050827 | Warren | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Rejected | EHD - Lord Fairfax | Greenway Engineering | 1942001008 | Jeremy | Ferguson | 1.000000 | 1250 | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium"] | [] | NA | [17 empty] | Peat is bad and needs replaced. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. |  | 09/28/2020 | 12:30 PM
04/22/2020 |  | Follow-Up |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | SES MidAtlantic LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Replaced concrete casing lid. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/15/2021 | 09:00 AM
06/15/2020 |  | RoutineScheduled | 179-17-0086-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Distribution Pump Operation" ,"Recirculation Pump" ,"Dispersal System Operation" ,"Auxiliary Filter" ,"Attached Growth Medium"] | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Recirculation Pump" ,"Auxiliary Filter" ,"Attached Growth Medium"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 |  | 04/09/2021 | 03:25 PM
08/06/2020 |  | Reportable Incident | 175-11-0268 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green | [9 empty] | ["Blower/Compressor/Aerator Operation"] | ["Blower/Compressor/Aerator Operation"] | [18 empty] | Installed new D80 compressor. | This AOSS should now return to normal function after having provided the above state routine maintenance |  | 08/06/2020 | 04:00 PM
06/22/2020 |  | RoutineScheduled | 179-07-0276-SWP | Stafford | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Recirculation Pump"] | ["Auxiliary Filter" ,"Recirculation Pump"] | NA | [15 empty] | Will be sent separately | Inspected | In the past 30 days, the system averaged 5.9 discharge cycles @ 10.9 minutes per day with no override cycles. Users alarm log had not recorded any high level alarms yet this year. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
04/17/2020 |  | Routine/Scheduled |  | Frederick | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Review | EHD - Lord Fairfax | POWELLS PLUMBING, INC. | 1942001036 | Kurt | Holthaus | 1.000000 | 1000 | Puraflo |  | Pump | Drip | Drip Tubing |  | 450.000000 | ["Control Operation","Effluent Screens"] | ["Control Operation","Effluent Screens"] | N/A | [17 empty] | Annual Inspection - Serviced spin filter and effluent screen(s). Alarm bulb missing from drainfield control box (panel two). Repair four inch clean out adapter that is damaged. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. |  | 07/02/2020 | 02:07 PM
02/03/2020 |  | Routine, Scheduled | 177-14-0211-SWP | Spotsylvania County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Orenco Advantex | None | Pump | Distribution Box | Aggregate Trench |  |  | ["Control Operation","Distribution Pump Operation","Level Sensor Operation"] | ["Control Operation","Distribution Pump Operation","Level Sensor Operation"] | [18 empty] | [Comments]: Control panel alarmed a couple of times in the past few days. Effluent level was very close to low level in recirc tank, but high in septic tank due to dirty effluent filter. Recirc pump sends a portion of each cycle back to the septic tank for nitrogen reduction. The dirty filter slowed the flow of effluent back into the recirc tank and caused the alarms. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/05/2020 | 07:59 AM
12/11/2020 |  | RoutineScheduled | 187080103 | Warren | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Lord Fairfax | Cloverleaf Environmental Consulting, Inc | 1942001135 | Robert | Charnley |  |  | Sand Filter |  | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","Level Sensor Operation"] | ["Attached Growth Medium","Level Sensor Operation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. |  |  | 12:00 AM
10/17/2020 |  | RoutineScheduled | 137-STS-25542 | Orange | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Wastemaster Inc |  | Timothy | Jenkins | 2.000000 |  | Recirculating Sand Filter | Wetlands | Pump | Gravity | Discharge | Chlorination |  | ["SludgeScum Accumulation"] | [] | [18 empty] | Trash Tank access below grade. Pump tank requires pumping. No discharge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 11/05/2020 | 01:55 PM
07/07/2020 |  | RoutineScheduled | SWP-05-276 | Stafford | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Ecoflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Attached Growth Medium" ,"Control Operation"] | ["Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Attached Growth Medium" ,"Distribution Pump Operation" ,"Control Operation" ,"Effluent Screens" ,"Level Sensor Operation"] | YES | [15 empty] | Will be sent separately | Inspected | Fiberglass unit has cracks; which has been known. Effluent filter housing is broken; need new filter. Proposal to be sent to replace filter. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
12/03/2020 | Alternative | Routine/Scheduled | 166-07-078 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 2.000000 | 2000 | Puraflo |  | Pump | Manifold | Aggregate Bed |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12/03/2020 | 05:00 PM
04/10/2020 |  | Initial Visit | S 800-19-0050 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [9 empty] | 42.000000 | [7 empty] | Serviced system. Checked the pump, panel, & floats (ok). Cleaned filter and diffuser in the Clearstream and cleaned the filter in the aerator. Installed said it is not getting enough pressure - system is not going to a drip so it will not have back pressure on gauge. The pump is working correctly. There is plenty of flow going to the drainfield. The pressure gauge will not shut much pressure because there is no return to restrict the flow. The timer is set to 8 minutes every 1 hour. Took initial BOD sample. NOTE: BOD sample is a little high - system should function properly after service. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 04/10/2020 | Jan 1 1900 12:00PM
11/03/2020 |  | Routine/Scheduled |  | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Gravity | Distribution Box | Gravel-Less Trench | None |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 11/03/2020 | Jan 1 1900 2:00PM
01/31/2020 |  | Routine, Scheduled | 2012-143-0018 | Henrico County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Henrico | [7 empty] | None | Pump | Distribution Box | None | None |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles"] | [18 empty] | [Comments]: A new Norweco aerator was installed to replace the defective "other" branded aerator. The system is now functioning as designed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/10/2020 | 08:38 AM
12/07/2020 |  | RoutineScheduled | 179-14-0233-SWP | Stafford | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"BlowerCompressorAerator Operation" ,"Control Operation" ,"Attached Growth Medium" ,"Auxiliary Filter"] | ["Distribution Pump Operation" ,"Level Sensor Operation" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Control Operation" ,"Dispersal System Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Attached Growth Medium"] | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
04/21/2020 |  | Follow-Up | 124-STS-2379 | Surry | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Crater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | Meet the pumping company and they pumped out the septic tank and the Clearstream. Serviced system. Checked the pump, panel, & floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream, changed the filter in the aerator, changed the mesh screen in the spinfilter, and replaced the alarm light bulb. The timer is set at 6 minutes every 2 hours. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 04/21/2020 | Jan 1 1900 12:00PM
02/18/2020 |  | Routine, Scheduled | 15-160-0026 | Montgomery County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - New River | KING, DAVID A | 1942001094 | DAVID | KING | 2.000000 |  | Delta Environmental Products, DF Series | Septic Tank Only | Gravity | Distribution Box | Aggregate Trench | None |  | ["None"] | ["None"] | [18 empty] | [Comments]: System is working correctly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/18/2020 | 02:27 PM
01/16/2020 |  | Routine, Scheduled |  | Loudoun County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | None | Pump | Distribution Box | Aggregate Trench | [23 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/02/2020 | 04:43 AM
05/18/2020 |  | RoutineScheduled | SD-11-42 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Soils, Inc. | 1940001392 | Markham | Smith | 2.000000 | 1500 | ATU Bio-Mirobics INC Model MicroFast 0.75 |  | Gravity | Gravity | Pad |  |  | [] | ["BlowerCompressorAerator Operation","Attached Growth Medium","SludgeScum Accumulation"] | NA | [17 empty] | Recommended pump-out Compartment 1 sludge 7in Compartment 2sludge 10in | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 07/14/2020 | 03:25 PM
08/14/2020 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump | Drip | Elevated Sand Mound | UV Light |  | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  | 6.85 | 7.860000 | 6.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 08/14/2020 | Jan 1 1900 8:30AM
02/10/2020 |  | Routine, Scheduled |  | Powhatan County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Rejected | EHD - Chesterfield | Madison Environmental LLC |  | Larry | Madison, Jr. |  |  | Biomicrobics MicroFAST | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/10/2020 | Jan 1 1900 1:30AM
09/09/2020 |  | Routine, Scheduled | 175-17-0369 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Biomicrobics MicroFAST |  |  |  |  | UV Light |  | ["Blower/Compressor/Aerator Operation","Disinfection"] | ["Blower/Compressor/Aerator Operation","Disinfection"] |  | Good | Clear | [15 empty] | Spin filter cleaned. Pump Amps 10.05 ETM 473 hrs Cycles 4890 Water Meter Reading 212860 Septic Sludge 15" Scum 2" ATU Sludge 8" Scum 0 Pump Sludge 3" Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 09/09/2020 | 01:26 PM
06/23/2020 | Alternative | Initial Visit | 166-04-183 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | Biomicrobics MicroFAST |  | Pump | Drip | Drip Tubing | None | 750.000000 |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | Musty | Clear | [15 empty] | Pump Tank pumped to operating levels for evaluation. Initial visit for contract - Residence has a sewage lift station in basement - Piggy Back Demand - No audible / visual alarm located. Primary Septic tank in normal operating level MicroFAST - 0.75 FAST unit - blower unit serviced. Discharge tank in high level condition - pumped 750g to evaluate - serviced drip headworks controls and drip screen. Discharge pump operating at higher than normal amperage. Drip field appears to be functioning as designed - air release / vacuum breakers intact and operating - no surfacing noted. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 06/24/2020 | 08:00 AM
08/13/2020 |  | Routine, Scheduled | 175-17-0370 | Prince William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Biomicrobics MicroFAST |  | Pump | Drip | Drip Tubing | UV Light |  | ["Blower/Compressor/Aerator Operation","Disinfection"] | ["Blower/Compressor/Aerator Operation"] |  | Good | Good | [15 empty] | UV Bulb & housing needs replacement. Spin filter cleaned. Pump Amps 10.25 ETM 445 hrs Cycles 1860 Water Meter Reading 177370 Septic Sludge 12" Scum 4" ATU Sludge 14" Scum 0 Pump Sludge 4" Scum 0 | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 08/13/2020 | 11:12 AM
03/12/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Fairfax | SEAMON, CHARLIE L | 1942001108 | CHARLIE | SEAMON |  |  | Septic Tank Only | Microfast | Pump | Manifold | Drip Tubing | None |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | [8 empty] | 03/12/2020 |  | 24.000000 | [5 empty] | Attached to this report |  | [Comments]: Performance Inspection and BOD Sample: Microfast to 3 Zone American Drip. Septic-6"sludge 3"scum/ Microfast-0"sludge/ Pump tank-0"sludge. No pump out needed.Blower air filter cleaned.Counts: Z1-53 ff-8/Z2-52 ff-8/Z3-52 ff-8/Pump-183 ETM-36h 4m/ Peak-17 ETM-1h 50m/High-14 ETM-0/ Water meter-0027044.63/no breakout or spongy area on the field | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/07/2020 | Jan 1 1900 4:41PM
09/17/2020 |  | RoutineScheduled |  | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 6.000000 |  | Septic Tanks | EZ-Treat Recirculation Tanks | Pump | Pressure | Pad | Not Applicable |  | ["Other"] | ["Other"] | NO |  |  |  | 53.800000 | [13 empty] | 3rd Quarter Inspection: Septic Tank#1-10"sludge 12"scum/Septic Tank #2-8"sludge0"scum/Recirc Pump Tank #3-0"sludge Counts: cc1-6763 ETM-96.04 cc2-9101 ETM-95.42/ Recirc Tank #4-6"sludge/Recirc. Tank #5-0"sludge/ Discharge Pump Tank #6-2"sludge Counts: Pump 1-400 ETM-90h 41m Pump 2-380 ETM-86h 32m Peak-12 High-9/ DO-53.8%/ Found inlet tee clogged in the 1st septic tank-unclogged it during inspection. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
01/09/2020 |  | Routine, Scheduled | 033-07-0192-SP | Caroline County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Ware, Michele P | 1942001165 | Michele | Ware |  |  | Septic Tank Only | Septic Tank Only | None | None | None | None |  |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/13/2020 | 04:20 PM
02/25/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Fairfax | Hott, Joshua D. | 1942001301 | Joshua | Hott | 1.000000 | 1875 | Septic Tank Only | Puraflo | Pump | Distribution Box | Aggregate Trench | None |  | ["Effluent Screens"] | ["Effluent Screens"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/27/2020 | Jan 1 1900 8:59AM
04/29/2020 | Alternative |  | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | McKim Construction | 1942001330 | Michelle | McKim | 2.000000 |  |  |  | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 10/23/2020 | 12:00 AM
06/04/2020 |  | Reportable Incident |  | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | [9 empty] | ["Effluent Screens"] | ["Effluent Screens"] | [18 empty] | Had tank pumped out by others and installed a new Zoeller 5000 filter | This AOSS should now return to normal function after having provided the above state routine maintenance. |  |  | 12:00 AM
11/11/2020 |  | RoutineScheduled | SD-09-52 | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC |  | Jason | Brown | 2.000000 | 1500 | Trash tank | Microfast | Gravity | Gravity | Trenches | Not Applicable |  | [] | [] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12/28/2020 | 03:05 PM
06/22/2020 |  | Routine/Scheduled | 2015-143-0130 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | Serviced system. Checked the pump, panel, & floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. The timer is set to 8 minutes every 1 hour. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 06/22/2020 | 12:00 PM
07/29/2020 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  |  | Drip | Elevated Sand Mound | UV Light |  | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  |  | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 07/29/2020 | Jan 1 1900 8:00AM
04/09/2020 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump | Distribution Box | Gravel-Less Trench | None |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  |  | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/09/2020 | Jan 1 1900 11:45AM
02/27/2020 |  | Routine, Scheduled | 234-18-156 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesapeake | VANHOLTEN, CRAIG S | 1934000053 | CRAIG | VANHOLTEN |  |  | Septic Tank Only | Septic Tank Only | None | None | None | None | [11 empty] | 02/27/2020 |  | 9.000000 |  | 13.000000 |  |  |  | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/27/2020 | Jan 1 1900 8:30AM
03/05/2020 |  | Routine, Scheduled |  | Loudoun County | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Paid | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | None | Pump | Distribution Box | Aggregate Bed | [22 empty] | [Comments]: Septic and pump tank need pumped out. The pump tank landscaping needs to be cut back. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 04/12/2020 | 02:21 PM
11/09/2020 |  | Routine/Scheduled | 147-08-0141 | James City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Peninsula | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1250 | Orenco Advantex |  | Pump | Manifold | Aggregate Bed | None | 750.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | None | Clear | [15 empty] | Routine service Primary Septic tank - normal operating level Processing Tank - normal operating level - RSV, Recirc Pump, Effluent screen serviced. Treatment Module (2 present) - media drapes & spray grid serviced. Pump Basin - normal operating level - discharge pump serviced, float sensors & controls operating properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 11/10/2020 | Jan 1 1900 7:30AM
09/02/2020 |  | Routine/Scheduled | 05-120-0723A | Powhatan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Old Dominion Onsite, Inc. | 1942001698 | Robert | Nicholas | [9 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump"] | N/A | [17 empty] | checked float/ pump operation. Cleaned effluent filter. System was pumped out and refilled during the visit | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 09/09/2020 | Jan 1 1900 1:16PM
04/18/2020 |  | RoutineScheduled | 109-05-0545 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 2.000000 | 2000 | Advantex |  | Pump | Gravity | Trenches |  |  | ["None"] | ["None"] | [18 empty] | 20" of solids in first septic tank. Flushed each of the treatment units spray manifolds. Cleaned recirculation basket filter. Tested floats pumps and alarm. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 09/17/2020 | 07:03 PM
02/17/2020 |  | Routine, Scheduled | 02-125-301 | Dickenson County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Cumberland Plateau | DEEL, DENNY M | 1942001097 | DENNY | DEEL |  |  | Norweco Singulair ATU | None | Gravity | None | Alternative Discharge | Chlorine | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens"] |  | Musty | Clear | [15 empty] | [Comments]: 5 blue crystals , 15 biomax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/08/2020 | Jan 1 1900 1:55PM
07/30/2020 |  | Routine/Scheduled | 05-172-0270A | Powhatan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesterfield | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1500 | Orenco Advantex | None | Pump | Distribution Box | Aggregate Trench | None | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | None | Clear | [15 empty] | Annual service conducted. Processing tank at normal operating level - RSV, Effluent Screen & Recirc. pump serviced. AdvanTex Module - media drapes and spray grid serviced. Discharge tank at normal operating level - discharge pump, float sensors and controls operating properly. Surge Box and Distribution box at normal level - removed minor root intrusion - all laterals accepting effluent. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 07/31/2020 | Jan 1 1900 7:00AM
04/29/2020 |  | RoutineScheduled | 06-184-5005 | Scott | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | Septic Inc |  | Denny | Deel |  |  | Norweco |  | Gravity |  | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
03/31/2020 |  | Routine, Scheduled |  | Loudoun County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | Orenco Advantex | None | Gravity | Distribution Box | Gravel-Less Trench | [23 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/12/2020 | 02:21 PM
10/07/2020 |  | RoutineScheduled | {FIPSCode}-STS-30776 | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 2705110225 | Larry | Royston | [9 empty] | ["None"] | ["None"] | YES | [16 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 10/17/2020 | 12:00 AM
04/01/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Fairfax | MAJEWSKI, SHANE | 1934000134 | SHANE | MAJEWSKI | 1.000000 | 1500 | Septic Tank Only | Septic Tank Only | Pump | Distribution Box | Aggregate Trench | None | 750.000000 | ["None"] | ["None"] | [18 empty] | [Comments]: Maintenance Inspection open pods | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/23/2020 | Jan 1 1900 12:51PM
10/01/2020 |  | Routine/Scheduled | 073-STS-94639 | Gloucester | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Three Rivers | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | None | None | Gravity | Distribution Box | Aggregate Trench | None | 450.000000 |  | ["Dispersal System Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | [17 empty] | Septic tank pumped empty for evaluation Distribution box pumped empty for absorption field evaluation Hydraulically overloaded - absorption laterals "bucking" grade - recommend obtain permit for French Drain and/or replace absorption field. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 10/09/2020 | 08:00 AM
08/03/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Payment | EHD - Loudoun | Great Falls Septic Service, Inc | 1942001301 | Josh | Hott | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/27/2021 | 11:51 AM
11/18/2020 |  | RoutineScheduled |  | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - New River | MSS INC |  | Tim | Conner | 1.000000 | Christiansburg | infiltrator |  | Gravity | Gravity | Trenches | Not Applicable |  | ["on"] | ["on"] | YES | Septic | Black | [5 empty] | 11/18/2020 | Sample Chamber | [6 empty] | Attached to this report | Inspected | EVERYTHING FUNCTIONING AT THIS TIME. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12/15/2020 | 12:00 PM
08/14/2020 | Alternative | Routine/Scheduled | 159-12-104 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001063 | K.R. Trapper | Davis | 2.000000 | 4000 | Clearstream | Clearstream | Pump | Distribution Box | Aggregate Trench | None | 2000.000000 |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | Musty | Clear | [15 empty] | Pumped one clearstream unit - refilled with fresh water. Routine service conducted. Primary septic tank (Chinese?) at normal level - effluent screen serviced. Secondary septic tank (Bank) - at normal level - effluent screen serviced. Flow Equalization Tanks - at normal levels - pump, float sensors and controls operating properly. Dual Clearstream units - compressors serviced - units pumped empty for service and refilled with fresh water. Discharge tank - normal operating level - pump, float sensors and controls operating properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 08/17/2020 | 08:00 AM
08/20/2020 |  | Routine/Scheduled | 07-120-0593A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesterfield | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1500 | Orenco Advantex | None | Pump | Drip | Drip Tubing | None | 600.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | None | Clear | [15 empty] | Routine service conducted. Processing tank - normal operating level - RSV, Recirc. Pump, effluent screen serviced. Treatment Module - media drapes and spray grid serviced. Discharge tank - discharge pump serviced, float sensors and controls operating properly. Drip Manual headworks - field flushed - drip screen serviced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 08/27/2020 | Jan 1 1900 7:00AM
09/23/2020 |  | Routine/Scheduled | 03-190-105 | Surry | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Crater | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1500 | Norweco Singulair ATU |  | Pump | Distribution Box | Aggregate Trench | None | 450.000000 |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | Musty | Clear | [15 empty] | Routine Service Trash Tank - normal operating level Aeration Tank - normal operating level - aspirator serviced Clarifier - normal operating level - effluent screen serviced Discharge tank - pump, float sensors and controls operating properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 10/05/2020 | Jan 1 1900 1:00PM
03/19/2020 |  | Initial Visit | 2018-143-0107 | Henrico County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Henrico |  |  |  |  | 1.000000 | 1250 |  | None | Pump | Manifold | Gravel-Less Bed | None | 450.000000 | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [18 empty] | [Comments]: Unit is PuraSys SBR Recirculation pump = SBR sludge pump Sludge = 3" Scum = 0 Excessive amount of diapers & wipes in system | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/25/2020 | 08:37 AM
03/27/2020 |  | Routine, Scheduled | 179-12-0201-SWP | Stafford County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Orenco Advantex | None | Pump | Drip | Drip Tubing |  |  | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | [18 empty] | [Comments]: Vacuumed recic. vault. Replaced RO flat in Recirc. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/01/2020 | 06:33 AM
03/02/2020 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 | Approved | EHD - Loudoun | Eco Virginia | 1942001235 | William | Poindexter | 1.000000 |  | none | none | Gravity | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Disinfection"] | ["BlowerCompressorAerator Operation" ,"Disinfection" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced UV unit. | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 |  | 06/03/2021 | 05:53 AM
06/12/2020 |  | Routine/Scheduled | 02-160-0103 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Orenco Advantex |  | Gravity | Distribution Box | Aggregate Trench | None |  | ["None"] | ["Control Operation","Level Sensor (Float) Operation","Recirculation Pump","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 06/12/2020 | 09:00 AM
09/21/2020 | Alternative | RoutineScheduled | 166-18-0156 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
04/18/2020 |  | RoutineScheduled | SD-99-382 | Culpeper | This AOSS is not functioning as designed or in acc | Approved | EHD - Rappahannock-Rapidan | Wastemaster | 1965004241 | Douglas | Crooks | 1.000000 |  |  |  | Discharge | Drip |  | Chlorine |  | [] | [] |  | Low | Clear | 7.800000 | 5.400000 |  |  |  | 04/18/2020 |  |  | 2.800000 |  | 2.000000 |  |  | Will be sent separately |  | Functioning as Designed | This AOSS is not functioning as designed or in acc |  |  | 12:00 AM
06/25/2020 |  | Reportable Incident | 05-142-0093A | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1500 | Orenco Advantex |  | Pump | Distribution Box | Aggregate Trench | None | 450.000000 | ["Attached Growth Medium","Control Operation"] | ["Control Operation"] | NA | [17 empty] | Responded to owner request due to control panel alarming ... last documented service from 2017 ... Owner has "other" service provider - name not provided - contacted Miller's Services due to "other" service provider not responding. Found that system was alarming low level from pumpout by unknown company and not refilled as recommended by manufacturer. Owner allowing system to refill on own, and will consider resuming service with Miller's ... | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 06/26/2020 | Jan 1 1900 8:00AM
09/01/2020 |  | RoutineScheduled | 175-14-0234 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/Microfast | Pump Tank | Pump | Pressure | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","SludgeScum Accumulation","Attached Growth Medium"] | ["BlowerCompressorAerator Operation"] | NA | [7 empty] | 09/01/2020 | Sample Chamber | 10.000000 | [5 empty] | Attached to this report |  | Septic-12"sludge 2"scum/Microfast-18"sludge (Requires pump out and spray media) Pump Tank-1"sludge/ Blower air filter cleaned. Pump counts-26775 ETM-555.82/ No ponding or spongy area on the drainfield. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  |  | 12:00 AM
09/14/2020 |  | RoutineScheduled | 107-08-0069 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Onsite Wastewater Services - May Supply | 1942001627 | Drew | Shull | 1.000000 |  | Orenco Advantex | none | Pump | Gravity |  | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 05/28/2021 | 05:41 AM
02/27/2020 |  | Routine, Scheduled |  | Albemarle County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Blue Ridge | CLARK, MICHAEL J | 1934000023 | MICHAEL | CLARK |  |  | Septic Tank Only | Septic Tank Only | None | None | None | None |  |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/17/2020 | 05:07 AM
10/26/2020 |  | RoutineScheduled | 179-10-0005-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump" ,"Attached Growth Medium"] | ["Effluent Screens" ,"Recirculation Pump" ,"Attached Growth Medium" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | YES | [15 empty] | Will be sent separately | Inspected | Roots were observed growing into the ratio box & distribution box. Owner will remove roots. | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 |  | 04/09/2021 | 03:25 PM
08/10/2020 | Alternative | Routine/Scheduled | 151-03-430 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | Orenco Advantex | None | Pump | Drip | Drip Tubing | None | 600.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | None | Clear | [15 empty] | Annual service conducted. Processing tank - normal operating level - RSV, Effluent screen & Recirc. pump serviced. AdvanTex Module - media drapes serviced - spray grid serviced. Discharge tank - normal operating level - discharge pump serviced, float sensors and controls operating properly. Drip Headworks - drip screen serviced - drip field walked - no indication of surfacing noted. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 08/12/2020 | 10:00 AM
01/02/2020 |  | Reportable Incident | 177-07-0196-SWP | Spotsylvania County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Biomicrobics MicroFAST | None | Pump | Distribution Box |  |  |  | ["Control Operation","Distribution Pump Operation"] | ["Control Operation","Distribution Pump Operation"] | [18 empty] | [Comments]: High level alarm. Pump not pumping, pulling high amps. Installed slightly stronger pump, new check valve, gate valve and camlock. New pump did 2" in 2 minutes (approximately 22.5 gpm). | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/15/2020 | 10:52 AM
08/05/2020 | Alternative | RoutineScheduled | 171-04-0079 | Shenandoah | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Lord Fairfax | [6 empty] | Fast | [6 empty] | ["Control Operation","Dispersal System Operation"] | ["Control Operation","Dispersal System Operation"] | [19 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 08/05/2020 | 12:00 AM
03/20/2020 |  | Routine, Scheduled | 171-15-0211 | Pittsylvania County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Pittsylvania-Danville | WAUGH, IAIN C | 1942001512 | IAIN | WAUGH | 1.000000 | 1000 | Septic Tank Only | Orenco Advantex | Pump | Distribution Box | Aggregate Trench | None |  | ["Attached Growth Medium","Control Operation","Effluent Screens"] | ["Attached Growth Medium","Control Operation","Effluent Screens"] | [18 empty] | [Pumpout Comments]: Not needed [Comments]: Septic Tank 2-3" Scum 10" Sludge Recirc Zone 6" Sludge- Discharge zone 12" Sludge Set Recirculation pump Off time for two Occupants to 30 min(19.5) pump recirc run time to 45sec ON (from 30), Checked 6 Floats & vocal alarm- Good RTU#134250 Connected to monitoring, only high usage alarms from few large family gathering | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/20/2020 | 08:46 PM
01/31/2020 |  | Routine, Scheduled | 033-06-0507-SP | Caroline County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | None | Pump | Distribution Box | Aggregate Trench |  |  | ["Attached Growth Medium","None","Recirculation Pump"] | ["Attached Growth Medium","None","Recirculation Pump"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/02/2020 | 11:52 AM
02/24/2020 |  | Routine, Scheduled | 177-06-0671-SWP | Spotsylvania County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | None | Pump | Distribution Box | Aggregate Trench |  |  | ["Attached Growth Medium","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Recirculation Pump"] | ["Attached Growth Medium","Distribution Pump Operation","Effluent Screens","Recirculation Pump"] | [18 empty] | [Comments]: We recommend mowing the drainfield & maintaining it in a mowed condition. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/06/2020 | 02:45 PM
04/13/2020 |  | RoutineScheduled | 107-99-0683 (LEGACY ALT. SYSTEM) | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Gravity | Gravity | Trenches | Not Applicable |  | ["None"] | ["None"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 06/03/2021 | 12:00 AM
09/01/2020 |  |  | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 1.000000 |  | Septic/Microfast |  | Gravity | Gravity | Trenches | Not Applicable |  | ["SludgeScum Accumulation"] | [] | NA | [17 empty] | Septic-13"sludge 10"scum/ Microfast-13"sludge. Requires pump out due to sludge levels and clogging of the media.Blower air filter cleaned.Noted: leak on inlet side of septic tank riser,Tree located on the drainfield needs to be removed. All done on 7/10 | This AOSS should now return to normal function after having provided the above state routine maintenance. |  |  | 12:00 AM
12/05/2020 |  | RoutineScheduled | -STS-20164 | Prince William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Prince William | Wastemaster Inc |  | Timothy | Jenkins | 2.000000 |  | Recirculating Sand Filter |  | Pump | Gravity | Discharge | Chlorination |  | [] | [] |  | Musty | Clear | 7.000000 |  |  | 2.200000 | [11 empty] | #1 Pump on constantly | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. |  |  | 02:00 PM
03/06/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Paid | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Biomicrobics MicroFAST | [6 empty] | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] |  | Good | Good | [15 empty] | [Comments]: Spin filter cleaned.UV light is bad.Water ponding at D/F toe.Pump 1 Amps 9.85 ETM 168h 34m Cycles 1274Water Meter Reading 88700Septic Sludge 5" Scum 2"ATU Sludge 11" Scum 0Pump Sludge 0.50 Scum 0 | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 03/06/2020 | Jan 1 1900 2:40PM
07/30/2020 |  | RoutineScheduled | 09-113-003 | Buchanan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
04/08/2020 |  | RoutineScheduled | {FIPSCode}-STS-19569 | Frederick | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Lord Fairfax | Onsite Wastewater Services - May Supply | 1942001022 | Sara | Tusing | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/28/2021 | 05:41 AM
07/23/2020 |  | RoutineScheduled |  | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/Microfast | Pump Tank | Pump | Pressure | Drip | UV |  | ["Attached Growth Medium","SludgeScum Accumulation","BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [17 empty] | Septic Tank-10"sludge 4"scum/Microfast-14"sludge (Microfast needs pump out and sprayed) Pump Tank-2"sludge/ Blower air filter cleaned. Counts: Zone 1-1664 ff-58/Zone 2-1664 ff-58/Pump-3443 ETM-525h 46m/Peak-1 ETM-0/High-3 ETM-0/ Water meter-0274848.82 | This AOSS should now return to normal function after having provided the above state routine maintenance. |  |  | 12:00 AM
10/23/2020 |  | RoutineScheduled | 2011-143-0016 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Onsite Maintenance Team | 1942001039 | Corey | Braxton | 3.000000 |  | Norweco Singulair |  | Pump | Gravity | Trenches |  | 1000.000000 | [] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation"] | YES | Musty | Clear | 7.100000 | 2.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
01/21/2020 |  | Routine, Scheduled |  | Loudoun County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | None | None | Gravity | [24 empty] | [Comments]: Sale inspection on a conventional gravity septic system. The sewer line was camera snaked. The septic tank was inspected for any leaks or cracks. The 7 port plastic d-box was dug up it was 18" under the ground. The 3 header lines were camera snaked and the drain field probed. At time of inspection all components were in working condition. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/02/2020 | 04:43 AM
04/14/2020 |  | RoutineScheduled |  | Warren | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Review | EHD - Lord Fairfax | Greenway Engineering | 1942001008 | Jeremy | Ferguson | 1.000000 | 1800 | Aquarobic Mini Plant | none | Pump | Pressure | Mound | Not Applicable |  | ["BlowerCompressorAerator Operation"] | [] | NA | [17 empty] | Blower is bad and needs replaced. System is not operational. Also needs pumped out. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. |  | 07/21/2020 | 03:20 PM
09/30/2020 |  | Routine, Scheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Clearstream ATU |  |  |  |  | UV Light |  | ["Blower/Compressor/Aerator Operation","Disinfection"] | ["Blower/Compressor/Aerator Operation","Disinfection"] |  | Acceptable | Clear | [15 empty] | Spin filter cleaned. Pump Amps 9.45 Septic Sludge 4" Scum 2" ATU Sludge 0 Scum 2" Pump Sludge 4" Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 09/30/2020 | Jan 1 1900 11:08AM
12/09/2020 |  | Routine/Scheduled | 2010-143-0125 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Old Dominion Onsite, Inc. | 1942001549 | Russell | Revis | [9 empty] | ["Blower/Compressor/Aerator Operation","Control Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | Replaced air filter. Checked float, pump, and blower function. System appears to be working normally. Sludge judged aeration tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12/09/2020 | 11:15 AM
03/13/2020 |  | Routine, Scheduled |  | Caroline County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Rappahannock | Ware, Michele P | 1942001165 | Michele | Ware |  |  | Septic Tank Only | Septic Tank Only | None | None | None | None |  |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/25/2020 | 02:51 PM
04/15/2020 | Alternative | Routine/Scheduled | 157-13-0074 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | Serviced system. Checked the pump, panel, & floats (ok). Cleaned the filter in the Clearstream and cleaned the filter in the septic tank. Changed the diffuser in the Clearstream, changed the filter in the aerator, and replaced the alarm float in the Clearstream. There is a 12" riser and top by the tanks that has nothing under it. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 04/15/2020 | 12:00 PM
04/08/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | SES MidAtlantic LLC | 1942001203 | James | Green | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity |  | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/15/2021 | 09:00 AM
03/16/2020 |  | Reportable Incident |  | King William County | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Paid | EHD - Three Rivers | Farmer’s Septic Service, Inc. |  | Ross | Cole | 1.000000 | [28 empty] | [Comments]: Owner called due to there being water by the tanks. Alarm float is bad - common wire from panel was nicked and corroded - repaired it. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 03/16/2020 | 12:00 PM
12/10/2020 |  | RoutineScheduled | 107-13-0324 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter | [9 empty] | ["Distribution Pump Operation"] | ["Distribution Pump Operation"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 06/02/2021 | 12:00 AM
04/14/2020 |  | Routine, Scheduled | 14-142-0065 | Hanover County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chickahominy | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Ecoflo | None | Pump | Distribution Box | Aggregate Trench |  |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [18 empty] | [Comments]: Recommend homeowner have water softener discharge taken off of septic. Pump line settled and broken riser, no water leaking in at this time. Roots at inlet wedge lid on septic tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/27/2020 | Jan 1 1900 4:14AM
01/20/2020 |  | RoutineScheduled | 033-14-0103-SWP | Caroline | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Refiled to correct error in previous report filed. | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 |  | 04/09/2021 | 03:25 PM
05/11/2020 |  | RoutineScheduled |  | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 2705051738 | Joshua | Hott |  | 1875 | [7 empty] | ["Effluent Screens"] | ["Effluent Screens"] | YES | [17 empty] | Needs plumbing work and all pods need to be lifted up and trenches need to be dug and gravel placed in trenches. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. |  |  | 12:00 AM
11/13/2020 |  | RoutineScheduled | 06-184-5005 | Scott | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Effluent Screens"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Effluent Screens"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
12/29/2020 |  |  | VAG400175 | Tazewell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 12/29/2020 |  | 19.400000 |  |  | 2.200000 |  |  | Attached to this report |  | BOD: 19.4 TSS: 2.20 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12/29/2020 | Jan 1 1900 12:30PM
05/21/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/27/2021 | 01:26 PM
11/21/2020 |  | RoutineScheduled | -STS-20169 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Wastemaster Inc |  | Timothy | Jenkins |  |  | Sequencing Bat Reactor |  |  |  | Discharge | Chlorination |  | [] | [] |  | Musty | Clear | 7.500000 |  |  | 2.200000 | [12 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:55 PM
02/28/2020 |  | Routine, Scheduled | 11-125-010 | Dickenson County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Cumberland Plateau | DEEL, DENNY M | 1942001097 | DENNY | DEEL |  |  | Norweco Singulair ATU | None | Pump | Drip | Drip Tubing | None | 200.000000 | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump"] |  | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/03/2020 | Jan 1 1900 10:26AM
06/15/2020 |  | RoutineScheduled | 05-142-0274 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1500 | Orenco Advantex | None | Pump | Gravity | Trenches | Not Applicable |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump","Septic Tank Baffles","Sludge/Scum Accumulation"] | NA | [17 empty] | The Processing Tank was found below normal level upon arrival, and may be due to a fractured Return Line between the Processing Tank and the Advantex Media Unit, the Recirculation Pump is near its end of life, the Floats have exceeded their expected life, and the Riser Lid has deteriorated; the Hinges on the Advantex Media Unit Lid & the support Struts have failed, and the Vent Stack has damage; the Discharge Tank Floats have exceeded their expected life; the Control Panel is near the end of its life; Homeowner has approved all repairs 06/22/2020 - Excavated and repaired conveyance line between processing tank. Replaced controls with new - | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 06/16/2020 | Jan 1 1900 2:40PM
04/10/2020 |  | Routine/Scheduled | 02-163-0065 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chickahominy | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1250 | Clearstream ATU | None | Pump | Distribution Box | Aggregate Trench | None |  |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | The Air Line in the Aeration Tank is not serviceable (as a result, the Diffuser could not be serviced), and the Riser had root infiltration; the Air Pump was not functioning; Distribution Box had roots growing in under the Lid | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/13/2020 | Jan 1 1900 1:13PM
08/19/2020 |  | RoutineScheduled |  | Rockingham | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [7 empty] | 08/19/2020 |  | 17.000000 | [5 empty] | Will be sent separately | Inspected | Lab Sample Normal | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/26/2021 | 09:04 AM
03/06/2020 |  | Routine, Scheduled |  | Loudoun County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | None | None | Pump | Distribution Box | Gravel-Less Trench | [22 empty] | [Comments]: The pump union was loose and leaking slightly. It was tightened at time of inspection. There is a small crack on the Eco Pod lid, It was sealed with silicone. Recommend the homeowner monitors it to ensure it does not become larger. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/16/2020 | 11:28 AM
05/14/2020 |  | Routine, Scheduled | 175-17-0583 | Prince William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Biomicrobics MicroFAST |  |  |  |  | None |  | ["Blower/Compressor/Aerator Operation","Dispersal System Operation"] | ["Blower/Compressor/Aerator Operation"] |  | Good | Good | [15 empty] | Spin filter cleaned. Pump Amps 11.24 ETM 163 h 22 m Cycles 1733 Water Meter Reading 152290 Septic Sludge 11" Scum 0.50 ATU Sludge 14" Scum 0 Pump Sludge 1" Scum 0 D/F area wet. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 05/14/2020 | 12:26 PM
10/12/2020 |  | RoutineScheduled | SD-03-189 | Madison | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC |  | Jason | Brown | 1.000000 | 1250 gallons | trash tank | Microfast | Gravity | Gravity | Discharge | Chlorination |  | [] | [] | NA | Musty | Clear | 7.000000 |  |  | 1.200000 |  | 10/12/2020 | Sample Chamber | 2.000000 | 1.200000 | 0.000000 | 15.500000 |  |  | Attached to this report |  | Tank needs pumping I let homeowner know | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 10/29/2020 | 03:25 PM
12/09/2020 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | A inspection was done on a conventional pump septic system. The state requires that all conventional septic tanks must be pumped out every 5 years and filed with the state and county. The septic control panel is an interior demand dose. The sewer line was camera snaked and was clear. The septic tank lid was dug up it was 24 inches under the ground. The septic tank was pumped out and inspected for any leaks or cracks none were found. The pump tank, pump, floats and force main were inspected. The 8 port concrete d-box was dug up it was 2 feet below the surface. All 3 header lines were camera snaked and the drain field was probed. At time of inspection all components were in working condition. | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 |  | 04/14/2021 | 04:27 PM
02/10/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS should now return to normal function after having provided the above stated routine maintenance. | Paid | EHD - Fairfax | SEAMON, CHARLIE L | 1942001108 | CHARLIE | SEAMON |  |  | Septic Tank Only | EcoPod | Pump | Distribution Box | Aggregate Trench | None |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | [8 empty] | 02/10/2020 |  | 147.000000 | [5 empty] | Attached to this report |  | [Comments]: Performance Inspection and Sample: Ecopod to Drainfield. Septic-4"sludge 3"scum/Ecopod-6"sludge Pump tank-2"sludge. No pump out needed at this time. Service call on 2/3/2020 found all floats and blower were faulty, replaced on 2/10/2020. P1 cnts-2537 ETM-43h 24m/P2 cnts-2615 ETM-42h 23m/ Peak-7039/High-2432/Drainfield area good. | This AOSS should now return to normal function after having provided the above stated routine maintenance. |  | 04/07/2020 | Jan 1 1900 5:33AM
10/13/2020 | Alternative | RoutineScheduled | 124-STS-2379 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Chickahominy | GeoEnvironmental Services, Inc. | 1942001010 | Peter | Mamunes | 1.000000 | 1250 | Clearstream ATU |  | Pump | Pressure | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["SludgeScum Accumulation","Effluent Screens","Level Sensor Operation","Distribution Pump Operation","Dispersal System Operation","Control Operation","BlowerCompressorAerator Operation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 10/13/2020 | Dec 30 1899 1:30PM
07/25/2020 |  | RoutineScheduled | {FIPSCode}-STS-17837 | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Wastemaster Inc |  | Timothy | Jenkins | 2.000000 |  | ATU |  | Gravity | Gravity | Discharge | Chlorination |  | [] | [] |  | Musty | Clear | 7.400000 |  | 45.000000 | 2.200000 | [12 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 08/03/2020 | 02:50 PM
09/08/2020 |  | Reportable Incident | 136-06-0511 | Gloucester | This AOSS should now return to normal function after having provided the above state routine maintenance | Approved | EHD - Three Rivers | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1500 | Biomicrobics MicroFAST | None | Pump | Distribution Box | Aggregate Trench | None | 450.000000 |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | Pungent | Discolored | [15 empty] | Pumpout to effect repairs / correct alarm condition. Alarm - no documented service since 2017 - No Service Agreement in place. Trash Tank - removed solids from top Aeration - Air line fractured - Repaired - Rotary Compressor serviced. Discharge Tank - Discharge pump failure - pump replaced like for like - discharge tank pumped to mid point for repairs. Distribution box intact and at normal level. | This AOSS should now return to normal function after having provided the above state routine maintenance |  | 09/09/2020 | 07:45 AM
06/13/2020 |  | RoutineScheduled | 2037-96-153 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Wastemaster Inc |  | Timothy | Jenkins | 2.000000 |  | Recirculating Sand Filter |  | Pump | Gravity | Discharge | Chlorination |  | [] | [] |  | Musty | Clear | 6.400000 | 5.600000 |  | 1.700000 |  | 06/13/2020 |  | 13.000000 |  |  | 10.400000 |  |  | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 06/29/2020 | 05:35 PM
09/01/2020 |  | Reportable Incident | 175-13-0295 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | [9 empty] | ["Other"] | ["Other"] | [18 empty] | Service call: Leaking riser (30") on the pump tank. Sealed the riser at the point where the riser is placed in the pouring of the tank interface. Counts: Pump-8959/High-15/ Hand -7 | This AOSS should now return to normal function after having provided the above state routine maintenance. |  |  | 12:00 AM
08/12/2020 |  | RoutineScheduled | 17-120-0326AR | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Stamie E. Lyttle Co. | 1942001470 | Eric | Tambourine | [9 empty] | [] | [] | [19 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 08/12/2020 | 12:00 AM
07/15/2020 |  | RoutineScheduled |  | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Rappahannock | Wastemaster Inc |  | Timothy | Jenkins | 2.000000 |  | PuraFlo |  | Pump | Gravity | Discharge | UV |  | [] | ["Disinfection"] |  |  |  | 7.000000 | [14 empty] | Replaced UV Bulb | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 08/27/2020 | 03:50 PM
01/13/2020 |  | Routine, Scheduled |  | Louisa County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Blue Ridge | CLARK, MICHAEL J | 1934000023 | MICHAEL | CLARK |  |  | Septic Tank Only | Septic Tank Only | None | None | None | None |  |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/14/2020 | 03:19 AM
05/14/2020 |  | RoutineScheduled | 107-09-0308 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Onsite Wastewater Services - May Supply | 1942001022 | Sara | Tusing | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | INSPECTION BY DS | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 05/28/2021 | 05:41 AM
07/09/2020 |  | Routine, Scheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Puraflo |  |  |  |  | None |  | ["Effluent Screens"] | ["Effluent Screens"] | [18 empty] | Pump 1 Amps 13.80 ETM 783.83 Cycles 60960 Pump 2 Amps 12.99 ETM 1049.47 Cycles 74746 Septic Sludge 11" Scum 0.50 Pump Sludge 2" Scum 0 Strongly recommend BOD Sampling for Puraflo's ponding. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 07/09/2020 | Jan 1 1900 12:00PM
11/23/2020 |  | RoutineScheduled | 139-06-0542 | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | [6 empty] | Puraflo |  | Gravity | Gravity | Trenches |  |  | ["Attached Growth Medium","Septic Tank Baffles","Dispersal System Operation"] | ["Attached Growth Medium","Septic Tank Baffles","Dispersal System Operation"] | [18 empty] | repair sample box | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 11/23/2020 | 12:00 AM
05/12/2020 |  | RoutineScheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | R.H. Combs & Sons Excvating | 1942001353 | RUSSELL | COMBS | 2.000000 | 1000 |  |  | Pump | Pressure | Drip | Not Applicable | 450.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation"] | YES | None | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12/18/2020 | 12:00 PM
06/12/2020 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintanence requirements | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | septic tank needs pumped out | This AOSS is not functioning as designed or in accordance with the performance/maintanence requirements |  | 04/14/2021 | 04:27 PM
01/30/2020 |  | Routine, Scheduled |  | Fluvanna County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Blue Ridge | CLARK, MICHAEL J | 1934000023 | MICHAEL | CLARK |  |  | Septic Tank Only | Septic Tank Only | None | None | None | None |  |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/09/2020 | 04:55 AM
08/07/2020 |  | RoutineScheduled | 182-94-0418 (LEGACY ALT. SYSTEM) | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter | [9 empty] | ["None"] | ["None"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 06/02/2021 | 12:00 AM
09/28/2020 |  | Reportable Incident | JASN-A6EKJF | Suffolk | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | Owner called due to the aerator not running. Serviced system. Checked the pump, panel, & floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream, changed the filter in the aerator, and changed the mesh screen in the spinfilter. Installed a re-build kit on the aerator. Return line runs to the Clearstream not the septic tank. The UV is not working - blowing fuses - probably needs a new ballast, bulb, and cord. The septic tank needs additional risers on it so it can be properly inspected in the future. The timer is set to 7 minutes every 1 hour. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. |  | 09/28/2020 | Jan 1 1900 12:00PM
03/03/2020 |  | RoutineScheduled |  | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | FIVE STAR SEPTIC INC | 1944001248 | AARON | GOINS | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 03/19/2020 | 12:00 AM
02/26/2020 |  | Routine, Scheduled | 179-13-0235-SP | Stafford County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Clearstream |  |  |  |  | None |  | ["BlowerCompressorAerator Operation","Effluent Screens"] | ["Effluent Screens"] |  | Good | Clear | [15 empty] | [Comments]: Septic Sludge 4" Scum 2"ATU Sludge 0 Scum 1" | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/26/2020 | 11:32 AM
02/14/2020 |  | Routine, Scheduled |  | Loudoun County | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Paid | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | Delta Environmental Products, DF Series | None | Pump | Drip | Drip Tubing | [22 empty] | [Comments]: Sale inspection on a alternative drip septic system. This septic system is required by law to be inspected every year between January 1 to july 1. The septic control panel is a exterior timed dose. There are 2 clean outs from house to the septic tank. The septic tank was pumped out and inspected for any leaks. There is a plastic riser on the outlet side of the tank. The atu tank and air blower are in working condition. The pump tank, pump, floats and force main were inspected. The hydraulic unit, flag heater and water meter were inspected. The manifold for zone 2 is broken and will need to be fixed. At this time the septic system is not in working condition | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 03/02/2020 | 04:43 AM
09/30/2020 |  |  |  | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic Tank | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [17 empty] | Septic tank-6"sludge 0"scum/ Pump tank-2"sludge (No pump out needed at this time) Cleaned septic filter/ Counts: Pump1-5010 ETM-61h 55m/ Pump2-4976 ETM-61h 35m/Peak-28/ High-7/ No breakout or spongy areas on the drainfield. Puraflo peat in good condition and was fluffed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
07/02/2020 |  | RoutineScheduled | 139-05-0105 | Greene | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Blue Ridge | Onsite Wastewater Services - May Supply | 1942001022 | Sara | Tusing | 1.000000 |  | Whitewater ATU | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | INSPECTION BY DS | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/28/2021 | 05:41 AM
04/23/2020 |  | RoutineScheduled |  | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 | 1500 |  | ME-1500 | Pump | Gravity | Trenches | Not Applicable |  | ["None"] | ["None"] | NO | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 06/29/2020 | 12:00 AM
12/07/2020 |  | RoutineScheduled | 14-197-A2 | Wise | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | MULTIFLO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","Disinfection"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
05/27/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | EcoPod | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Septic tank has lots of rags and other debris in it. This is a reoccurring issue. The filter was clogged and the level was high. Recommend pumping the septic tank and distribution box. Also recommend adding a tee to the inlet of the distribution box to slow the flow and avoid the effluent going straight across and into one line. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/27/2021 | 01:26 PM
06/26/2020 |  | RoutineScheduled | 179-13-0259-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions |  | Michele | Ware | [9 empty] | [] | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 06/26/2020 | 12:00 AM
01/24/2020 |  | Initial Visit | 228-18-0153 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Virginia Beach |  |  |  |  | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [10 empty] | 30.000000 | [7 empty] | [Comments]: Serviced system. Checked the pump, panel, & floats (ok). Cleaned the filter in the Clearstream, cleaned the filter in the aerator, and cleaned the filter in the septic tank. Changed the diffuser in the Clearstream. The pressure switch on the aerator is not hooked up. The septic tank has no inlet tee - need to install one. The timer is set to 2 minutes every 2.25 hours. Took initial BOD sample. NOTE: The BOD sample was a little high - system should function properly after service. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/24/2020 | Jan 1 1900 12:00PM
09/24/2020 |  | Routine/Scheduled | S800-18-0323 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Western Tidewater | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | None | None | Pump | Distribution Box | Aggregate Trench | None | 450.000000 |  | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | [17 empty] | COSS - Routine Service - Alarm Septic tank in high level due to effluent screen clog causing back-up and slow drain in residence - effluent screen serviced. Pump tank - normal operating level - pump, float sensors and controls operating properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 10/06/2020 | Jan 1 1900 7:30AM
06/09/2020 | Alternative | RoutineScheduled | 128.13.0086 | Essex | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Three Rivers |  |  | joel | pinnix | [9 empty] | [] | [] | [18 empty] | MicroFAST unit installed backwards - dating back to 2013. Non-functional - no aeration. Septic effluent passing through to drainfield dosing pump tank. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. |  |  | 12:00 AM
03/23/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Paid | EHD - Fairfax | MCKIM, STEPHEN E | 1934000043 | STEPHEN | MCKIM |  |  | Septic Tank Only | Septic Tank Only | None | None | None | None |  | ["SludgeScum Accumulation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | [18 empty] | [Comments]: Septic/Atu needs pumped out | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 04/20/2020 | Jan 1 1900 10:33AM
02/11/2020 |  | Routine, Scheduled | C-07-111-0053 | Botetourt County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Alleghany-Roanoke | AYRES, HUNTER E | 1942001166 | HUNTER | AYRES | 1.000000 | 1000 | Septic Tank Only | None | Pump | Manifold | Alternative Discharge | None |  | ["None"] | ["None"] | [18 empty] | [Comments]: Filter checked and cleaned. Control panel functioning properly. System did not need to be pumped. No apparent leaks in system or drain field area. Lids properly secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/11/2020 | Jan 1 1900 8:11PM
05/18/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | SES MidAtlantic LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Dispersal System Operation" ,"Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. LPD lines were soft. System recheck 06/16/2020 | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 |  | 04/15/2021 | 09:00 AM
04/07/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Loudoun | SES MidAtlantic LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. Strongly recommend BOD sample be taken for Puraflo modules. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/15/2021 | 09:00 AM
08/31/2020 |  | Routine, Scheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Biomicrobics MicroFAST |  | Pump | Drip | Drip Tubing | UV Light |  | ["Blower/Compressor/Aerator Operation"] | ["Blower/Compressor/Aerator Operation"] |  | Acceptable | Clear | [15 empty] | Spin filter cleaned. Pump Amps 9.03 ETM 647 hrs Cycles 5184 Water Meter Reading 298500 Septic Sludge 13" Scum 0.25 ATU Sludge 15" Scum 0 Pump Sludge 2" Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 08/31/2020 | Jan 1 1900 9:10AM
02/14/2020 |  | Routine, Scheduled | NYII-B9RNK3 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesapeake | R & K Septic, Inc. |  | John | Butt, Jr |  |  | Clearstream ATU |  | Pump | Drip | Elevated Sand Mound | UV Light |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] |  |  | 2.57 | 7.910000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/14/2020 | Jan 1 1900 11:45AM
08/01/2020 |  | RoutineScheduled | 2044-02-153 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Wastemaster Inc |  | Timothy | Jenkins | 2.000000 |  | PuraFlo |  | Pump | Gravity | Discharge | Chlorination |  | [] | [] |  | Musty | Clear | 7.500000 |  |  | 2.200000 | [12 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 09/02/2020 | 02:00 PM
06/04/2020 |  |  | 069051106 | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | ["None"] | ["None"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 07/28/2020 | 12:00 AM
12/15/2020 |  | Follow-Up | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance | Approved | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green | [9 empty] | ["Dispersal System Operation"] | ["Dispersal System Operation"] | [18 empty] | Repaired broken Air Release Valve. | This AOSS should now return to normal function after having provided the above state routine maintenance |  | 12/15/2020 | Jan 1 1900 4:00PM
05/15/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/14/2021 | 04:27 PM
11/05/2020 |  | RoutineScheduled | 179-06-0036-SWP | Stafford | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Attached Growth Medium" ,"Control Operation"] | ["Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Attached Growth Medium" ,"Control Operation"] | YES | [15 empty] | Will be sent separately | Inspected | Pump (outside - time-dosed) max amps is 12. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
06/22/2020 |  | Routine/Scheduled | 06-120-0042A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesterfield | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1500 | Orenco Advantex |  | Pump | Manifold | Spray Irrigation | UV Light | 600.000000 |  | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | None | clear | [15 empty] | Routine service conducted. Processing tank in normal operating level - Recirculating Splitter Valve serviced - Effluent screen serviced - Recirculation pump serviced and operating properly. AdvanTex - media and distribution spray grid serviced. UV Disinfection unit serviced - bulb and crystal serviced. Discharge tank in normal operating level - discharge pump serviced. Spray field walked over - spray heads appear to be functioning properly in proper spray pattern. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 06/23/2020 | Jan 1 1900 8:15AM
01/06/2020 |  | Routine, Scheduled |  | Essex County | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Paid | EHD - Three Rivers | PINNIX, JOEL S | 1934000193 | JOEL | PINNIX |  |  | Septic Tank Only | Septic Tank Only | None | None | None | None | [21 empty] | [Comments]: Approx 2/3’s of drip emitters clogged resulting on localized flooding of drainfield. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 01/13/2020 | 03:33 PM
03/16/2020 |  | Routine, Scheduled |  | Greene County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Blue Ridge | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Biomicrobics MicroFAST | None | Gravity | Distribution Box | Aggregate Trench |  |  | ["Attached Growth Medium","BlowerCompressorAerator Operation","None","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","None"] | [18 empty] | [Comments]: We recommend pumping the ATU and the Septic Tank due to solids accumulation.We also recommend replacing the air filter for the blower motor. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/06/2020 | 02:46 PM
10/13/2020 | Alternative | Routine/Scheduled | 166-12-109 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 3.000000 | 2600 | Clearstream |  | Pump | Distribution Box | Aggregate Trench |  |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 10/13/2020 | 02:30 PM
04/16/2020 | Alternative | Routine/Scheduled | 157-14-0108 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | Serviced system. Checked the pump, panel, & floats (ok). Cleaned the filter and diffuser in the Clearstream. Changed the filter in the aerator. There is rust and corrosion in the panel. The timer is set to 4 minutes every 2 hours. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 04/16/2020 | 12:00 PM
10/09/2020 |  | Follow-Up |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Eco Virginia | 1942001235 | William | Poindexter | 1.000000 |  | none | none | Gravity | Pressure | Trenches | Not Applicable |  | ["Dispersal System Operation" ,"Distribution Pump Operation"] | ["Distribution Pump Operation" ,"Dispersal System Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced pump, flushed LPD lines. Pump rate restored. | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 |  | 06/03/2021 | 05:53 AM
04/10/2020 |  | RoutineScheduled | 98027809 | Clarke | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Greenway Engineering | 1942001008 | Jeremy | Ferguson | 1.000000 | 1250 | LPD | none | Pump | Gravity | Trenches | Not Applicable |  | ["Level Sensor Operation","SludgeScum Accumulation"] | ["Level Sensor Operation","SludgeScum Accumulation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 07/21/2020 | 11:45 AM
06/03/2020 |  | RoutineScheduled | {FIPSCode}-STS-15233 | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | ["None"] | ["None"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 07/28/2020 | 12:25 PM
12/31/2020 |  |  | 09-113-213 | Buchanan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 12/31/2020 |  | 12.400000 |  |  | 2.330000 |  |  | Attached to this report |  | BOD: 12.4 TSS: 2.33 SV DC | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12/31/2020 | Jan 1 1900 10:30AM
12/18/2020 |  | RoutineScheduled | 13-163-0139 | New Kent | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chickahominy | Onsite Maintenance Team | 1942001039 | Corey | Braxton | 3.000000 | 1000 | Clearstream |  | Pump | Pressure | Trenches |  | 150.000000 | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","Effluent Screens"] | ["BlowerCompressorAerator Operation","Control Operation","Effluent Screens","Level Sensor Operation"] | YES | Musty | Clear | 7.490000 | 6.000000 |  |  | Turb 5.65 | [11 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12/18/2020 | 12:00 AM
10/02/2020 |  | Routine/Scheduled |  | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Whitewater ATU |  | Pump | Distribution Box |  | None |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 10/02/2020 | Jan 1 1900 11:30AM
08/21/2020 |  | Routine, Scheduled | 175-17-0270 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Biomicrobics MicroFAST |  | Pump | Drip | Drip Tubing | None |  | ["Blower/Compressor/Aerator Operation"] | ["Blower/Compressor/Aerator Operation"] |  | Acceptable | Clear | [15 empty] | Spin filter cleaned. Pump Amps 7.777 ETM 436 hrs Cycles 22454 Water Meter Reading 103200 Septic Sludge 6" Scum 12" ATU Sludge 18" Scum 0 Pump Sludge 1" Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 08/21/2020 | 04:26 PM
04/21/2020 |  | Routine/Scheduled |  | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Pump | Distribution Box |  | None |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Recirculation Pump","Sludge/Scum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Recirculation Pump","Sludge/Scum Accumulation"] | N/A |  | 16.51 | 7.290000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/21/2020 | Jan 1 1900 11:15AM
04/17/2020 | Alternative | RoutineScheduled | 171-07-0226 | Shenandoah | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Lord Fairfax | Onsite Wastewater Services - May Supply | 1942001022 | Sara | Tusing | 1.000000 |  | Orenco Advantex | none | Pump | Gravity |  | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/28/2021 | 05:41 AM
11/02/2020 |  | RoutineScheduled | SWP-05-545 | Stafford | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Level Sensor Operation"] | ["Attached Growth Medium" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Level Sensor Operation"] | YES | [15 empty] | Will be sent separately | Inspected | Raked media ponding water drained. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
04/23/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | Orenco Advantex | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/14/2021 | 04:27 PM
07/01/2020 |  | RoutineScheduled | 133 11 0265 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1500 | Advantex | None | Pump | Pressure | Trenches | Not Applicable |  | ["None"] | [] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 08/19/2020 | 12:00 AM
03/12/2020 |  | Routine, Scheduled | 061-17-394 | Fauquier County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | BLEVINS, JOEL R, SR | 1934000415 | JOEL | BLEVINS |  |  | Microfast | Septic Tank Only | None | None | None | None |  | ["None"] | ["None"] | [18 empty] | [Comments]: UV light is good. Compressor is strong and the ditches are dry. Cleaned the air filter. 6" of sludge in treatment tank. Good for another year. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/23/2020 | 10:55 AM
05/07/2020 |  | Reportable Incident | S 800-15-0031 | Suffolk | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | Owner called due hearing bubbling. Serviced system. Checked the panel & floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. Replaced the pump with a Clearstream CS 50 S pump. The timer is set to 4 minutes every 5 hours. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 05/07/2020 | Jan 1 1900 12:00PM
12/14/2020 |  | Routine, Scheduled | 175-18-0010 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Biomicrobics MicroFAST |  |  |  |  | UV Light |  | ["Blower/Compressor/Aerator Operation","Disinfection"] | ["Blower/Compressor/Aerator Operation","Disinfection"] |  | Acceptable | Clear | [15 empty] | Spin filter cleaned. Pump Amps 8.33 ETM 395 hrs Cycles 3069 Water Meter Reading 264850 Septic Sludge 13" Scum 2" ATU Sludge 17" Scum 0 Pump Sludge 2" Scum 0 On 8 mins 19 secs Off 2 hrs 51 mins | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 12/14/2020 | 01:35 PM
11/19/2020 |  | Reportable Incident |  | Virginia Beach | This AOSS should now return to normal function after having provided the above state routine maintenance | Pending Payment | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  |  |  | ["Blower/Compressor/Aerator Operation","Control Operation"] | ["Blower/Compressor/Aerator Operation","Control Operation"] | N/A | [17 empty] | Replaced aerator | This AOSS should now return to normal function after having provided the above state routine maintenance |  | 11/19/2020 | Jan 1 1900 10:30AM
06/23/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | SES MidAtlantic LLC | 1942001203 | James | Green | 1.000000 |  | Multiflo FTB | none | Gravity | Gravity |  | Not Applicable |  | ["Effluent Screens" ,"BlowerCompressorAerator Operation"] | ["Effluent Screens" ,"BlowerCompressorAerator Operation"] | YES | [11 empty] | 2420.000000 |  |  |  | Will be sent separately | Inspected |  | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 |  | 04/15/2021 | 09:00 AM
09/29/2020 | Alternative | Routine/Scheduled | 151-09-0003 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | PremierTech, EFX |  | Pump | None | Aggregate Bed | None | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | Musty | Clear | [15 empty] | Routine Service Septic tank - normal operating level - effluent screen serviced. Pump Basin - high level - noted no weep hole, believe pump is "air locking" - repaired - pump, float sensors and controls operating properly. Biofilter - peatmoss in poor condition - raked / turned - recommend replacement. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 10/07/2020 | 08:00 AM
02/28/2020 |  | Routine, Scheduled | 03-125-239 | Dickenson County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Cumberland Plateau | DEEL, DENNY M | 1942001097 | DENNY | DEEL |  |  | Norweco Singulair ATU | None | Gravity | Distribution Box | Aggregate Bed | None | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Effluent Screens"] |  | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/03/2020 | Jan 1 1900 10:17AM
04/21/2020 |  | Routine/Scheduled |  | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Ecoflo |  | Pump |  |  | None |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  |  | 7.000000 | 3.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/21/2020 | Jan 1 1900 9:30AM
06/11/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/27/2021 | 01:26 PM
08/11/2020 |  | Reportable Incident | 175-02-0623 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green | [9 empty] | ["Distribution Pump Operation"] | ["Distribution Pump Operation"] | [18 empty] | Installed Z163/115v effluent pump. | This AOSS should now return to normal function after having provided the above state routine maintenance |  | 08/11/2020 | 10:30 AM
10/29/2020 |  | Routine/Scheduled | 177-STS-87228 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Old Dominion Onsite, Inc. | 1942001549 | Russell | Revis | [9 empty] | ["Blower/Compressor/Aerator Operation","Control Operation","Level Sensor (Float) Operation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Level Sensor (Float) Operation"] | N/A | [17 empty] | Took BOD sample and cleaned air filter. Reduced settings on recirc from 30 to 20. System seems to be working well. BOD 27mg/L | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 10/29/2020 | 01:17 PM
12/02/2020 | Alternative | Routine/Scheduled | 166-11-149 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | Puraflo |  | Pump | None | Aggregate Bed | None | 600.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | Musty | Clear | [15 empty] | Routine Service Primary septic tank - normal level - effluent screen serviced. Pump Tank - normal level - pump, float sensors & controls operating properly. PuraFlo Modules - FIVE - peatmoss in good condition - raked / turned. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 12/03/2020 | 07:45 AM
04/01/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Fairfax | Hott, Joshua D. | 1942001301 | Joshua | Hott | 1.000000 | 1500 | Septic Tank Only | Puraflo | Pump | Distribution Box | Aggregate Trench | None |  | ["Effluent Screens"] | ["Effluent Screens"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/14/2020 | Jan 1 1900 12:58PM
02/24/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green | [7 empty] | None |  | ["Effluent Screens"] | ["Effluent Screens"] | [8 empty] | 02/24/2020 |  | 363.000000 | [7 empty] | [Comments]: Pump 1 Amps 7.22 ETM 1615h Cycles 562Pump 2 Amps 5.32 ETM 1377h Cycles 544Septic Sludge 8" Scum 1"Pump Sludge 0 Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/24/2020 | Jan 1 1900 11:35AM
02/13/2020 |  | Routine, Scheduled | 181-00-0402 (LEGACY ALT. SYSTEM) | Rockbridge County | This AOSS should now return to normal function after having provided the above stated routine maintenance. | Approved | EHD - Central Shenandoah |  |  |  |  | 1.000000 | 1500 |  | Biomicrobics MicroFAST | Pump | Drip | Drip Tubing | None |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | [18 empty] | [Comments]: New air sensor installed. System did not need to be pumped. Filters checked and cleaned. Control panel functioning properly. No apparent leaks in system or drain field area. Lids properly secured. | This AOSS should now return to normal function after having provided the above stated routine maintenance. |  | 02/21/2020 | 30-12-1899 05:30 PM
07/09/2020 |  | Routine, Scheduled | 175-15-0218 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Clearstream | EZ Treat Sandfilter |  |  |  | UV Light |  | ["Blower/Compressor/Aerator Operation","Effluent Screens"] | ["Blower/Compressor/Aerator Operation","Effluent Screens"] |  | Good | Clear | 7.400000 | 5.100000 | [13 empty] | Pump Amps 9.94 Septic Sludge 8" Scum 2" ATU Sludge 0 Scum 0 Pump Sludge 0 Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 07/09/2020 | 11:30 AM
05/07/2020 |  | Follow-Up | 179-11-0157-SP | Stafford | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [9 empty] | 18.000000 | [5 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
03/13/2020 |  | RoutineScheduled | SD-89-86 | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | SEAL’S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal | 1.000000 |  |  |  | Gravity | Pressure | Trenches | Not Applicable |  | ["None"] | ["None"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 03/13/2020 | 12:00 AM
06/30/2020 |  | RoutineScheduled | 179-06-0251-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Attached Growth Medium"] | ["Effluent Screens" ,"Attached Growth Medium"] | YES | [15 empty] | Will be sent separately | Inspected | We recommend replacing the 18" EZ Set riser on the pump tank. | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 |  | 04/09/2021 | 03:25 PM
03/27/2020 |  | Routine/Scheduled |  | Southampton | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Whitewater ATU |  | Pump | Distribution Box |  | None |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  |  | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/27/2020 | Jan 1 1900 9:30AM
07/30/2020 |  | RoutineScheduled | {FIPSCode}-STS-8940 | Dickenson | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Effluent Screens"] | ["Disinfection","BlowerCompressorAerator Operation","Control Operation","Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
03/17/2020 |  | Routine, Scheduled |  | Albemarle County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Blue Ridge | Dominion Septic, Inc | 1942001350 | Mike | Cook | 2.000000 |  | Ecoflo | None | Pump |  |  |  |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | [Comments]: Drip field is dry, house is vacant. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/01/2020 | 06:33 AM
10/03/2020 |  | RoutineScheduled | {FIPSCode}-STS-11298 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Wastemaster Inc |  | Timothy | Jenkins | 2.000000 |  | PuraFlo |  | Pump | Gravity | Discharge | Chlorination |  | [] | [] |  | Musty | Clear | 7.000000 |  |  | 2.200000 | [11 empty] | Replaced Post Aerator | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 10/22/2020 | 12:35 PM
02/03/2020 |  | Routine, Scheduled |  | Loudoun County | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Paid | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | None | None | Gravity | [24 empty] | [Comments]: Sale inspection on a conventional septic system. There is one clean out near the house. We camera snaked the sewer line to the septic tank and the pvc line was clear. The septic tank was dug up to pump out it is 24" in the ground. The tank was inspected for any leaks or cracks none were seen. Both Tees are pvc. The conveyance line was camera snaked to the d-box all was clear. The 9 port plastic d-box was 18" under the ground and has 4 drain field lines. We camera snaked all 4 lines they were not crushed or blocked but all 4 lines were full of water. At this time the septic system is not in working condition. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 03/02/2020 | 04:43 AM
10/09/2020 | Alternative | RoutineScheduled | 171-07-0271 | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Greenway Engineering | 1942001008 | Jeremy | Ferguson | 1.000000 | 1000 | Eco-Flo | none | Pump | Pressure | Trenches | Not Applicable |  | ["Level Sensor Operation","SludgeScum Accumulation"] | ["Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 10/20/2020 | 02:00 PM
12/04/2020 |  | Routine/Scheduled |  | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Pump | Distribution Box |  | None |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Recirculation Pump","Sludge/Scum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Recirculation Pump","Sludge/Scum Accumulation"] | N/A |  |  | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 12/04/2020 | Jan 1 1900 8:30AM
06/01/2020 |  | Routine/Scheduled | 05-137-0225 | Goochland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chickahominy | Miller's Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1500 | Orenco Advantex | None | Pump | Distribution Box | Aggregate Trench | None |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | [17 empty] | Homeowner has agreed to repair the following: - Replace lid on trash compartment - Replace lid and section o pump tank - Install new vent assembly | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 06/02/2020 | Jan 1 1900 10:48AM
02/25/2020 |  | Routine, Scheduled | {FIPSCode}-STS-70642 | Spotsylvania County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Ware, Michele P | 1942001165 | Michele | Ware |  |  | Septic Tank Only | Septic Tank Only | None | None | None | None |  |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/26/2020 | 07:30 AM
11/05/2020 |  | RoutineScheduled | 15-184-5003 | Scott |  |  | EHD - Lenowisco |  |  | John | Hyder | 1.000000 | 1300 | Norweco 960 |  | Gravity |  |  | Chlorination | 450.000000 | [20 empty] | Dwelling has been removed from property. No testing done. |  |  |  | 12:00 AM
04/09/2020 |  | Routine, Scheduled | 124-STS-2379 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Rejected | EHD - Lord Fairfax | Cubbage, Harrison Lee, II | 1942001021 | Harrison | Cubbage | 1.000000 | 1500 | Septic Tank Only | Biomicrobics MicroFAST | Pump | Drip | Drip Tubing | None |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation"] |  | Musty | Clear | [5 empty] | 04/09/2020 | Pump Tank | 20.000000 | [5 empty] | Attached to this report |  | [Lab Comments]: Lab Sample Normal [Comments]: Corrected blower alarm Pump Settings: Off 3Hrs On 8min ETM-29.20Hr Cycle Count-270 Sludge/Scum Accumulations: Comp.1-13"/4" Comp.2-13"/0" Pump Tank-2"/0" VENIS File Names: 240 Endless Caverns 4-13-20.pdf | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/20/2020 | 05:27 PM
02/25/2020 |  | Routine, Scheduled | 177-06-0044-SWP | Spotsylvania County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | EcoPod | None | Pump |  |  |  |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","SludgeScum Accumulation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation","Distribution Pump Operation"] | [18 empty] | [Comments]: We recommend pumping the Pump Tank due to solids accumulation.The alarm light and horn are not working and should be replaced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/06/2020 | 02:45 PM
06/22/2020 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump | Drip | Elevated Sand Mound | UV Light |  | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  |  | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 06/22/2020 | Jan 1 1900 10:45AM
09/01/2020 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Fairfax | FIVE STAR SEPTIC INC | 1944001248 | AARON | GOINS | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 09/01/2020 | 12:00 AM
08/19/2020 |  | Reportable Incident | 177-18-0146-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | Owner called dude to the red light and alarm being on. Serviced system. Checked the pump, panel, & floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. Installed 1" spring check valve, replaced wire nuts, put floats on a float tree, and pumped down to check everything. There is visible wetness on the drainfield - most likely from rain - need to keep an eye on it. The timer is set to 3.5 minutes every 2 hours. Did not take initial sample. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 08/19/2020 | 12:00 PM
05/26/2020 |  | Reportable Incident | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance | Approved | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green | [9 empty] | ["Dispersal System Operation"] | ["Dispersal System Operation"] | [18 empty] | Repaired force main. | This AOSS should now return to normal function after having provided the above state routine maintenance |  | 05/26/2020 | Jan 1 1900 4:00PM
03/09/2020 |  | Routine, Scheduled | 175-02-0291 | Southampton County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Western Tidewater | R & K Septic, Inc. |  | Craig | Van Holten |  |  | Whitewater ATU |  |  |  |  | None |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/09/2020 | Jan 1 1900 10:00AM
03/26/2020 |  | Routine, Scheduled | 179-14-0222-SR | Stafford County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson |  |  | Orenco Advantex | None | Pump | Distribution Box | Aggregate Trench | UV Light |  | ["Control Operation","Disinfection"] | ["Control Operation","Disinfection"] | [18 empty] | [Comments]: Owner got alarm because UV lamp was burnt out. Last service Oct 2017. Did all normal cleaning and replaced UV lamp, then collected 5-year samples. Roots growing in at pump tank inlet under the riser adapter plate. Minor infiltration at this point. Keeping the roots out will be very difficult until bamboo is removed (very close to tank). | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/01/2020 | 06:33 AM
09/18/2020 | Alternative | Reportable Incident | 136-17-0188 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | Owner called due to the alarm going off. Serviced system. Checked the pump, panel, & floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. There is visible wetness on the drainfield - most likely from rain - need to keep an eye on it. The timer is set to 3 minutes every 2 hours. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 09/18/2020 | 12:00 PM
05/11/2020 |  | Routine, Scheduled | SD-06-51 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Biomicrobics MicroFAST |  |  |  |  | None |  | ["Blower/Compressor/Aerator Operation"] | ["Blower/Compressor/Aerator Operation"] |  | Good | Good | [15 empty] | Spin filter cleaned. Pump Amps 10.52 ETM 309.19 Cycles 13599 Septic Sludge 7" Scum 3" ATU Sludge 9" Scum 0 Pump Sludge 3" Scum 0 Electric box on pump tank needs to be remounted. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 05/11/2020 | 10:50 AM
04/17/2020 |  | Routine, Scheduled |  | Louisa County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Blue Ridge | CLARK, MICHAEL J | 1934000023 | MICHAEL | CLARK |  |  | Septic Tank Only | Septic Tank Only | None | None | None | None |  |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/19/2020 | 03:55 AM
06/03/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 | Pending Payment | EHD - Loudoun | Great Falls Septic Service, Inc | 1942001301 | Josh | Hott |  |  | Delta Environmental Products, UC Series | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] |  | NA | [15 empty] | Will be sent separately | Inspected | Blower motor needs to be replaced. | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 |  | 04/27/2021 | 11:51 AM
11/30/2020 |  | Reportable Incident |  | King William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Three Rivers | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 500 | None | None | Pump | None | None | None | 300.000000 |  | ["Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | [17 empty] | 1000g total Septic Tank / Lift Station - Alarming due to "ragging of pump" Pumped primary septic and pump station empty for maintenance. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 12/01/2020 | 7:30AM
07/07/2020 | Alternative | Initial Visit | 136-07-0645 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | Clearstream |  | Pump | Distribution Box | Aggregate Trench | None | 450.000000 |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | Musty | Clear | [15 empty] | Initial Visit - Full service / inspection conducted. Primary Septic Tank - at normal level, noted roots present around riser. ATU - at normal level - compressor serviced - weir removed and serviced. Pump Tank - at normal operating level - pump, float sensors and controls functioning properly. Require FOIA filed to obtain onsite documents - unable to locate distribution box. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 07/08/2020 | 07:30 AM
06/09/2020 |  | RoutineScheduled |  | Buckingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Piedmont | Taylor's Septic Service, Inc | 1942001028 | Penny | Taylor | 1.000000 | 1000 | Septic | Puraflo | Pump | Pressure | Trenches | Not Applicable | 450.000000 | ["on"] | ["on"] | YES | Musty | Clear | [5 empty] | 06/17/2020 | Sample Chamber | [6 empty] | Attached to this report | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 06/09/2020 | Jan 1 1900 12:00PM
08/14/2020 |  | Reportable Incident |  | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic | Pump Tank | Pump | Pressure | Drip | Not Applicable |  | ["Dispersal System Operation"] | ["Dispersal System Operation"] | NO | [17 empty] | Flushed the drip field to unclog the emitters and test. Pump #1 Zone 1- 7 gpm open return 4.5gpm closed return/ Zone 2-5.5gpm open return 5 gpm close return. Pump #2 Zone 1-10 gpm open return 7.7 close return/ Zone 2- 6.6 open return 5.8 close return/Peak-23134/ High-184/ Water meter-2078337 | This AOSS should now return to normal function after having provided the above state routine maintenance. |  |  | 12:00 AM
06/18/2020 | Alternative | Initial Visit | 159-08-050 | Middlesex | This AOSS should now return to normal function after having provided the above state routine maintenance | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | PremierTech, EFX |  | Gravity | None | Aggregate Bed | None | 450.000000 | ["Level Sensor (Float) Operation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | Musty | Clear | [15 empty] | System service conducted. System in alarm on arrival in discharge dosing pump basin due to bad float sensor. Float sensor replaced - system pumped out of high level normally - Peat biofilter raked. | This AOSS should now return to normal function after having provided the above state routine maintenance |  | 06/19/2020 | 08:00 AM
07/13/2020 |  | Follow-Up | 179-13-0356-SWP | Stafford | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Clearstream | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [9 empty] | 27.000000 | [5 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
01/15/2020 |  | Routine, Scheduled |  | Page County | This AOSS should now return to normal function after having provided the above stated routine maintenance. | Paid | EHD - Lord Fairfax | Cubbage, Harrison Lee, II | 1942001021 | Harrison | Cubbage |  |  | Septic Tank Only | Septic Tank Only | None | None | None | None |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation"] |  | Musty | Dark | [15 empty] | [Comments]: Replaced bottom float Pump Settings: Off 2hrs On 5min Sludge/Scum Accumulations: Septic Tank-11"/1" Pump Tank-3"/0" | This AOSS should now return to normal function after having provided the above stated routine maintenance. |  | 01/18/2020 | 01:33 PM
06/01/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Best 1 | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/27/2021 | 01:26 PM
09/04/2020 |  | RoutineScheduled | 107-04-0629 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Onsite Wastewater Services - May Supply | 1942001022 | Sara | Tusing | 1.000000 |  | Orenco Advantex | none | Pump | Gravity |  | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Inspected DKS | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 05/28/2021 | 05:41 AM
07/03/2020 |  | RoutineScheduled | SD-98-43 | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Wastemaster Inc |  | Timothy | Jenkins | 2.000000 |  | Recirculating Sand Filter |  | Pump | Gravity | Discharge | Chlorination |  | [] | [] |  | Musty | Clear | 7.000000 | 5.700000 |  | 2.200000 |  | 07/03/2020 |  | 16.000000 |  |  | 17.500000 |  |  | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 08/24/2020 | 02:35 PM
04/21/2020 |  | Routine, Scheduled | 109-08-0278 | Bedford County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Central | WAUGH, IAIN C | 1942001512 | IAIN | WAUGH | 1.000000 | 1500 | Septic Tank Only | Multiflo ATU | Pump | Distribution Box | Aggregate Trench | None |  |  | ["SludgeScum Accumulation"] | [18 empty] | [Pumpout Comments]: Recommend to owner to pump multiflo tank deck sludge (about 2-3"in.) with wet vac and pour into septic tank or contact septic pumper to do this to minimize solids in the pump tank. If called, have them pump out the pump tank chamber but really No need to pump septic tank yet, however it would not hurt if contacting a septic pumper! [Comments]: Septic tank 1" scum 8 " sludge Multiflo Clear Effluent with some buildup on deck Pump Tank 12" Sludge (a bit thick and heavy) Alarm is functional Aspirator runs good, Good aeration, Timer controlled discharge. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/22/2020 | 10:26 PM
08/24/2020 |  | Initial Visit | 800-08-0119 | Suffolk | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Western Tidewater | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | Puraflo |  | Gravity | None | Aggregate Bed | None | 600.000000 | ["Attached Growth Medium"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | Musty | Clear | [15 empty] | Initial Visit Primary septic tank in normal operating level - effluent screen serviced - Noted that their appears to be infiltration to the tank. Pump tank - normal operating level - pump, float sensors and controls operating properly. Peatmoss biofilter media is spent and requires replacement. Inspection port holding effluent and not draining. Area of wetness noted around absorption bed. Requires underground / AOSE consult. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 08/27/2020 | Jan 1 1900 10:00AM
09/19/2020 |  | RoutineScheduled | 2073-05-153 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Wastemaster Inc |  | Timothy | Jenkins | 2.000000 |  | Recirculating Sand Filter |  | Pump | Gravity | Discharge | Chlorination |  | [] | [] |  | Musty | Clear | 6.600000 |  |  | 2.200000 | [12 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 10/06/2020 | 02:55 PM
05/30/2020 |  | RoutineScheduled | SD-05-411 | Orange | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC | 1942001049 | Jason | Brown | 3.000000 |  | Trash/Septic Tank | BioMicrobics | Gravity | Pressure | Trenches | Not Applicable |  | [] | [] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 06/24/2020 | 12:00 AM
03/03/2020 |  | Routine, Scheduled |  | Prince William County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Prince William | Dominion Septic, Inc | 1942001125 | Tom | Jackson |  |  | Orenco Advantex | None | Pump | Distribution Box | Aggregate Trench |  |  | ["Control Operation","SludgeScum Accumulation"] | ["Control Operation","SludgeScum Accumulation"] | [18 empty] | [Comments]: Met pumper on site today and removed recirc pump, floats, and biotube to ensure a complete pump-out of the septic/recirc tank. No measurable sludge in discharge tank, so no pumping needed. Inspected plastic d-box, no problems found. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/04/2020 | 05:31 AM
01/02/2020 |  | Routine, Scheduled |  | Albemarle County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Blue Ridge | CLARK, MICHAEL J | 1934000023 | MICHAEL | CLARK |  |  | Septic Tank Only | Septic Tank Only | None | None | None | None |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/09/2020 | 05:15 AM
09/16/2020 |  | RoutineScheduled | 154-08-0068 | Louisa | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 | Approved | EHD - Blue Ridge | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump" ,"Attached Growth Medium"] | ["Effluent Screens" ,"Recirculation Pump" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Attached Growth Medium"] | YES | [15 empty] | Will be sent separately | Inspected | We repaired the broken discharge pump line. We recommend adding soil cover over the repaired area. | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 |  | 04/09/2021 | 03:25 PM
07/01/2020 |  | Reportable Incident | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance | Approved | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green | [9 empty] | ["Control Operation"] | ["Control Operation"] | [18 empty] | Installed new control panel. | This AOSS should now return to normal function after having provided the above state routine maintenance |  | 07/01/2020 | Jan 1 1900 4:00PM
11/30/2020 |  | Routine/Scheduled | 15-120-0268A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesterfield | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | Orenco Advantex |  | Pump | Distribution Box | Aggregate Trench | None | 450.000000 |  | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | Musty | Clear | [15 empty] | Routine Service Primary Septic Tank - normal level - effluent screen serviced. Processing Tank - normal level - recirc pump serviced - media drapes & spray grid serviced. UV - Orenco - Single Bulb - serviced Pump Tank - pump serviced - float sensors & controls operating properly. Distribution Box - concrete - intact - all laterals accepting effluent. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 12/01/2020 | Jan 1 1900 8:00AM
08/06/2020 |  | RoutineScheduled | 061-16-097 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Soils, Inc. | 1940001392 | Markham | Smith | 1.000000 | 1500 | MircFast model .65 Atu |  | Gravity | Pressure | Pad | Not Applicable |  | [] | ["BlowerCompressorAerator Operation","SludgeScum Accumulation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 08/10/2020 | 08:00 AM
12/23/2020 |  | RoutineScheduled |  | Warren | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Puraflo | none | Pump | Gravity |  | Not Applicable |  | ["Auxiliary Filter" ,"Effluent Screens" ,"Level Sensor Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"Control Operation" ,"Effluent Screens" ,"Level Sensor Operation"] | YES | [7 empty] | 12/23/2020 |  | 151.000000 | [5 empty] | Will be sent separately | Inspected | Replaced effluent filter Installed float tree and repaired floats | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance |  | 04/26/2021 | 09:04 AM
09/01/2020 |  | RoutineScheduled | VAG408372 | Bath | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Central Shenandoah | Onsite Wastewater Services - May Supply | 1942001022 | Sara | Tusing | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Pad | UV |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | BOD <2 Ecoil <1 TSS 4.0 | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/28/2021 | 05:41 AM
11/03/2020 |  | Routine, Scheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Puraflo |  |  |  |  | None |  | ["Effluent Screens"] | ["Effluent Screens"] | [18 empty] | Pump 1 Amps 15.13 ETM 130 hrs Cycles 12549 Pump 2 Amps 15.79 ETM 112 hrs Cycles 10913 Septic Sludge 13" Scum 1" Pump Sludge 1" Scum 0 On 39secs Off 2 hrs | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 10/03/2020 | Jan 1 1900 9:18AM
09/03/2020 |  | Pump-Out Only | 181-14-0108 | Rockbridge | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central Shenandoah | Hunter E. Ayres, General Contractor | 1942001166 | Hunter | Ayres | 1.000000 | 2000 | Biomicrobics MicroFAST |  | Gravity | Gravity | Trenches | Not Applicable |  | ["SludgeScum Accumulation"] | ["SludgeScum Accumulation"] | NO | [16 empty] | Pumped Out | Septic system pumped and cleaned. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 09/03/2020 | 08:20 PM
12/29/2020 |  | Routine, Scheduled | 175-04-0706 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Orenco Advantex |  |  |  |  | None |  | ["Dispersal System Operation","Effluent Screens"] | ["Dispersal System Operation","Effluent Screens"] |  | Acceptable | Clear | [15 empty] | Pump to D/F 10.45 Amps Recirculation Pump 9.36 Amps Septic Sludge 15" Scum 0.25 ATU Sludge 16" Scum 0 Pump Sludge 3" Scum 0 On 5 mins 15 secs Off 12 hrs | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 12/29/2020 | 03:56 PM
09/11/2020 |  | RoutineScheduled | 099-17-0007 SWP | King George | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter" ,"Distribution Pump Operation"] | ["Control Operation" ,"Distribution Pump Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | On site for annual inspection and to check high level alarm in discharge tank. Drip rate had slowed from startup, field flush valve needed cleaning, and power had blinked off several times. In the past 30 days, system averaged 3.2 discharge cycles per day at 10.6 minutes per cycle. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
03/03/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | EZ Treat Sandfilter |  | Pump | Drip | Drip Tubing | UV Light |  | ["Disinfection","Effluent Screens","Recirculation Pump"] | ["Disinfection","Recirculation Pump"] |  | Good | Clear | [15 empty] | [Comments]: Effluent filter needs to be installed.Pump Amps 9.77 ERTM 157h 37m Cycles 2043Pump Amps 9.79Water Meter Reading 55890Septic Sludge 2" Scum 2"Pump Sludge 0 Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/03/2020 | Jan 1 1900 2:24PM
07/15/2020 |  | RoutineScheduled | 177-18-0373-SWP | Spotsylvania | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | 90-DAY INSPECTION | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/09/2021 | 03:25 PM
05/13/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/27/2021 | 01:26 PM
08/27/2020 | Alternative | RoutineScheduled | 166-05-141 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services |  | joel | pinnix | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
08/11/2020 |  | Routine, Scheduled | 175-15-0477 | Prince William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Biomicrobics MicroFAST |  |  |  |  | UV Light |  | ["Blower/Compressor/Aerator Operation","Disinfection"] | ["Blower/Compressor/Aerator Operation"] |  | Good | Clear | [15 empty] | UV Bulb needs replacing. Spin filter cleaned. Pump Amps 7.03 ETM 2102hrs 14 mins Cycles 13336 Water Meter Reading 703000 Septic Sludge 12" Scum 0.25 ATU Sludge 10" Scum 0 Pump Sludge 1" Scum 0 | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 08/11/2020 | 10:37 AM
05/05/2020 |  | RoutineScheduled | 187050003 | Warren | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Lord Fairfax | Onsite Wastewater Services - May Supply | 1942001022 | Sara | Tusing | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | INSPECTION BY DS | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/28/2021 | 05:41 AM
05/28/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Best 1 | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/27/2021 | 01:26 PM
05/01/2020 |  | RoutineScheduled | 109-06-0799 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Acres of Virginia, Inc. | 1942001044 | Melvin | Collins | 1.000000 | 500 | Multiflo | none | Pump | Pressure | Trenches | Not Applicable | 450.000000 | ["None"] | ["None"] | YES | [17 empty] | Aerator is functioning properly. Alarm checked. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 06/24/2020 | 01:25 PM
05/20/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Payment | EHD - Loudoun | Great Falls Septic Service, Inc | 1942001301 | Josh | Hott | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/27/2021 | 11:51 AM
06/02/2020 |  | Routine/Scheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | POWELLS PLUMBING, INC. | 1942001036 | Kurt | Holthaus | 1.000000 | 1250 | Puraflo |  | Pump | Distribution Box | Aggregate Trench |  | 600.000000 | ["Effluent Screens"] | ["Effluent Screens"] | N/A | [17 empty] | Annual Inspection - Serviced effluent screen(s). | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 06/16/2020 | 12:42 PM
10/27/2020 |  | RoutineScheduled | 061-19-146 | Fauquier | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Clearstream | none | Pump | Gravity | Drip | UV |  |  |  | NA | [7 empty] | 10/27/2020 | [7 empty] | Will be sent separately | Inspected | Six month inspection. Alarm horn was muted on arrival, reset it. Multiple wet spots at the toe of first mound, and one spot at distal end of second mound (farthest from house). Poor grass growth on first mound, needs re-seeded. Second mound has good grass growth, although only over each emitter. Owner may want to have OSE revisit the site. Collected first BOD and Fecal samples. Not able to verify drip rate or flush rates in any kind of timely or accurate manner. System is a continuous flush and has no flow meter. Timer on/off settings were found to be set exactly as per engineer's plans to achieve a maximum of 300 gals/day. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
06/23/2020 |  | Routine/Scheduled | 14-160-0148 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Biomicrobics MicroFAST |  | Gravity | Distribution Box |  | None |  | ["None"] | ["Blower/Compressor/Aerator Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 06/23/2020 | 10:30 AM
01/30/2020 |  | Routine, Scheduled | 04-118-0095 | Charles City County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Chickahominy | Chapin, Ben |  | Ben | Chapin |  |  | Septic Tank Only | Septic Tank Only | None | None | None | None | [21 empty] | VENIS File Names: 5301 West Run Rd.jpeg | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/11/2020 | Jan 1 1900 1:14PM
01/13/2020 |  | Follow-Up |  | Fairfax County | This AOSS should now return to normal function after having provided the above stated routine maintenance. | Paid | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green | [9 empty] | ["None"] | ["None"] | [18 empty] | [Comments]: Replaced concrete casing lid. | This AOSS should now return to normal function after having provided the above stated routine maintenance. |  | 01/13/2020 | Jan 1 1900 4:00PM
06/29/2020 |  | Follow-Up |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/14/2021 | 04:27 PM
12/04/2020 |  | Initial Visit | 136-14-0238 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | Delta Environmental Products, UC Series |  | Pump | Distribution Box | Aggregate Trench | None | 450.000000 |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | Musty | Clear | [15 empty] | Initial site visit Primary septic tank - normal operating level Aeration Tank - normal operating level - compressor serviced. Pump Tank - normal level - Pump, float sensors & controls operating properly Distribution box - concrete - all laterals accepting effluent. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 12/07/2020 | 08:30 AM
01/03/2020 |  | Routine, Scheduled |  | Warren County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Lord Fairfax | Cubbage, Harrison Lee, II | 1942001021 | Harrison | Cubbage | 1.000000 | 1500 | Septic Tank Only | Biomicrobics MicroFAST | Pump | Drip | Drip Tubing | None |  | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation"] | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation"] |  | Musty | Dark | [15 empty] | [Comments]: Added solution to media to help with sludge. Pump Settings: Off 2hrs On 12.2min ETM-699.10Hr Cycle COunt-3099 Sludge/Scum Accumulations: Comp.1-10"/2" Comp.2-12"/0" Pump Tank-2"/0" | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/18/2020 | 11:49 AM
06/03/2020 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [11 empty] | N/A | [7 empty] | 06/03/2020 |  | 2.000000 |  | 1.000000 | [6 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 06/09/2020 | Jan 1 1900 9:30AM
01/13/2020 |  | Routine, Scheduled | 17-142-0227 | Hanover County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chickahominy | Old Dominion Onsite, Inc. |  | John | Ewing | 1.000000 | 1500 | EZ Treat Sandfilter |  | Pump | Manifold | Drip Tubing | None | 100.000000 | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump"] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump"] | [18 empty] | [Comments]: Owner reported that the installer (Robert Johnston) and sales rep. for EZ treat recently worked on control panel because it was working intermittently causing high water alarms in the recirculation tank. The spin filter was found to be installed backwards, this was corrected. The dripfield was flushed and the spin filter was cleaned. The pressure gauge on the EZ treat was corroded and was replaced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/13/2020 | Jan 1 1900 8:06AM
03/19/2020 |  | Routine, Scheduled | {FIPSCode}-STS-22887 | Frederick County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Lord Fairfax | POWELLS PLUMBING, INC. | 1942001036 | Kurt | Holthaus | 1.000000 | 1000 | Puraflo |  | Pump | Drip | Drip Tubing |  | 450.000000 | ["Effluent Screens"] | ["Effluent Screens"] | [18 empty] | [Comments]: Annual Inspection - Serviced effluent screen(s). | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/19/2020 | 12:28 PM
07/23/2020 |  | RoutineScheduled | 179-12-0195-SWP | Stafford | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Dispersal System Operation" ,"Recirculation Pump"] | ["Dispersal System Operation" ,"Auxiliary Filter" ,"Recirculation Pump"] | NA | [15 empty] | Will be sent separately | Inspected | Both ARV's and valve boxes for zone 1 were in pieces, apparently hit by lawnmower. Found mud and grit in pvc manifold. Flushed piping into 5 gal bucket prior to making final connections. Did extended flush on both zones and bleach-cleaned spin filter prior to checking drip rates. Drip rates are over 40% lower than design, most likely due to plugged emitters caused by improper venting (ARV's broke off below grade). Returned on 7-24 and bleach-flushed both zones in an attempt to improve drip and flush rates. No improvement to rates. No effluent surfacing so system can certainly be used, but the daily flow capacity is reduced. | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
07/28/2020 |  | Follow-Up |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | All 5 purflo pods the peat fiber was replaced System is in working condition | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/14/2021 | 04:27 PM
10/08/2020 |  | RoutineScheduled | 187050534 | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 2705110225 | Larry | Royston | [9 empty] | ["None"] | ["None"] | YES | [16 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 10/08/2020 | 12:00 AM
01/14/2020 |  | Reportable Incident |  | Fairfax County | This AOSS should now return to normal function after having provided the above stated routine maintenance. | Paid | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green | [9 empty] | ["Dispersal System Operation"] | ["Dispersal System Operation"] | [18 empty] | [Comments]: Replaced 3 solenoids. | This AOSS should now return to normal function after having provided the above stated routine maintenance. |  | 01/14/2020 | Jan 1 1900 4:00PM
06/23/2020 |  | Routine/Scheduled |  | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Pump |  |  | None |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Recirculation Pump","Sludge/Scum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Recirculation Pump","Sludge/Scum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 06/23/2020 | Jan 1 1900 7:00AM
02/26/2020 |  | Routine, Scheduled | 2018-143-0198 | Henrico County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Henrico | [13 empty] | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump"] | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump"] | [18 empty] | [Comments]: Cleaned effluent filter. Flushed Manifold. Checked float and pump operation. Lots of wet wipes were found clogging the filter in septic tank. these items are not septic safe and should not be flushed. Grading needs to be fixed around treatment unit. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/26/2020 | 02:30 PM
07/28/2020 |  | Follow-Up | 179-06-0259-SWP | Stafford | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [9 empty] | 9.000000 | [5 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
11/09/2020 |  | RoutineScheduled | SWP-05-479 | Spotsylvania | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart |  |  | Orenco Advantex | none | Pump | Gravity | Pad | Not Applicable |  | ["Recirculation Pump" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Attached Growth Medium" ,"BlowerCompressorAerator Operation"] | ["Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Attached Growth Medium" ,"BlowerCompressorAerator Operation"] | YES | [15 empty] | Will be sent separately | Inspected | Advantex tank needs pumped out, proposal to assist pumper to be sent to home owner. Massive growth on drain field, we have been advising home owner to clear for 8 years and still has not been done. if drain field is not cleared O&M contract will not be renewed next year. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
12/01/2020 |  | RoutineScheduled | 06911261 | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Combs Wastewater Management LLC | 1942001353 | Amy | Combs | 1.000000 | 1500 |  |  | Gravity | Gravity | Trenches | Not Applicable | 450.000000 | [] | ["BlowerCompressorAerator Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12/23/2020 | 12:00 PM
06/15/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim |  |  | Best 1 | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Best 1 tank needs pumped | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 |  | 04/14/2021 | 04:27 PM
01/03/2020 |  | Routine, Scheduled | SD-15-187 | Orange County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | CLARK, MICHAEL J | 1934000023 | MICHAEL | CLARK |  |  | Septic Tank Only | Septic Tank Only | None | None | None | None |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/14/2020 | 03:51 AM
06/25/2020 |  | RoutineScheduled |  | Shenandoah | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Control Operation"] | ["Auxiliary Filter" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/26/2021 | 09:04 AM
11/20/2020 |  | RoutineScheduled | 13-163-0037 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Onsite Maintenance Team | 1942001039 | Corey | Braxton | 3.000000 |  |  |  | Pump | Gravity | Trenches |  | 250.000000 | [] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Dispersal System Operation","Level Sensor Operation","Auxiliary Filter"] | YES | Musty | Clear | 7.100000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 11/28/2020 | 12:00 AM
05/18/2020 |  | RoutineScheduled | 07-113-006 | Buchanan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | Septic Inc |  | Denny | Deel |  |  |  |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens"] | true | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
01/06/2020 |  | RoutineScheduled | 107-06-0650 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Pump | Pressure | Drip | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 06/02/2021 | 12:00 AM
10/30/2020 |  | Routine, Scheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Biomicrobics MicroFAST |  |  |  |  | None |  | ["Blower/Compressor/Aerator Operation"] | ["Blower/Compressor/Aerator Operation"] |  | Acceptable | Clear | [15 empty] | Pump 1 Amps 9.34 ETM 26 hrs Cycles 278 Pump 2 Amps 9.53 ETM 25 hrs Cycles 272 ATU Sludge 12" Scum 14" Recommend pumping MicroFast. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 10/30/2020 | Jan 1 1900 1:00PM
02/22/2020 |  | Routine, Scheduled |  | Amelia County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Piedmont | Dominion Septic, Inc | 1942001350 | Mike | Cook | 1.000000 |  | None | None | Pump | Distribution Box | Aggregate Trench |  |  | ["Attached Growth Medium","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/03/2020 | Jan 1 1900 5:36AM
02/07/2020 |  | Routine, Scheduled | 98-142-0046 | Hanover County | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Chickahominy | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | None | None | Pump |  |  |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | [18 empty] | [Comments]: Upon arrival water lever was high in the septic tank, indicating possible clogged or crushed conveyance line. Subsequent inspection confirmed line is crushed. Repairs to be completed by others. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 04/06/2020 | Jan 1 1900 2:45PM
11/03/2020 |  | RoutineScheduled | SP-01-593 | Spotsylvania | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Attached Growth Medium" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | ["Attached Growth Medium" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"Control Operation" ,"Dispersal System Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Media is clogged, there is no recirc trough present. Blower alarm is not working. Pump alarm buzzer is not working. FAST control panel needs to be replaced. Drip rate is higher than normal, check valves holding and return valves holding. Adjusted timer. Proposal for repairs to be sent to homeowner. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
10/09/2020 |  | Routine/Scheduled | 06-120-0682A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. |  |  | Biomicrobics MicroFAST |  | Pump |  |  |  |  | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 10/09/2020 | Jan 1 1900 11:00AM
06/08/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | Orenco Advantex | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/14/2021 | 04:27 PM
10/20/2020 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 | Approved | EHD - Fairfax | Ace Contracting Services Inc | 1942001120 | Lawrence | Fellenz Jr. | 1.000000 |  | Puraflo | none | Pump | Gravity |  | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 |  | 06/29/2021 | Jan 1 1900 10:39PM
11/12/2020 |  | Routine, Scheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Puraflo |  |  |  |  | None |  | ["Effluent Screens"] | ["Effluent Screens"] | [18 empty] | Pump 1 Amps 11.70 ETM 41 hrs Cycles 3866 Pump 2 Amps 12.67 ETM 41 hrs Cycles 3867 Septic Sludge 2" Scum 1" Pump Sludge 6" Scum 0 On 1 mins 12 secs Off 2 hrs | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 11/12/2020 | Jan 1 1900 11:46AM
05/07/2020 |  | Routine/Scheduled | S 800-17-0101 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | Serviced system. Checked the pump, panel, & floats (ok). Cleaned the filter and the diffuser in the Clearstream. Changed the filter in the aerator. Replaced the wire nuts for the alarm in the Clearstream. The timer is set to 1 minute every 2 hours. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 05/07/2020 | Jan 1 1900 12:00PM
01/15/2020 |  | Routine, Scheduled |  | Richmond City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Richmond | BEASLEY, THOMAS W | 1934000450 | THOMAS | BEASLEY | 2.000000 | 2600 | Multiflo ATU | Septic Tank Only | Pump | Distribution Box | Aggregate Trench | None |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [5 empty] | 45.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/15/2020 | Jan 1 1900 4:00PM
11/19/2020 |  | RoutineScheduled | 98-197-428 | Wise | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | Wise Health Dept |  | Rodney | Neece |  |  | ATU Jet |  | Gravity | Gravity | Discharge | Chlorination |  |  |  |  | None | Clear | 6.800000 | 7.000000 |  | 0.000000 | No tablets | [11 empty] | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 11/19/2020 | 12:00 AM
06/08/2020 | Alternative | RoutineScheduled | 115-03-0340 | Campbell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Septic Tank | Ecoflo | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","Effluent Screens"] | ["Attached Growth Medium","Effluent Screens"] | NA | Musty | [15 empty] | Inspected | Sludge level-minimal Scum & 12" Sludge in Septic tank. Cleaned Effluent screens. Alarm functional and pump is operational, Peat shows its age, some ponding, Turned and broke up, minor roots noted to owner. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 06/08/2020 | 05:30 PM
09/23/2020 |  | RoutineScheduled |  | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","SludgeScum Accumulation","BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [17 empty] | Septic-6"sludge 3"scum/ Microfast-20"sludge (REQUIRES PUMP OUT) Pump tank-0"sludge/ Blower air filter cleaned/ Counts: P1-1239 ETM-42h 18m 54gpm/ P2-1223 ETM-41h 44m 45gpm (adjusted run time) /Peak-7/ High-11/ No breakout or spongy areas on the drainfield. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  |  | 12:00 AM
07/27/2020 |  | RoutineScheduled |  | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Pressure | Trenches |  |  | ["Level Sensor Operation","BlowerCompressorAerator Operation"] | ["Level Sensor Operation","BlowerCompressorAerator Operation"] | NA | [9 empty] | 8.000000 | [7 empty] | Septic-6"sludge 2"scum/ Microfast-8"sludge/ Pump Tank-1"sludge. Blower air filter cleaned. Counts: Pump 1-86 ETM-3h 32m/ Pump 2-82 ETM-3h 25m/ Peak-10/ High-7/ Upon arrival found system in low level alarm, adjusted float and alarm back to normal. No pump out required at this time. No breakout or spongy areas on the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
09/19/2020 |  | RoutineScheduled | SD-13-158 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | RCWWS | 1942001335 | Randy | Gray | 1.000000 | 1000 | Puroflo |  | Gravity | Pressure | Trenches |  | 100.000000 | ["None","None"] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 09/22/2020 | 07:03 PM
05/15/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim |  |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/14/2021 | 04:27 PM
02/11/2020 |  | Routine, Scheduled | 11-125-158 | Dickenson County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Cumberland Plateau | DEEL, DENNY M | 1942001097 | DENNY | DEEL |  |  | Norweco Singulair ATU | None | Gravity | None | Alternative Discharge | Chlorine | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens"] |  | Musty | Clear | [15 empty] | [Comments]: 5 Blue Crystal 8 Bio max added | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/18/2020 | Jan 1 1900 11:17AM
12/17/2020 | Alternative | Routine/Scheduled | 151-04-043 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 1.000000 | 1500 | Microfast |  | Pump | Distribution Box | Aggregate Trench |  |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12/17/2020 | 05:00 PM
01/16/2020 |  | Initial Visit |  | Williamsburg | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Peninsula | Farmer’s Septic Service, Inc. |  | Ross | Cole | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [10 empty] | 14.000000 | [7 empty] | [Comments]: Serviced system. Checked the pump, panel, & floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. The timer is set to 2 minutes every 2 hours. Took initial BOD sample. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/16/2020 | Jan 1 1900 12:00PM
08/17/2020 |  | RoutineScheduled | 182-07-0067 | Rockingham | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Central Shenandoah | Onsite Wastewater Services - May Supply | 1942001022 | Sara | Tusing |  |  | Orenco Advantex | none | Pump | Gravity |  | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/28/2021 | 05:41 AM
10/07/2020 |  | RoutineScheduled | 179-17-0034-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 |  | 04/09/2021 | 03:25 PM
04/06/2020 |  | RoutineScheduled | 182-07-0287 | Rockingham | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Central Shenandoah | Onsite Wastewater Services - May Supply | 1942001022 | Sara | Tusing | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Pressure | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/28/2021 | 05:41 AM
11/13/2020 |  | RoutineScheduled | 12-184-5001 | Scott | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Effluent Screens"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
11/20/2020 |  | Routine/Scheduled | 05-177-1234 | Pulaski | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Orenco Advantex |  | Pump | Distribution Box |  | None |  | ["None"] | ["Control Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 11/20/2020 | 01:00 PM
03/18/2020 |  | Routine, Scheduled |  | Loudoun County | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Paid | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | None | None | Pump | Manifold | [23 empty] | [Comments]: One line on the right when looking at RT 7 is bleeding out. The homeowner had trees removed properly from the drainfield area, but it appears that one line near a large stump is surfacing. Homeowner is going to contact someone for the repair. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 03/19/2020 | 08:35 AM
12/17/2020 |  | Routine, Scheduled | SD-06-308 | Fauquier | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Rappahannock-Rapidan | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Ecoflo |  |  |  |  | UV Light |  | ["Blower/Compressor/Aerator Operation","Disinfection"] | ["Blower/Compressor/Aerator Operation"] |  | Acceptable | Clear | [15 empty] | Needs new UV Bulb & chord. Pump Amps 6.35 Septic Sludge 4" Scum 3" ATU Sludge 0 Scum 0 Pump Sludge 0 Scum 0 Control panel demand. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 12/17/2020 | 02:47 PM
03/09/2020 |  | Reportable Incident | 2017-143-0122 | Henrico | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Henrico | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | 3/6/2020 - Contractor called stating the pump is not coming on - might be the relay. System was flooded. Going to a drip. Pump tank needs to be pumped and cleaned out. Pump screen and spinfilter screen were stopped up. Cleaned pump screen and replaced the spinfilter screen. Pump is running properly. 3/9/2020 - Pumping company pumped out pump tank and trash off of the Clearstream tank. Serviced system. Checked the pump, panel, & floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream, changed the filter in the aerator, and changed the mesh screen in the spinfilter. Fixed the grade on the pipe in the Clearstream. The UV is not working. Lots of grease in the septic - inlet tee was stopped up. Need to re-wire splice box w/ silicone wire nuts and fix UV light. The timer is set to 5 minutes every 1 hour. Vacuum breakers are not working. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. |  | 03/09/2020 | 12:00 PM
01/10/2020 |  | Routine, Scheduled | 15-137-0106 | Goochland County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chickahominy | SHAW, WILLIAM A, JR. | 1934000449 | WILLIAM | SHAW |  |  | Septic Tank Only | Septic Tank Only | None | None | None | None |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | [18 empty] | [Comments]: Replaced UV bulbs | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/14/2020 | Jan 1 1900 12:17PM
03/18/2020 |  | Routine, Scheduled |  | Loudoun County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Biomicrobics MicroFAST | None | Gravity | Distribution Box | Gravel-Less Trench | [23 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/19/2020 | 08:35 AM
03/31/2020 |  | Follow-Up |  | Fairfax County | This AOSS should now return to normal function after having provided the above stated routine maintenance. | Paid | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green | [9 empty] | ["Distribution Pump Operation"] | ["Distribution Pump Operation"] | [18 empty] | [Comments]: Installed Z 140 effluent pump in Puraflo pump tank. | This AOSS should now return to normal function after having provided the above stated routine maintenance. |  | 03/31/2020 | Jan 1 1900 4:00PM
02/26/2020 |  | Follow-Up | 179-11-0236-SWP | Stafford County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001350 | Mike | Cook | 1.000000 |  | EZ Treat Sandfilter | None | Pump | Distribution Box | [15 empty] | 22.000000 | [8 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/06/2020 | 08:57 AM
11/24/2020 |  | RoutineScheduled | 099-06-0307-SWP | King George | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Rejected | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Attached Growth Medium" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | ["Distribution Pump Operation" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Control Operation" ,"Dispersal System Operation" ,"Attached Growth Medium"] | NA | [15 empty] | Will be sent separately | Inspected | During yearly maintenance I noticed the inspection port at D-box had standing water in it. To further investigate I dug up D-box to find the sides of the box to be broke and letting dirt fill the box. After cleaning out the box I noticed back flow from the drain field. Proposal to be sent to the customer to camera the lines to make sure there is not a blockage. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
02/12/2020 |  | Routine, Scheduled | 061-16-250 | Fauquier County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 5.000000 |  | Bio Barrier | Bio Barrier | Pump | Drip | Drip Tubing |  |  | ["Control Operation","Distribution Pump Operation","Level Sensor Operation"] | ["Control Operation","Distribution Pump Operation","Level Sensor Operation"] | [18 empty] | [Comments]: All tanks in high level again, this time due to failed fitting on drip pump #1. Closed gate valve for pump #1 and changed alternator in panel to pump on #2 only until repairs can be made. Flow meter reading on 2-3-20 was 11,007,052 gals. Since then (9 days), the system pumped an average of 3,918 gals/day. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/09/2020 | 04:39 AM
04/16/2020 |  | Follow-Up | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance | Approved | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green | [9 empty] | ["None"] | ["None"] | [18 empty] | Replaced peat in 2 modules. | This AOSS should now return to normal function after having provided the above state routine maintenance |  | 04/16/2020 | Jan 1 1900 4:00PM
06/16/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/27/2021 | 01:26 PM
04/06/2020 |  | Routine, Scheduled | 04-100-0686 | Accomack County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Eastern Shore | DUER, PETE C | 1942001051 | PETE | DUER | 1.000000 | 1000 | Septic Tank Only | Ecoflo | Pump | None | None | None |  | ["None"] | ["None"] | [18 empty] | [Comments]: Aoss Inspection. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/16/2020 | 02:51 PM
11/24/2020 |  | RoutineScheduled | 107-05-0586 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Onsite Wastewater Services - May Supply | 1942001627 | Drew | Shull | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Pressure | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | inspection by Ds | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 05/28/2021 | 05:41 AM
09/01/2020 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Gravity | Gravity |  | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Sale septic inspection on a conventional gravity. The state requires that all conventional septic tanks must be pumped out EVERY 5 years and filed with the state and county. The sewer line was camera snaked and was clear. The septic tank lid was dug up it was 6" under the ground and the tank was pumped out. The tank was inspected for any leaks none were found. The conveyance line was camera snaked and all was clear. The plastic 7 port d-box was dug up it was 18" under the ground. All 6 header lines were camera snaked and were clear. The drain field was probed and was dry. At time of inspection all components were in working condition. | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 |  | 04/14/2021 | 04:27 PM
11/23/2020 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump | Drip | Elevated Sand Mound | UV Light |  | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  |  | 7.870000 | 6.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 11/23/2020 | Jan 1 1900 11:15AM
07/14/2020 | Alternative |  | 166-13-148 | Northumberland | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers |  |  | joel | pinnix | [9 empty] | ["Disinfection"] | ["Disinfection"] | [18 empty] | Replaced UV bulb. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  |  | 12:00 AM
09/16/2020 |  | Routine, Scheduled | 175-05-0351 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Orenco Advantex |  |  |  |  | None |  | ["Attached Growth Medium","Distribution Pump Operation","Effluent Screens"] | ["Attached Growth Medium","Distribution Pump Operation","Effluent Screens"] |  | Good | Clear | [15 empty] | Pump Amps 12.38/12.44 Septic Sludge 8" Scum 1" Pump Sludge 4" Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 09/16/2020 | 05:11 PM
10/20/2020 | Alternative | Routine/Scheduled | -STS-101820 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1500 | Orenco Advantex |  | Pump | Drip | Drip Tubing | None | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | None | Clear | [15 empty] | Routine Service Processing Tank - normal operating level - RSV, recirc. pump and effluent screen serviced. Treatment Module - media drapes & spray grid serviced. Pump Tank - normal operating level - pump serviced - float sensors & controls operating properly. Drip headworks - vortex filter serviced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 10/21/2020 | 09:30 AM
05/21/2020 |  | Initial Visit | R18-180-0016 | Roanoke | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1000 | EZ Treat |  | Pump | Gravity | Trenches |  |  | ["None"] | ["None"] | [18 empty] | Initial start-up inspection. Set timers at 2 1/2 minutes ON, 7 1/2 minutes OFF. Raised alarm float up. All aspects operating as designed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 10/12/2020 | Jan 1 1900 7:00PM
10/12/2020 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Soils, Inc. | 1942001004 | Mark | Smith | 1.000000 |  | EcoPod | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 |  | 05/31/2021 | 09:07 AM
05/22/2020 |  | Routine/Scheduled | 08-160-0240 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Delta Environmental Products, DF Series |  | Pump | Drip | Drip Tubing | None | 87.000000 | ["None"] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 05/22/2020 | 12:00 PM
11/03/2020 |  | RoutineScheduled |  | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - New River | MSS INC |  | Tim | Conner | 3.000000 | Christiansburg | ECOFLO |  | Pump | Pressure | Trenches | Not Applicable |  | ["on"] | ["on"] | YES | Septic | Discolored | [5 empty] | 11/13/2020 | Sample Chamber | [6 empty] | Attached to this report | Inspected | EVERYTHING FUNCTIONING | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 11/13/2020 | 12:00 PM
10/31/2020 |  | RoutineScheduled | SD-15-273 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | EcoVirginia LLC | 1942001235 | William | Poindexter | [9 empty] | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 11/02/2020 | 08:45 PM
09/24/2020 | Alternative | RoutineScheduled | 159-06-0217 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Church View Septic Service Inc. | 1942001302 | Charles | Langford | 1.000000 | 1000 | Puraflow |  | Pump | Pressure | Pad | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | [17 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 01/14/2021 | 12:00 AM
07/09/2020 |  | Routine, Scheduled | 175-08-0284 | Prince William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Multiflo ATU |  |  |  |  | Chlorine |  | ["Dispersal System Operation","Level Sensor (Float) Operation","Recirculation Pump"] | ["Recirculation Pump"] | [18 empty] | Found discharge not operating. Samples not taken. Pump Amps 24 Septic Sludge 24" Scum 2" ATU Sludge 10" Scum 0 Pump Sludge 0 Scum 0 | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 07/09/2020 | 01:53 PM
01/21/2020 |  | Routine, Scheduled | 093-05-0388 | Isle of Wight County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Western Tidewater | R & K Septic, Inc. |  | John | Butt, Jr |  |  | Clearstream ATU |  | Pump | Distribution Box |  | None |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] |  |  | 6.26 | 7.800000 | 4.000000 | [13 empty] | [Comments]: Replaced buzzer | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/21/2020 | Jan 1 1900 2:45PM
09/01/2020 |  | RoutineScheduled |  | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001301 | Joshua | Hott | [9 empty] | ["Effluent Screens"] | ["Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
05/15/2020 |  | RoutineScheduled | 175-05-0679 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | Aquarobic Services | 1934000142 | Michael | Blake |  |  | none | none | Pump | Gravity | Mound | Not Applicable |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced air filter. Re-located 2 willow trees that were planted earlier in the year. Seed and straw re-applied to filter bed manifold area. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 07/01/2022 | 10:30 AM
05/05/2020 |  | RoutineScheduled | 061-16-400 | Fauquier | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock-Rapidan | Onsite Wastewater Services - May Supply | 1942001022 | Sara | Tusing | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | INSPECTION BY DS | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/28/2021 | 05:41 AM
11/05/2020 |  | Follow-Up | SD-11-312 | Fauquier | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Distribution Pump Operation" ,"Control Operation"] | ["Distribution Pump Operation" ,"Auxiliary Filter" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Septic tank and recirc tank pumped 3 days ago. Tanks not yet refilled. Performed hose test on septic tank. Only a minor drip observed at septic riser joints. Also ran camera down sewer line and did not see any leaks. Installed new flow meter between headworks and solenoids valve box. System pumps down hill. Added an air release valve on each supply line just after zone solenoids to prevent siphoning. Added bleach to discharge pump basin and flushed tubing. Both zones dripping more than 50% below design, but flush rates are good (11.8 gpm average). Need to return in a few days to clean the sheets and tweak settings to help ensure discharge basin stays out of high level (which shuts off the recirc pump and stops treatment). | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
10/15/2020 |  | RoutineScheduled | {FIPSCode}-STS-5225 | Frederick | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | none | none | Gravity | Gravity |  | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Attached Growth Medium"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Attached Growth Medium"] | NA | [7 empty] | 10/15/2020 |  | 16.000000 | [5 empty] | Will be sent separately | Inspected | Lab Sample Normal | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/26/2021 | 09:04 AM
02/12/2020 |  | Initial Visit | C-122-09-0046 | Craig County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Alleghany-Roanoke | KING, DAVID A | 1942001094 | DAVID | KING | 1.000000 |  | Microfast | Septic Tank Only | Gravity | Distribution Box | Gravel-Less Trench | None | [22 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/12/2020 | Jan 1 1900 2:26PM
10/02/2020 |  | Routine/Scheduled | 085-STS-31790 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chickahominy | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | Orenco Advantex |  | Pump | Distribution Box | Aggregate Trench | None | 600.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | None | Clear | [15 empty] | Routine Service Primary Septic Tank - normal operating level - effluent screen serviced. Treatment Module - media drapes & spray grid serviced. Discharge tank - pump serviced, float sensors & controls operating properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 10/09/2020 | Jan 1 1900 9:15AM
12/15/2020 | Alternative | RoutineScheduled | 171-16-098 | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Lord Fairfax | Onsite Wastewater Services - May Supply | 1942001627 | Drew | Shull |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | None | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/17/2022 | 06:40 AM
05/05/2020 |  | Routine/Scheduled | 01-163-0109 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chickahominy | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | Ecoflo | None | Pump | Distribution Box | Aggregate Trench | None |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | Tipping Bucket was found damaged, and has been repaired | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 05/26/2020 | Jan 1 1900 2:47PM
03/12/2020 |  | Routine, Scheduled |  | Loudoun County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | Orenco Advantex | None | Gravity | Distribution Box | Aggregate Bed | [23 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/12/2020 | 02:21 PM
01/06/2020 |  | Routine, Scheduled | 234-18-156 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesapeake | R & K Septic, Inc. |  | John | Butt, Jr |  |  | Clearstream ATU |  | Pump | Drip | Elevated Sand Mound | UV Light |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] |  |  | 6 | 8.050000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/06/2020 | Jan 1 1900 10:45AM
08/21/2020 |  | RoutineScheduled | 07-197-023 | Wise | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | Wise County health deprtment |  | Rodney | Neece | 1.000000 |  | ATU |  | Gravity | Gravity | Discharge | Chlorination |  |  |  |  | Musty | Clear | 1.000000 | 1.000000 |  | 0.000000 | [12 empty] | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 08/21/2020 | 12:00 AM
10/13/2020 |  | RoutineScheduled | SD-14-368 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Greenway Engineering | 1942001008 | Jeremy | Ferguson | 1.000000 | 1500 | Microfast | none | Pump | Pressure | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Level Sensor Operation","SludgeScum Accumulation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 10/13/2020 | 01:45 PM
03/05/2020 | Alternative | RoutineScheduled | 115-11-0079 | Campbell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | WAUGH, IAIN C | 1942001512 | IAIN | WAUGH | 1.000000 | 1500 | Septic Tank Only | Orenco Advantex | Gravity | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | [18 empty] | [Pumpout Comments]: Not Needed [Comments]: Septic Tank minimal scum 1-2" Sludge, Recirc 4-5" Sludge, Discharge 6" sludge, Cleaned Effluent Filter, CLeaned Bio filter, Checked Float switches Ran in Test mode, Good SPray Pattern, Alarm good, 1 Alarm in history from during Familu reunion for high water use, Everything is opperational. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 03/07/2020 | 10:43 AM
08/14/2020 |  | Initial Visit | 43434 | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | [6 empty] | EcoFlo | [6 empty] | ["SludgeScum Accumulation"] | ["SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 08/14/2020 | 12:00 AM
10/09/2020 |  | RoutineScheduled | 107-06-0330 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Onsite Wastewater Services - May Supply | 1942001022 | Sara | Tusing | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Pressure | Drip | Not Applicable |  | ["Recirculation Pump"] |  | NA | [15 empty] | Will be sent separately | Inspected | Inspected DKs | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 05/28/2021 | 05:41 AM
04/15/2020 |  | RoutineScheduled | 182-07-0080 | Rockingham | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Central Shenandoah | Onsite Wastewater Services - May Supply | 1942001022 | Sara | Tusing | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/28/2021 | 05:41 AM
07/13/2020 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Gravity | Gravity |  | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | sale inspection on a conventional gravity septic system. The sewer line was camera snaked and was clear. The septic tank was pumped out by other a year ago. Effluent was at the proper level. And the T's are pvc. The 8 port concrete d-box was dug up it was 10" under the ground. All 4 header lines were camera snaked and were clear. the drain field was probed and dry. at time of inspection all components were in working condition. | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 |  | 04/14/2021 | 04:27 PM
08/08/2020 |  | RoutineScheduled | 2106-05-153 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Wastemaster Inc |  | Timothy | Jenkins | 2.000000 |  | PuraFlo |  | Pump | Gravity | Discharge | Chlorination |  | [] | [] |  | Musty | Clear | 7.200000 |  |  | 2.200000 | [11 empty] | Cable across driveway. Unable to access trash and pump tank | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 09/03/2020 | 01:35 PM
05/04/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | SES MidAtlantic LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/15/2021 | 09:00 AM
06/17/2020 |  |  | 08-142-0360 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Puraflo | [6 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 09/17/2020 | 12:00 AM
03/16/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Fairfax | Hott, Joshua D. | 1942001301 | Joshua | Hott | 1.000000 | 1500 | Septic Tank Only | Puraflo | Pump | Distribution Box | Aggregate Trench | None |  | ["Effluent Screens"] | ["Effluent Screens"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/18/2020 | Jan 1 1900 3:06PM
10/01/2020 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump | Drip | Elevated Sand Mound | UV Light |  | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 10/01/2020 | Jan 1 1900 2:00PM
04/21/2020 |  | Routine, Scheduled |  | Northumberland County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Three Rivers | Thomas W. Beasley Septic Contractor |  | Thomas | Beasley | 3.000000 |  | EcoPod |  | Pump | Distribution Box | Aggregate Trench |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [5 empty] | 0.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/21/2020 | 05:00 PM
03/09/2020 |  | Routine, Scheduled | 01-197-286 | Wise County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Lenowisco | DEEL, DENNY M | 1942001097 | DENNY | DEEL |  |  | Multiflo ATU | None | Gravity | None | Alternative Discharge | Chlorine | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection"] |  | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/16/2020 | Jan 1 1900 1:21PM
10/19/2020 |  | Reportable Incident |  | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | [9 empty] | ["Level Sensor Operation"] | ["Level Sensor Operation"] | NO | [17 empty] | Service call only: Alarm-Found off float completely disconnected, on time set for 25 min. instead of 25 sec. and floats were narrow angle instead of wide angle/ Replaced both off float and timer enable float with wide angle floats/ checked pump gpm and it is close to original rate so the timer was set for 25 sec. pumping to the puraflo modules. Changed peak off back to normal 1h 30m | This AOSS should now return to normal function after having provided the above state routine maintenance. |  |  | 12:00 AM
03/18/2020 |  | Routine, Scheduled |  | Prince William County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Prince William | SEAMON, CHARLIE L | 1942001108 | CHARLIE | SEAMON |  |  | Septic Tank Only | Microfast | Pump | Distribution Box | Aggregate Trench | None |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | [8 empty] | 03/18/2020 |  | 58.000000 | [5 empty] | Attached to this report |  | [Comments]: Performance Inspection & Sample: Microfast to Drainfield.Septic-6"sludge 2"scum/Fast-0"sludge Pump tank-0"sludge. No pump out needed at this time. Changed run time to 6m 46s for plan dose of 244 gal. due to pump current rate of 36 gpm.Peak-0 High-7/Pump cnts-63/ETM-4h 52m. Blower air filter cleaned.No breakout or spongy areas on the field. VENIS File Names: Finish Line Dr. 3532.pdf | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/08/2020 | 08:53 AM
06/04/2020 |  | RoutineScheduled | 061-16-250 | Fauquier | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 5.000000 |  | Bio Barrier | Bio Barrier | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Level Sensor Operation"] | ["Control Operation" ,"Level Sensor Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Biweekly inspection. Added a peak float to the surge tank and reduced the dose to 350 gals to allow for more treatment. In the past 7 days, the system pumped an average of 894 gals/day for a total of 6,258 gals to the drip field. Approximately 22,795 gallons were recirculated, and 19,448 gallons dosed to the Nitrifast unit. | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
03/06/2020 |  | Routine, Scheduled | SWP-02-33 | Stafford County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001350 | Mike | Cook |  |  | Orenco Advantex | None | Pump | Distribution Box | Aggregate Trench |  |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | [18 empty] | [Comments]: Will resend proposal for new lid and vent. Must be done | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/18/2020 | 06:42 AM
05/11/2020 | Alternative | RoutineScheduled | 166-18-0156 | Northumberland | This AOSS is functioning as designed and in accord | Approved | EHD - Three Rivers | [13 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accord |  |  | 12:00 AM
04/03/2020 |  | Routine, Scheduled |  | Loudoun County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim |  |  | None | None | Pump | [7 empty] | YES | YES | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/12/2020 | 02:21 PM
11/04/2020 | Alternative | Follow-Up | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Soils, Inc. | 1942001004 | Markham | Smith | 2.000000 | 1500 | MircFast model .75 ATU |  | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Attached Growth Medium","SludgeScum Accumulation","Level Sensor Operation","BlowerCompressorAerator Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 11/06/2020 | Dec 30 1899 12:00AM
07/22/2020 |  | Routine, Scheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Clearstream |  |  |  |  | None |  | ["Blower/Compressor/Aerator Operation"] | ["Blower/Compressor/Aerator Operation"] |  | Good | Clear | [15 empty] | Pump 1 Amps 10.08 ETM 82.39 Cycles 1056 Pump 2 Amps 10.15 ETM 81.38 Cycles 1034 Septic Sludge 10" Scum 0 ATU Sludge 0 Scum 0 Pump Sludge 1" Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 07/22/2020 | Jan 1 1900 9:48AM
02/14/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Payment | EHD - Loudoun | Loudoun Water | 1942001460 | Raymond | Kirkpatrick | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  |  |  | NO | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/28/2021 | 09:57 AM
07/11/2020 |  | RoutineScheduled | 177-18-350-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Aiternative Systems Inspection Services, LLC | 1942001047 | Wesley | Basore | 1.000000 | 500 | Aquasafe |  | Gravity | Pressure | Trenches | Not Applicable | 150.000000 | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Level Sensor Operation","Distribution Pump Operation","SludgeScum Accumulation","Effluent Screens"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation","Effluent Screens"] | YES | [7 empty] | 07/11/2020 | Pump Chamber | 27.000000 | [5 empty] | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 09/01/2020 | 07:10 PM
08/08/2020 |  | RoutineScheduled | 175-16-0043 | Prince William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Prince William | Wastemaster Inc |  | Timothy | Jenkins | 2.000000 |  | ATU | Effluent Filter | Pump | Gravity | Discharge | UV |  | ["Disinfection"] | [] | YES | Musty | Clear | 7.200000 | [14 empty] | Lead UV bulb burned out | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. |  | 09/02/2020 | 02:45 PM
09/24/2020 |  | RoutineScheduled | 39358 | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Greenway Engineering | 1942001008 | Jeremy | Ferguson | 1.000000 | 800 | Aquarobic Mini Plant | none | Pump | Gravity | Trenches | Not Applicable |  | ["Dispersal System Operation"] | ["Dispersal System Operation"] | NA | [17 empty] | Adjusted bottom line due to it receiving more than any other line causing it to be overloaded. Will check next year to make sure it has dryed up. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 09/28/2020 | 09:00 AM
05/28/2020 |  | RoutineScheduled |  | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic | 1942001301 | Josh | Hott | 1.000000 | 1500 | septic | puraflo | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | YES | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
06/26/2020 |  | Reportable Incident | C 800-17-0109 | Suffolk | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | Owner called due to septic leaking and gurgling. Pumping company came out and pumped out over 1000 gals. out - trash out of Clearstream and pumped and cleaned the pump tank. Replaced the relay and alarm float. Draw down test = 624 GPD. Timer is set to 7 minutes every 1.5 hours. Need to install check valve on pump and return. Run new conduit from panel to splice box and other repairs. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. |  | 06/26/2020 | Jan 1 1900 12:00PM
03/16/2020 |  | Reportable Incident | 06-142-0043 | Hanover County | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Chickahominy | Old Dominion Onsite, Inc. |  | John | Ewing |  |  | Microfast |  | Pump | Manifold | Drip Tubing |  |  | ["BlowerCompressorAerator Operation"] | [19 empty] | [Comments]: Blower is not working. Possible cause is direct bury wire supplying power. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 03/16/2020 | Jan 1 1900 4:59AM
03/03/2020 |  | Routine, Scheduled | SD-05-112 | Fauquier County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Puraflo | None | Pump | Distribution Box | Aggregate Trench |  |  | ["Control Operation","Distribution Pump Operation","Level Sensor Operation"] | ["Control Operation","Distribution Pump Operation","Level Sensor Operation"] | [18 empty] | [Comments]: Peat had more puddles this year with some slimy gray regrowth starting. Peat is fairly compacted and hard to tell if it is effectively treating the wastewater. Recommend replace by year end. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/04/2020 | 05:31 AM
06/08/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Septic tank was dug up to inspect no risers. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/14/2021 | 04:27 PM
03/24/2020 |  | Routine, Scheduled | 08-183-181 | Russell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Cumberland Plateau | DEEL, DENNY M | 1942001097 | DENNY | DEEL |  |  | Norweco Singulair ATU | None | Gravity | None | Alternative Discharge | Chlorine | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens"] |  | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/30/2020 | Jan 1 1900 5:22PM
11/05/2020 |  | Routine, Scheduled | 175-18-0404 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Orenco Advantex |  |  |  |  | None |  | ["Effluent Screens","Recirculation Pump"] | ["Effluent Screens","Recirculation Pump"] |  | Acceptable | Clear | [15 empty] | Spin filter cleaned. Pump Amps 11.61 ETM 231 hrs Cycles 41562 Pump Amps 9.69 ETM 273 hrs Cycles 1573 Water Meter Reading 86200 Septic Sludge 4" Scum 4" ATU Sludge 3" Scum 0 Pump Sludge 1" Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 11/05/2020 | 09:44 AM
05/13/2020 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Aquarobic Services | 1934000142 | Michael | Blake |  |  | none | none | Pump | Gravity | Mound | Not Applicable |  | ["Auxiliary Filter" ,"Control Operation"] | ["Auxiliary Filter" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Annual inspection. Air pre-filter cleaned and filter for blower canister filter replaced as routine maintenance. Found terminal screw #4 loose when checking terminal screws, tightened it. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 07/01/2022 | 10:30 AM
01/21/2020 |  | Routine, Scheduled |  | Prince William County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Prince William | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 2.000000 |  | None | None | Pump | Drip | Drip Tubing |  |  | ["Control Operation","Distribution Pump Operation"] | [19 empty] | [Comments]: Dripfield is overgrown, could not locate air release valves. Based on flow rates, at least one check valve in dripfield is not closing. All 4 zone indicator lights in control panel are not working. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/28/2020 | 01:39 PM
08/10/2020 |  | Routine/Scheduled |  | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Microfast |  | Pump |  |  |  |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  |  | 8.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 08/10/2020 | Jan 1 1900 1:00PM
08/01/2020 |  | RoutineScheduled | 153-STS-20182 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Wastemaster Inc |  | Timothy | Jenkins | 2.000000 |  | PuraFlo |  | Pump | Gravity | Discharge | UV |  | [] | [] |  | Musty | Clear | 6.900000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 08/27/2020 | 12:25 PM
11/20/2020 |  | RoutineScheduled | SD-13-153 | Fauquier | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Control Operation"] | ["Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Attached Growth Medium" ,"Control Operation"] | YES | [15 empty] | Will be sent separately | Inspected | Cleaned massive roots from sample box and applied root kill. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
10/22/2020 |  | RoutineScheduled |  | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001301 | Joshua | Hott | [9 empty] | [] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
06/24/2020 |  | RoutineScheduled | SR 03- | Spotsylvania | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Recirculation Pump" ,"SludgeScum Accumulation"] | ["Attached Growth Medium" ,"Recirculation Pump"] | NA | [15 empty] | Will be sent separately | Inspected | We recommend pumping the Septic Tank and the Advantex Tank due to scum & sludge accumulation. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/09/2021 | 03:25 PM
05/28/2020 |  | RoutineScheduled |  | Warren | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity |  | Not Applicable |  | ["Control Operation" ,"BlowerCompressorAerator Operation"] | ["Control Operation" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/26/2021 | 09:04 AM
03/16/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Fairfax | Hott, Joshua D. | 1942001301 | Joshua | Hott | 1.000000 | 1500 | Septic Tank Only | Puraflo | Pump | Distribution Box | Aggregate Trench | None |  | ["None"] | ["None"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/14/2020 | Jan 1 1900 1:10PM
08/14/2020 |  | Routine, Scheduled | 175-06-0480 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Puraflo |  |  |  |  | None |  | ["Effluent Screens"] | ["Effluent Screens"] | [18 empty] | Pump Amps 10.38 ETM 22810 h Cycles 14813 Septic Sludge 8" Scum 2" Pump Sludge 0 Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 08/14/2020 | 03:20 PM
03/05/2020 |  | Routine, Scheduled |  | Mathews County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Three Rivers | Farmer’s Septic Service, Inc. |  | Ross | Cole | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | [Comments]: Serviced system. Checked the pump, panel, & floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. There is roots in the pump tank - got them out. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/05/2020 | 12:00 PM
02/12/2020 |  | Routine, Scheduled |  | Loudoun County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | None | Pump | Distribution Box | Aggregate Trench | [23 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/02/2020 | 04:43 AM
09/08/2020 |  | Routine/Scheduled | 1990-143-0273 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Henrico | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | Sandfilter, High rate | None | Gravity | None | Alternative Discharge | Chlorine | 300.000000 |  | ["Disinfection","Distribution Pump Operation","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | None | Clear | [15 empty] | Quarterly inspection Septic tank in normal operating level Sand filter dosing tank in normal operating level - pump & float sensors operating properly. Added 4 tablets to chlorinator | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 09/09/2020 | 07:15 AM
04/01/2020 |  | Routine, Scheduled | 16-100-0212 | Accomack County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Eastern Shore | DUER, PETE C | 1942001051 | PETE | DUER | 1.000000 | 1000 | Septic Tank Only | Aqua Safe ATU | Pump | None | None | None |  | ["None"] | ["None"] | [18 empty] | [Comments]: Aoss Inspection. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/02/2020 | 12:20 PM
11/28/2020 |  | RoutineScheduled | SD-13-089 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC |  | Jason | Brown | 1.000000 | 1000 |  | Aquaworx | Gravity | Gravity | Trenches | Not Applicable |  | [] | [] | YES | Musty | Cloudy | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 03:25 PM
07/08/2020 |  | Follow-Up | SWP-05-156 | Stafford | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Septic and pump tank pumped out by others. Degraded peat was removed by hand and new peat was installed. Peat was purchased from Vamac and degraded peat was disposed at Spotsylvania Refuse. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
06/08/2020 | Alternative | RoutineScheduled | 115-05-0226 | Campbell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Septic Tank | Ecoflo | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","Effluent Screens"] | ["Attached Growth Medium","Effluent Screens"] | YES | Musty | [15 empty] | Inspected | Sludge level-14" Sludge in Septic tank 10" Sludge in Pump tank Peat Looks good for age- Peat was moist on one side and had minor ponding on the other. Turned and broke up peat and it drains well. Raked all 4 quadrants. Alarm and pump are operational | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 06/08/2020 | 05:30 PM
06/18/2020 |  | RoutineScheduled | SD-03-111 | Orange | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Effluent Screens" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Effluent Screens" ,"Recirculation Pump"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 |  | 04/09/2021 | 03:25 PM
01/16/2020 |  | Routine, Scheduled | 234-17-173 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesapeake | R & K Septic, Inc. |  | John | Butt, Jr |  |  | Clearstream ATU |  | Pump | Drip | Elevated Sand Mound | UV Light |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] |  |  | 8.36 | 7.530000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/16/2020 | Jan 1 1900 1:45PM
06/23/2020 | Alternative | Routine/Scheduled | 151-12-0052 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 1.000000 | 1250 | Puraflo |  | Gravity | None | Aggregate Bed |  |  | ["Attached Growth Medium","Dispersal System Operation","Effluent Screens","Septic Tank Baffles","Sludge/Scum Accumulation"] | ["Attached Growth Medium","Dispersal System Operation","Effluent Screens","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 06/23/2020 | 01:00 PM
12/03/2020 |  | RoutineScheduled | 00-197-224 | Wise | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Mound | Not Applicable | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","Effluent Screens"] | ["BlowerCompressorAerator Operation","Control Operation","Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
04/10/2020 |  | Routine/Scheduled | 07-174-0083 | Prince George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Crater | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1250 | Microfast | None | Pump | Drip | Drip Tubing | None |  |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | Septic Tank cast in section and Lid were buried, and the Lid was found cracked; Air Compressor was not functioning properly, and Control Panel Breaker was tripping; the Discharge Tank has root infiltration, the Pump is not properly set in Tank, and LB was found broken on outside of the Tank causing a leak | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/13/2020 | Jan 1 1900 2:51PM
06/23/2020 |  | RoutineScheduled |  | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/Microfast | Pump Tank | Pump | Pressure | Drip |  |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [17 empty] | Septic-0"sludge 0"scum/ Microfast-0"sludge/Pump Tank-0"sludge. No pump out needed. Counts: High-8/Hand-2/Override-8/Pump Starts-618/Pump Run-47/Water Meter-0029283/ Blower air filter cleaned. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
05/12/2020 | Alternative |  | 151-13-0152 | Lancaster | This AOSS is functioning as designed and in accord | Approved | EHD - Three Rivers | [13 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accord |  |  | 12:00 AM
08/31/2020 |  | Follow-Up | 179-10-0136-SP | Stafford | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | EcoPod | none | Pump | Pressure | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Dug up zone 1 check valve, didn't find anything wrong. Probably had debris that cleared itself. Tested and it is working now. Raised dirt around zone 2 valve so lid stays on valve box. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
08/22/2020 |  | RoutineScheduled | 133 16 0164 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1000 | Advantex |  | Gravity | Gravity | Trenches |  |  | ["None"] | ["None"] | [18 empty] | 12" of solids in septic tank. Cleaned septic tank filter. Flushed treatment unit spray manifold. Tested floats, pump and alarm. Discussed plumbing in basement bathroom. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 10/15/2020 | 07:03 PM
12/08/2020 |  | RoutineScheduled | 05-137-0308 | Goochland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Advantex | [6 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 01/04/2021 | 12:00 AM
06/05/2020 | Alternative | Routine/Scheduled | 073-STS-93943 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001063 | K.R. Trapper | Davis | 2.000000 | 1750 | None | None | Gravity | Distribution Box | Aggregate Trench | None | 450.000000 |  | ["Dispersal System Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | [17 empty] | Two septic tanks pumped for absorption field evaluation and real estate inspection. Residence currently has two separate COSS on the property. Older system, permitted 1971 - 750g Septic Tank, Distribution Box and three absorption laterals to be abandoned in place and disconnected from residence. Newer system permitted 1983 for a 3 BR peak flow - 1000g Septic Tank, Distribution Box and four absorption laterals to remain in place ... | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 06/10/2020 | 07:00 AM
06/10/2020 |  | Reportable Incident |  | Mathews | This AOSS should now return to normal function after having provided the above state routine maintenance | Pending Review | EHD - Three Rivers | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 750 | None | None | Pump | Distribution Box | Aggregate Trench | None | 450.000000 | ["Distribution Pump Operation"] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | [17 empty] | Emergency pumpout - discharge pump failure. Alarm event - discharge pump failure - septic tank and pump basin pumped empty - failed discharge pump replaced with new Liberty 240. | This AOSS should now return to normal function after having provided the above state routine maintenance |  | 07/15/2019 | 8:00AM
11/23/2020 |  | Routine/Scheduled | 234-15-005 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | Serviced system. Checked the pump, panel, & floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream, changed the filter in the aerator, installed a new mesh screen in the spinfilter, and replaced the UV light bulb. The timer is set to 5 minutes every 1 hour. There is visible wetness on the drainfield - most likely from rain - need to keep an eye on it. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 11/23/2020 | Jan 1 1900 12:00PM
07/28/2020 |  |  | 07-142-0155 | Hanover | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Delta Whitewater | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [18 empty] | Replace blower | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 05/01/2021 | 12:00 AM
06/18/2020 |  | RoutineScheduled | SD-07-039 | Orange | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Recirculation Pump" ,"Attached Growth Medium"] | ["Effluent Screens" ,"Recirculation Pump" ,"Attached Growth Medium"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 |  | 04/09/2021 | 03:25 PM
10/07/2020 |  | RoutineScheduled | 175-19-0058 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ EZ-Treat Recirculation Tank | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["None"] | ["None"] | NO | [17 empty] | Septic-4"sludge 0"scum/ Recirc-0"sludge/ Pump tank-0"sludge/ Counts: Pump-222 ETM-14h 15m/ Peak-0 (n/a) high-9 / replaced alarm bulb/ No breakout or spongy areas on the drainfield. System does not need a pump out. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
02/14/2020 |  | Routine, Scheduled |  | Fairfax City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Fairfax | JENKINS, TROY C, JR | 1942001050 | TROY | JENKINS |  |  | Septic Tank Only | Septic Tank Only | None | None | None | None | 964.000000 | [5 empty] | 6.800000 |  |  |  |  | 02/14/2020 | Effluent PS | 23.000000 |  |  | 36.300000 | 51.570000 |  | Attached to this report |  | [Pumpout Comments]: Pumped out to fix pump | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/13/2020 | Jan 1 1900 10:11AM
05/06/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Loudoun | SES MidAtlantic LLC | 1942001203 | James | Green | 1.000000 |  | Biomicrobics MicroFAST | Biomicrobics MicroFAST | Gravity | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/15/2021 | 09:00 AM
05/20/2020 |  | RoutineScheduled | 069050800 | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Greenway Engineering | 1942001008 | Jeremy | Ferguson | 1.000000 | 1000 | LPD | none | Pump | Pressure | Trenches | Not Applicable |  | ["Level Sensor Operation","SludgeScum Accumulation"] | ["Level Sensor Operation","SludgeScum Accumulation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 07/22/2020 | 10:45 AM
09/14/2020 |  | RoutineScheduled | 061-16-250 | Fauquier | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 5.000000 |  | Bio Barrier | Bio Barrier | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | ["Level Sensor Operation" ,"Control Operation" ,"Distribution Pump Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Biweekly inspection. Dripfield grass almost waist-high, could not check air release valves or tell if any effluent had been surfacing. Surge dosing pump #1 pulling high amps and not pumping any water. Removed pump and set panel to run on only pump #2. In the past 19 days, an average of 3,218.6 gals/day at 244.6 gals/dose (avg.) was pumped to the dripfield for a total of 61,154 gallons. Average daily flow has dropped significantly since the sewer line was repaired at Ross Industries. Treatment still not hitting nitrogen limits so system considered not operating as designed. | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
02/21/2020 |  | Routine, Scheduled | 177-06-0309-SWP | Spotsylvania County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | EcoPod | None | Pump | Drip | Drip Tubing |  |  | ["Attached Growth Medium","Distribution Pump Operation","Effluent Screens"] | ["Attached Growth Medium","Distribution Pump Operation","Effluent Screens"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/06/2020 | 02:45 PM
02/17/2020 |  | Routine, Scheduled |  | Mathews County | This AOSS should now return to normal function after having provided the above stated routine maintenance. | Paid | EHD - Three Rivers | Farmer’s Septic Service, Inc. |  | Ross | Cole | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | [Comments]: Serviced system. Checked the pump, panel, & floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream, changed the filter in the aerator, and replaced the UV light bulb. The timer is set to 6.5 minutes every 2 hours. | This AOSS should now return to normal function after having provided the above stated routine maintenance. |  | 02/17/2020 | 12:00 PM
10/31/2020 |  | Reportable Incident | SD-11-312 | Fauquier | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | System in high level again. Effluent up into the risers in septic tank and RT pod nearly full. Poor treatment because recirc pump locked out by high level in discharge basin. System potentially would be doing better with a 1,000 gal pump tank instead of the 24" pump basin. Observed all air release valves were weakly pressurized on arrival (pump not running). System pumps downhill so pump prone to siphoning. In hindsight, this siphoning may have been what damaged the zone diaphragm earlier this year and several years ago. The drip return manifolds are buried a foot or more below the drip tubing. This prevents the manifolds from draining and impedes proper venting. No further diagnosis can be made without the addition of a flow meter. Recommend pump out of tanks to help speed up recovery from the high level alarm and prevent a backup in the house. | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
12/03/2020 |  | Routine/Scheduled | 06-120-0704A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesterfield | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | PremierTech, EFX |  | Pump | Distribution Box | Aggregate Trench | None | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | Musty | Clear | [15 empty] | Routine Service Primary Septic Tank - normal level - effluent screen serviced. Biofilter - fiberglass - intact - peatmoss in good condition - raked / turned. Pump Basin - plastic - intact - pump, float sensors and controls operating properly. Distribution Box - concrete - lid fractured - all laterals accepting effluent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 12/04/2020 | Jan 1 1900 7:30AM
08/13/2020 |  | Follow-Up | 061-18-432 | Fauquier | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [9 empty] | 10.000000 | [5 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
07/20/2020 |  | RoutineScheduled | 099-15-0094 SR | King George | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation" ,"Level Sensor Operation" ,"BlowerCompressorAerator Operation"] | ["Level Sensor Operation" ,"BlowerCompressorAerator Operation" ,"Distribution Pump Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Pump failed and pump tank got into high level. Alarm did not activate because high level alarm float failed in the off position. Replaced float and pump. New pump tested at 37 gpm. High level count at 218, low level at 23. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
04/27/2020 |  | Routine, Scheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Biomicrobics MicroFAST |  |  |  |  | UV Light |  | ["Blower/Compressor/Aerator Operation"] | ["Blower/Compressor/Aerator Operation"] |  | Good | Good | [5 empty] | 04/27/2020 | Pump tank | 11.000000 |  | 1600.000000 | [5 empty] | Spin filter cleaned. Pump Amps 8.43 ETM 90 h Cycles 25 Septic Sludge 8" Scum 0 ATU Sludge 7" Scum 0 Pump Sludge 0 Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/27/2020 | Jan 1 1900 11:40AM
02/21/2020 |  | Routine, Scheduled |  | Warren County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Lord Fairfax | Ferguson, Jeremy | 1942001008 | Jeremy | Ferguson | 1.000000 | 1500 | Orenco Advantex | None | Pump | Manifold | Aggregate Trench | None | [21 empty] | [Comments]: system is operational and is working as intended. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/24/2020 | 10:49 AM
11/04/2020 |  | RoutineScheduled | SP-05-400 | Stafford | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"Recirculation Pump" ,"SludgeScum Accumulation"] | ["Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"Recirculation Pump"] | NA | [15 empty] | Will be sent separately | Inspected | On site for annual inspection and to investigate alarms. Pump tank still in high level. Everything working at this time, but 3 points of groundwater infiltration were observed. End of one strut for Advantex pod is broken off, needs new strut. Will send proposal to reseal areas leaking and to replace gas strut. Owner to make arrangements to pump out recirc tank and pump tank. Sent note to owner to advise OP has not been issued. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
04/23/2020 |  | RoutineScheduled | 09-163-0059 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | GeoEnvironmental Services, Inc. | 1942001010 | Peter | Mamunes | 1.000000 | 1250 | Clearstream |  | Pump | Pressure | Trenches | Not Applicable | 600.000000 | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 06/18/2020 | Jan 1 1900 4:20PM
10/23/2020 |  | Routine/Scheduled | 15-160-0167 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Orenco Advantex |  | Pump | Distribution Box | Gravel-Less Trench | None |  | ["None"] | ["Control Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Recirculation Pump","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 10/23/2020 | 12:00 PM
10/05/2020 |  | Routine/Scheduled | 05-174-0007 | Prince George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Crater | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. |  |  | Best 1 |  | Pump |  |  |  |  | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 10/05/2020 | Jan 1 1900 12:00PM
03/02/2020 |  | Initial Visit | S 800-19-0072 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | Owners called due to having an alarm - muted it. Serviced system. Checked the pump, panel, & floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. Replaced the pump union in the pump tank. Pumped it down till alarm went off. The timer is set to 1.5 minutes every 2 hours. Could not take initial sample due to the system being flooded. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 03/02/2020 | Jan 1 1900 12:00PM
09/10/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Best 1 | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | There is a 3" pipe coming in the riser from what appears to be an RV pad. Previous reports had mentioned it. Recommend capping line and replacing the riser. There is some corrosion in the control panel. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/27/2021 | 01:26 PM
09/14/2020 |  | RoutineScheduled |  | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Soils, Inc. | 1942001004 | Markham | Smith | 3.000000 | 2000 | 2 Advantex Ax20 Modules |  | Pump | Pressure | Trenches | Not Applicable |  | [] | ["Control Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 09/16/2020 | Jan 1 1900 11:00AM
02/06/2020 |  | Reportable Incident | 179-16-0068-SWP | Stafford County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | None | None | Pump |  |  | UV Light |  | ["Control Operation","Distribution Pump Operation","Level Sensor Operation"] | ["Control Operation","Distribution Pump Operation","Level Sensor Operation"] | [18 empty] | [Comments]: Tenant said panel started alarming again. This time, water level was low, almost in low level alarm status. Panel indicated 15 low level alarms and 3 high level alarms since last visit 5 weeks ago. Timer float was stuck on, replaced it. Observed steady inflow of water through spin filter ball valve and even heavier inflow through return to septic line in pump tank. Pump had not run in the past hour so any residual water in the pipes should have long since drained. Ground was saturated and more rain was falling. Added spring check valve on pump line after filter housing which stopped flow back through the filter housing. Need to do the same thing on return to septic line but with a stronger spring check valve. Will return in drier weather. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  |  | 05:59 AM
03/10/2020 |  | Routine, Scheduled | 033-12-0131-SWP | Caroline County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001350 | Mike | Cook | 1.000000 |  | Orenco Advantex | None | Pump | Distribution Box | Aggregate Bed |  |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/16/2020 | 06:19 AM
01/21/2020 |  | Routine, Scheduled | 38216 | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Lord Fairfax | Cubbage, Harrison Lee, II | 1942001021 | Harrison | Cubbage | 1.000000 | 1500 |  | Biomicrobics MicroFAST | Pump | Drip | Drip Tubing | None |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation"] |  | Musty | Clear | [15 empty] | [Comments]: Sludge/Scum Accumulations: Comp.1-11"/1" Comp.2- 11"/0" Pump Tank-6"/0" Pump Settings: Off 128min On 15min | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/31/2020 | 11:53 AM
05/12/2020 |  |  | 11-125-041 | Dickenson | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 05/12/2020 |  | 5.710000 |  |  | 1.000000 |  |  | Attached to this report |  |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 05/12/2020 | 12:00 AM
09/09/2020 |  | Follow-Up |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Gravity | Gravity |  | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | A new d-box has been installed. The broken plastic riser has been replaced with a new one. And the float weights have been corrected. | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 |  | 04/14/2021 | 04:27 PM
01/08/2020 |  | Routine, Scheduled |  | Fluvanna County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Blue Ridge | CLARK, MICHAEL J | 1934000023 | MICHAEL | CLARK |  |  | Septic Tank Only | Septic Tank Only | None | None | None | None |  |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/14/2020 | 03:31 AM
03/11/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Biomicrobics MicroFAST |  | Pump |  |  | None |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] |  | Good | Clear | [15 empty] | [Comments]: Pump Amps 6.35 ETM 5h 57mSeptic Sludge 1" Scum 2’Pump Sludge 0 Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/11/2020 | Jan 1 1900 12:59PM
04/18/2020 |  | Routine, Scheduled | 171-09-0131 | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Lord Fairfax | DOVEL, JERRY A | 1942001116 | JERRY | DOVEL | 1.000000 |  |  | Septic Tank Only | None | Drip | None | None | [22 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/22/2020 | 10:03 AM
04/10/2020 |  | RoutineScheduled |  | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | [9 empty] | ["Dispersal System Operation"] | ["Dispersal System Operation"] | [18 empty] | Septic/ATU had 6" sludge 4" scum ATU had 0' scum 4" sludge Pump tank had 0" scum 0" sludge Pump cnts-3339 ETM-619h 36m Peak-273 ETM-7h 6 m Zone#1-1672 Zone#2-1665 W/M-0213726.90 Check valves on common return were cleaned, air filter was cleaned Grass over Drain Field should be mowed | This AOSS should now return to normal function after having provided the above state routine maintenance. |  |  | 12:00 AM
02/13/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Fairfax | MCKIM, STEPHEN E | 1934000043 | STEPHEN | MCKIM |  |  | Septic Tank Only | Septic Tank Only | None | None | None | None |  |  | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/15/2020 | Jan 1 1900 3:51PM
12/18/2020 |  | RoutineScheduled | 175-00-0896 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Prince William | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 2.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | ["Auxiliary Filter" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Annual inspection. Zoner valve rotated correctly, no leaks. Advised owners to try to insulate the enclosure to protect the valve from freezing (such as putting a large pile of hay or mulch over it). Replaced filter on air compressor. Drip rates are much slower than at startup. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
09/30/2020 |  | Routine/Scheduled |  | Southampton | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Whitewater ATU |  | Pump | Distribution Box |  | None |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  |  | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 09/30/2020 | Jan 1 1900 11:30AM
03/03/2020 |  | Pump-Out Only |  | Warren County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Lord Fairfax | POWELLS PLUMBING, INC. | 1942001036 | Kurt | Holthaus |  |  | Delta Environmental Products, DF Series | [6 empty] | ["SludgeScum Accumulation"] | ["SludgeScum Accumulation"] | [18 empty] | [Comments]: Pumped septic. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/03/2020 | 03:06 PM
04/17/2020 | Alternative | Routine/Scheduled | 166-07-128 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001063 | K.R. Trapper | Davis | [11 empty] | N/A | [17 empty] | At the time of maintenance, the service expert found that the septic tank was at normal level with no solids and 5" of sludge. When inspecting the pump tank, the customer had concerns about an alarm that had gone off and. Found that the floats were too close together sot hey were adjusted during this visit. When inspecting the peat chamber, he noted that there was minor root intrusion and the peat raked out well. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/17/2020 | 12:31 PM
11/03/2020 |  | Routine/Scheduled |  | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump | Distribution Box |  |  |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  |  | 7.000000 | 3.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 11/03/2020 | Jan 1 1900 10:30AM
10/08/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | SES MidAtlantic LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/15/2021 | 09:00 AM
03/12/2020 |  | Routine, Scheduled | 17-100-0422 | Accomack County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Eastern Shore | JENKINS, TROY C, JR | 1942001050 | TROY | JENKINS | 1.000000 | 6000 | Septic Tank Only | Biomicrobics MicroFAST | Pump | Drip | Drip Tubing | UV Light | 1600.000000 | ["None"] | ["None"] | [18 empty] | [Pumpout Comments]: System was not pumped out | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/14/2020 | 01:46 PM
11/23/2020 | Alternative | Routine/Scheduled | 151-00-325 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | Clearstream | None | Pump | Drip | Drip Tubing | None | 450.000000 |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | Musty | Clear | [15 empty] | Routine Service Primary Septic Tank - normal Operating level - effluent screen serviced. Aeration Tank - normal operating level - compressor serviced. Pump Tank - normal operating level - pump serviced, float sensors & controls operating properly Drip Headworks - srviced - drip screen serviced - field flushed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 11/24/2020 | 07:15 AM
04/11/2020 |  | Routine, Scheduled | SD-12-167 | Culpeper County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | JENKINS, TIMOTHY R | 1942001062 | TIMOTHY | JENKINS | 1.000000 |  | Multiflo ATU | Septic Tank Only | Pump | Drip | Alternative Discharge | Chlorine |  | ["None"] | ["None"] |  | Musty | Clear | 7.400000 | 6.700000 |  | 1.800000 | [12 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/22/2020 | 02:08 PM
03/05/2020 |  | Routine, Scheduled |  | Loudoun County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Loudoun | Triple R Construction Co., Inc. | 1934000238 | Charles | Seamon | 1.000000 |  | Biomicrobics MicroFAST | None | Pump | Distribution Box | Aggregate Trench |  |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | [10 empty] | 59.000000 | [8 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/26/2020 | 04:49 AM
07/20/2020 |  | RoutineScheduled | 043-03-321 | Clarke | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 2705110225 | Larry | Royston | [9 empty] | ["None"] | ["None"] | YES | [16 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 09/02/2020 | 12:00 AM
02/28/2020 |  | Follow-Up | 177-STS-87619 | Spotsylvania County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Biomicrobics MicroFAST | None | Pump | Drip | Drip Tubing | [22 empty] | [Comments]: Replaced Fast control panel. Pump out by others. After cleaning the tank bottom we discovered many cracks,the tank will need to be replaced. Proposal to be sent to homeowner. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/28/2020 | 11:14 AM
06/17/2020 |  | Routine/Scheduled | 800-STS-14487 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Western Tidewater | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 9000 | Advanced Septic |  | Pump | Distribution Box | Aggregate Trench | None | 4000.000000 |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Recirculation Pump","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | Musty | Clear | [5 empty] | 06/17/2020 | Aerration Tank | 28.000000 |  |  | 56.000000 | 28.110000 |  |  |  | Laboratory sample expected to be higher in BOD and TSS than usual, due to obtaining sample directly from ATU vs. Clarifier outfall. Routine monthly service conducted as per consent order. Septic / Flow Equalization tank in normal operating level - pumps pulled to check for "Ragging" ... Aeration tank in high level due to clog present in Clarifier outfall - clog cleared. - Discharge tank - pushed to high level condition due to clog in Clarifier outfall - system pumping out of high level on own. Laboratory samples pulled directly from ATU as normal location under water. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 06/29/2020 | Jan 1 1900 7:30AM
10/30/2020 |  | RoutineScheduled | 182-12-0213 | Rockingham | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Central Shenandoah | Onsite Wastewater Services - May Supply | 1942001627 | Drew | Shull | 1.000000 |  | none | none | Gravity | Gravity |  | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/28/2021 | 05:41 AM
09/14/2020 |  | RoutineScheduled | {FIPSCode}-STS-84675 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Recirculation Pump" ,"Attached Growth Medium"] | ["Effluent Screens" ,"Recirculation Pump" ,"Attached Growth Medium"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 |  | 04/09/2021 | 03:25 PM
09/04/2020 |  | RoutineScheduled | 179-16-0408-SWP | Stafford | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Septic Works LLC | 1942001080 | michael | smith |  |  | Orenco Advantex | none | Gravity | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/25/2021 | 08:10 AM
06/22/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/14/2021 | 04:27 PM
04/23/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Loudoun Enviromental | 1942001460 | Austin | Kirkpatrick |  |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NO | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/28/2021 | 10:17 AM
11/18/2020 |  | Routine/Scheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | POWELLS PLUMBING, INC. | 1942001036 | Kurt | Holthaus | [9 empty] | ["Dispersal System Operation"] | ["Dispersal System Operation"] | N/A | [17 empty] | Replaced 15 valves, flushed and balanced system. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12/31/2020 | 12:37 PM
10/20/2020 | Alternative | RoutineScheduled | 42334 | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | Musty | Clear | 7.170000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 11/06/2020 | 04:05 PM
01/07/2020 |  | Routine, Scheduled |  | Prince William County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Puraflo |  |  |  |  | Chlorine |  | ["Effluent Screens"] | ["Effluent Screens"] |  | Good | Tan | 5.890000 | 1.020000 | [13 empty] | [Comments]: Pump Amps 12.3 ETM 219.21 Cycles 1458Septic Sludge 3" Scum 1"Pump Sludge 0 Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/07/2020 | 12:39 PM
04/06/2020 |  |  | 12-113-163 | Buchanan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 04/06/2020 | [10 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 04/06/2020 | 12:00 AM
04/16/2020 | Alternative | Routine/Scheduled | 157-05-272 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1250 | Clearstream ATU | None | Pump | Distribution Box | Aggregate Trench | None |  |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | Aeration Riser had root infiltration, the Air Line was not serviceable (unable to evaluate/service the Diffuser), and the wiring to power the Alarm Float was not present; the Pump Relay has a loud buzzing sound indicating imminent failure | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/17/2020 | 04:05 PM
12/11/2020 |  | RoutineScheduled | 177-07-0050-SP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Attached Growth Medium"] | ["Attached Growth Medium" ,"Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 |  | 04/09/2021 | 03:25 PM
05/27/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | SEPTIC/ATU AND PUMP TANK NEED PUMPED OUT | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 |  | 04/14/2021 | 04:27 PM
12/09/2020 |  | Follow-Up |  | Fauquier | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Recommend have plumber replace all piping. Added clean out on lower basement sewer line per customer request. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
01/13/2020 |  | Routine, Scheduled | 181-17-0146 | Rockbridge County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Central Shenandoah |  |  |  |  | 1.000000 | 1000 |  | Orenco Advantex | Gravity | Distribution Box | Aggregate Trench | None |  | ["None"] | ["None"] | [18 empty] | [Comments]: Filter checked and cleaned. Pump screen cleaned. Textile sheets sprayed off and in good condition. All controls functioning properly. No apparent leaks in system or drain field area. System did not need to be pumped. Lids properly secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/13/2020 | 30-12-1899 01:52 AM
09/09/2020 | Alternative | Routine/Scheduled | 157-08-0247 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | Puraflo | None | Pump | None | Aggregate Bed | None | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | Musty | Clear | [15 empty] | Routine Service Conducted. Septic tank - normal operating level - effluent screen serviced. Pump tank - normal operating level - pump, float sensors and controls operating properly. Peatmoss Biofilter - good condition all modules opened, peatmoss turned / raked. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 09/10/2020 | 08:45 AM
07/23/2020 |  | Follow-Up | 2132-10-153 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green | [9 empty] | ["Disinfection"] | ["Disinfection"] | [18 empty] | Replaced 2 UV bulbs. | This AOSS should now return to normal function after having provided the above state routine maintenance |  | 07/23/2020 | 04:00 PM
12/07/2020 |  | RoutineScheduled | 069120114 | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax |  |  | Michael | Edmonson | 1.000000 | 1500 | Microfast | none | Pump | Pressure | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NO | [17 empty] | 12/7/20 blower was releveled. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 01/18/2021 | 11:10 AM
04/07/2020 |  | RoutineScheduled | 182-05-0316 | Rockingham | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Central Shenandoah | Onsite Wastewater Services - May Supply | 1942001022 | Sara | Tusing | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Pressure | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/28/2021 | 05:41 AM
10/19/2020 |  | RoutineScheduled | 12-142-0026 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | GeoEnvironmental Services, Inc. | 1942001010 | Peter | Mamunes | 2.000000 | 2500 | EZ Treat Sandfilter |  | Pump | Pressure | Drip |  |  | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Distribution Pump Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation"] | ["Effluent Screens","Level Sensor Operation","Distribution Pump Operation","Dispersal System Operation","Control Operation","Attached Growth Medium"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 10/26/2020 | Jan 1 1900 4:05PM
10/06/2020 |  | Routine, Scheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Biomicrobics MicroFAST |  | Pump | Drip | Drip Tubing | UV Light |  | ["Blower/Compressor/Aerator Operation","Disinfection"] | ["Blower/Compressor/Aerator Operation","Disinfection"] |  | Acceptable | Clear | [15 empty] | Spin filter cleaned. Pump Amps 7.79 ETM 495.31 hrs Cycles 3674 Water Meter Reading 182000 Septic Sludge 5" Scum 1" ATU Sludge 12" Scum 0 Pump Sludge 1" Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 10/06/2020 | Jan 1 1900 1:52PM
12/03/2020 |  | RoutineScheduled | SWP-05-39 | Stafford | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Attached Growth Medium" ,"Control Operation"] | ["Recirculation Pump" ,"Attached Growth Medium"] | NA | [15 empty] | Will be sent separately | Inspected | The junction box lid on the Pump Tank should be replaced. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/09/2021 | 03:25 PM
01/21/2020 |  | Follow-Up |  | Fairfax City | This AOSS should now return to normal function after having provided the above stated routine maintenance. | Approved | EHD - Fairfax | THOMAS, RONALD Ray | 1942001052 | RONALD | THOMAS | 1.000000 |  | Septic Tank Only | Septic Tank Only | Gravity | None | Alternative Discharge | Chlorine |  | ["None"] | ["None"] | [8 empty] | 01/21/2020 |  | 9.000000 |  | 1.000000 | 16.000000 |  |  | Attached to this report |  |  | This AOSS should now return to normal function after having provided the above stated routine maintenance. |  | 02/04/2020 | Jan 1 1900 8:40AM
11/23/2020 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump | Drip | Elevated Sand Mound | UV Light |  | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  | 7.64 | 4.630000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 11/23/2020 | Jan 1 1900 12:30PM
06/25/2020 |  |  | 06-195-272-Dis | Washington | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Mount Rogers | S.E.P.T.I.C., Inc. |  | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Effluent Screens"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
06/18/2020 |  | Routine/Scheduled |  | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Western Tidewater | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | Delta Environmental Products, UC Series | None | Pump | Distribution Box | Aggregate Trench | None | 450.000000 |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | Musty | Clear | [15 empty] | Routine Service - At the time of maintenance, the technician noted that all tanks were found at normal level. He also confirmed that all pumps and floats were functioning as they should. The technician reported that upon completion all components were functioning properly and the system was operational. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 06/19/2020 | Jan 1 1900 8:00AM
06/03/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/14/2021 | 04:27 PM
01/14/2020 |  | Routine, Scheduled | 179-14-0130-SWP | Stafford County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001350 | Mike | Cook | 1.000000 |  | None | None | Pump | Drip | Drip Tubing |  |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | [Comments]: Home owner will pump out system | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/16/2020 | 01:20 PM
08/31/2020 |  | Routine/Scheduled | 19-142-0042 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Old Dominion Onsite, Inc. | 1942001549 | Russell | Revis | [11 empty] | N/A | [9 empty] | 32.000000 | [7 empty] | took BOD sample. BOD: 32 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 08/31/2020 | Jan 1 1900 1:00PM
07/30/2020 |  | Routine/Scheduled |  | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Ecoflo |  | Pump |  |  | None |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  |  | 7.590000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 07/30/2020 | Jan 1 1900 10:00AM
04/23/2020 |  | RoutineScheduled | 179-13-0333-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Attached Growth Medium"] | ["Effluent Screens" ,"Attached Growth Medium"] | YES | [15 empty] | Will be sent separately | Inspected | The Septic Tank does not appear to be level, but this is difficult to evaluate further because there is only a riser on the outlet side. If a riser is installed on the inlet, the tank can be evaluated further and we can check to see if water is flowing freely into the tank. | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 |  | 04/09/2021 | 03:25 PM
01/09/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Fairfax | Hott, Joshua D. | 1942001301 | Joshua | Hott | 1.000000 | 1125 | Septic Tank Only | Puraflo | Pump | Distribution Box | Aggregate Trench | None |  | ["None"] | ["None"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/18/2020 | Jan 1 1900 3:36PM
12/21/2020 |  |  | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | McKim Construction | 1942001330 | Michelle | McKim | [9 empty] | [] | [] | [17 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 02/06/2021 | 12:00 AM
02/25/2020 |  | Follow-Up | 179-12-0203-SWP | Stafford County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001350 | Mike | Cook |  |  | Orenco Advantex | None | Pump | Distribution Box | [15 empty] | 47.000000 | [8 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/04/2020 | 05:31 AM
04/30/2020 |  | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 2705110225 | Larry | Royston | [9 empty] | ["None"] | ["None"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 08/12/2020 | 12:00 AM
11/16/2020 |  | RoutineScheduled | 41237 | Warren | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lord Fairfax | McKim Construction | 1942001330 | Michelle | McKim | 2.000000 |  |  |  | Pump | Gravity | Trenches |  |  | [] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12/18/2020 | 12:00 AM
08/05/2020 |  | Reportable Incident | 036-STS-34328 | Charles City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Old Dominion Onsite, Inc. | 1942001549 | Russell | Revis | [9 empty] | ["Dispersal System Operation"] | ["Dispersal System Operation"] | N/A | [17 empty] | responded to high recirc alarm. System components were OK, however the field seems to have flooded from the rain brought by the recent tropical storm. There are no signs of any lines bleeding out. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 08/05/2020 | Jan 1 1900 2:40PM
01/08/2020 |  | Routine, Scheduled |  | Fluvanna County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Blue Ridge | CLARK, MICHAEL J | 1934000023 | MICHAEL | CLARK |  |  | Septic Tank Only | Septic Tank Only | None | None | None | None |  |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/14/2020 | 03:26 AM
04/06/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Fairfax | BLEVINS, JOEL R, SR | 1934000415 | JOEL | BLEVINS |  |  | Microfast | Septic Tank Only | None | None | None | None |  | ["None"] | ["None"] | [18 empty] | [Comments]: Compressor is strong and cleaned the air filter. Ditches are dry. 4" of sludge in treatment tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/07/2020 | Jan 1 1900 12:20PM
05/22/2020 |  | RoutineScheduled | 87-67 | Clarke | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Combs Wastewater Management LLC | 1942001353 | Amy | Combs | 2.000000 | 600 |  |  | Pump | Pressure | Discharge | Not Applicable | 600.000000 | [] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 01/13/2021 | 12:00 AM
05/04/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/27/2021 | 01:26 PM
03/18/2020 |  | Routine, Scheduled | 177-09-0169-SP | Spotsylvania County | This AOSS should now return to normal function after having provided the above stated routine maintenance. | Approved | EHD - Rappahannock | JOHNSTON, JOSHUA C | 1934000089 | JOSHUA | JOHNSTON | 1.000000 | 1250 | Septic Tank Only | Puraflo | Pump | Distribution Box | Aggregate Trench | None | 400.000000 |  | ["Control Operation","Effluent Screens","Level Sensor Operation"] |  | none detected | weak tea | [15 empty] | [Comments]: Peat in the pods needs turned soon | This AOSS should now return to normal function after having provided the above stated routine maintenance. |  | 04/01/2020 | 10:28 AM
07/17/2020 |  | Reportable Incident | 10-120-0371A | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance | Approved | EHD - Chesterfield | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1500 | Norweco Singulair ATU | None | Pump | Drip | Drip Tubing | None | 450.000000 |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | Musty | Clear | [15 empty] | System alarming high level - found system in high level due to clogged drip disk filter - serviced. Found leak at headworks due to o-ring failure - repaired. Processing tank - aspirator serviced - effluent screen serviced. Discharge tank - high level due to clogged drip disk filter - disk filter serviced - system pumped out of high level - discharge pump serviced. | This AOSS should now return to normal function after having provided the above state routine maintenance |  | 07/20/2020 | Jan 1 1900 11:30AM
01/16/2020 |  | Routine, Scheduled |  | Northumberland County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Three Rivers | BEASLEY, THOMAS W | 1934000450 | THOMAS | BEASLEY | 2.000000 | 2000 | Puraflo | Septic Tank Only | Pump | Manifold | Aggregate Bed | None |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [5 empty] | 45.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/16/2020 | 03:30 PM
07/21/2020 |  | RoutineScheduled | -STS-20177 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 1.000000 |  | Septic/ Microfast |  | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [9 empty] | 8.000000 | [7 empty] | Septic-4"sludge 2"scum/ Microfast-0"sludge/ Blower air filter cleaned/ Settlement on two drainfield lines, returned on 7/27/2020 to add fill to the drainfield trenches where needed. No breakout or spongy areas on the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
12/02/2020 |  | RoutineScheduled | 069120225 | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax |  |  | Michael | Edmonson | 1.000000 | 1250 | Microfast | none | Pump | Pressure | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 01/01/2021 | 11:30 AM
12/11/2020 |  | Routine/Scheduled | 196-15-0009 | Westmoreland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 3.000000 | 3000 | EcoPod |  | Pump | Distribution Box | Aggregate Bed |  |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12/11/2020 | 04:00 PM
12/07/2020 |  | Follow-Up | 99-197-054 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | Wise Health Dept |  | Rodney Neece |  | 1.000000 |  | ATU |  | Gravity | Gravity | Discharge | Chlorination | [9 empty] | 0.000000 | Tabets are now present. | [11 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12/08/2020 | 12:00 AM
04/21/2020 |  | Routine, Scheduled |  | Lancaster County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Three Rivers | Thomas W. Beasley Septic Contractor |  | Thomas | Beasley | 4.000000 | 10000 | Advanced Septic |  | Pump | Manifold | Aggregate Bed |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [5 empty] | 50.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/21/2020 | 05:00 PM
03/17/2020 |  | Routine, Scheduled | SWP-04-728 | Spotsylvania County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Ware, Michele P | 1942001165 | Michele | Ware |  |  | Septic Tank Only | Septic Tank Only | None | None | None | None |  |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/19/2020 | 07:28 AM
04/02/2020 |  | Routine, Scheduled | 175-13-0134 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Biomicrobics MicroFAST |  |  |  |  | UV Light |  | ["Blower/Compressor/Aerator Operation"] | ["Blower/Compressor/Aerator Operation"] |  | Good | Clear | [15 empty] | Spin filter cleaned. Pump Amps 10.05 ETM 1143 Cycles 10389 Water Meter Reading 279210 Septic Sludge 6" Scum 12" ATU Sludge 6" Scum 0 Pump Sludge 1" Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/02/2020 | 08:35 AM
04/30/2020 |  | RoutineScheduled | 14-192-098 | Tazewell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. |  | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","Effluent Screens","Disinfection"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
02/27/2020 |  | Routine, Scheduled | 234-18-025 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesapeake | VANHOLTEN, CRAIG S | 1934000053 | CRAIG | VANHOLTEN |  |  | Septic Tank Only | Septic Tank Only | None | None | None | None | [11 empty] | 02/27/2020 |  | 22.000000 |  | 1.000000 |  |  |  | Attached to this report |  | BOD5 is out of range. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/27/2020 | Jan 1 1900 8:30AM
11/21/2020 |  | RoutineScheduled | {FIPSCode}-STS-18653 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Wastemaster Inc |  | Timothy | Jenkins | 2.000000 |  | ATU | EZ Treat | Pump | Gravity | Discharge | UV |  | [] | [] |  | Musty | Clear | 6.900000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12/09/2020 | 12:50 PM
12/15/2020 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Gravity | Gravity |  | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | A inspection on a conventional gravity septic system. The state requires that all conventional septic tanks must be pumped out every 5 years and filed with the state and county. There was 1 cleanout near the house. The sewer line was camera snaked and was clear. There are two septic tanks on the property. Both were dug up they were about 6" under the ground . Both tanks were pumped out and inspected. The conveyance line was camera snaked and was clear. The 6 port concrete splitter and both 8 port concrete d-boxes were dug up they were about 18" under the ground. All 10 header lines were camera snaked and the drain field was probed. At time of the inspection all components appeared to be in working condition. | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 |  | 04/14/2021 | 04:27 PM
10/03/2020 |  | RoutineScheduled | 109-18-0101 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1500 | Advantex |  | Pump | Gravity | Trenches |  |  | ["None"] | ["None"] | [18 empty] | 12" of solids in septic tank. Flushed treatment unit spray manifold. Tested floats, pumps and alarm. Cleaned septic tank filter. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 10/20/2020 | 07:03 PM
01/22/2020 |  | Routine, Scheduled | 159-11-039 | Middlesex County | This AOSS should now return to normal function after having provided the above stated routine maintenance. | Approved | EHD - Three Rivers | LANGFORD, CHARLES T | 1934000143 | CHARLES | LANGFORD | 1.000000 | 1000 | Clearstream | Septic Tank Only | Gravity | Distribution Box | Aggregate Bed | None |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | [18 empty] | [Comments]: REPLACE FITTING FROM BLOWER TO AIR LINE | This AOSS should now return to normal function after having provided the above stated routine maintenance. |  | 02/19/2020 | 08:43 AM
04/10/2020 |  | Routine, Scheduled |  | Albemarle County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Blue Ridge | CLARK, MICHAEL J | 1934000023 | MICHAEL | CLARK |  |  | Septic Tank Only | Septic Tank Only | None | None | None | None |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/12/2020 | 04:41 AM
11/05/2020 |  | RoutineScheduled | SWP-05-228 | Stafford | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Attached Growth Medium" ,"Control Operation"] | ["Distribution Pump Operation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Attached Growth Medium" ,"Control Operation"] | YES | [15 empty] | Will be sent separately | Inspected | Septic tank needs pumped out; massive amount of grease. Infiltration @ pump tank outlet pipe. Re-timed distribution box. Briars overgrown around pods, please keep cleared. 2 Puraflo lids are cracked w/ duct tape covering. Proposal to be sent to homeowner for infiltration. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
07/10/2020 | Alternative | Routine/Scheduled | 157-03-162 | Mathews | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | Serviced system. Checked the pump, panel, & floats (ok). Cleaned the filter in the Clearstream and cleaned the filter in the septic tank. Changed the diffuser in the Clearstream, changed the filter in the aerator, changed the mesh screen in the spinfilter, installed a re-build kit on the aerator, wired up the pressure switch for the aerator, repaired the K-Rain valve, replaced the Clearstream lid, replaced the 24" EZ set lid, replaced gauge on pump, and replaced the missing cover under the panel. Could not locate any valve boxes. Pumped out Clearstream tank. Timer is set to 11 minutes every 1 hour. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 07/10/2020 | 12:00 PM
11/05/2020 | Alternative | Routine/Scheduled | 151-09-0151 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | PremierTech, EFX |  | Pump | None | Aggregate Bed | None | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | Musty | Clear | [15 empty] | Routine service Primary septic tank - normal operating level - effluent screen serviced. Pump Basin - plastic - piggy back demand - pump, float sensor operating properly. Biofilter - peatmoss good condition - raked / turned Absorption bed - no indications of surfacing | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 11/06/2020 | 10:45 AM
02/03/2020 |  | Routine, Scheduled | 179-17-0126-SP | Stafford County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | None | Pump | Distribution Box | Aggregate Trench |  |  | ["Attached Growth Medium","Effluent Screens","Recirculation Pump"] | ["Attached Growth Medium","Effluent Screens","Recirculation Pump"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/02/2020 | 11:52 AM
07/29/2020 |  | RoutineScheduled | 177-06-0385-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Multiflo FTB | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"BlowerCompressorAerator Operation"] | ["Attached Growth Medium" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 |  | 04/09/2021 | 03:25 PM
03/19/2020 |  | Routine, Scheduled |  | Loudoun County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | None | Pump | Drip | Drip Tubing | [23 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/12/2020 | 02:21 PM
02/07/2020 |  | Routine, Scheduled | 069080378 | Frederick County | This AOSS should now return to normal function after having provided the above stated routine maintenance. | Approved | EHD - Lord Fairfax | Ferguson, Jeremy | 1942001008 | Jeremy | Ferguson | 1.000000 | 1000 | Puraflo | None | Pump | Drip | Drip Tubing | None |  | ["Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Effluent Screens","Level Sensor Operation"] | [18 empty] | [Comments]: The levels of sludge in the septic tank and 2nd pump tank are above the minimum recommendation in being pumped. The Peat moss is still operation and has life left to all units depending on household strengths and usage. additional comments below | This AOSS should now return to normal function after having provided the above stated routine maintenance. |  | 02/07/2020 | 06:32 PM
03/10/2020 |  | Routine, Scheduled | 033-07-0385-SP | Caroline County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001350 | Mike | Cook |  |  | Orenco Advantex | None | Pump | Distribution Box | Aggregate Trench |  |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/18/2020 | 06:42 AM
03/18/2020 |  | Routine, Scheduled | 171-06-0249 | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Lord Fairfax | Cubbage, Harrison Lee, II | 1942001021 | Harrison | Cubbage | 1.000000 | 1000 |  | Puraflo | Pump | Distribution Box | Aggregate Trench | None |  | ["Control Operation","Dispersal System Operation","Effluent Screens"] | ["Control Operation","Dispersal System Operation","Effluent Screens"] |  | Musty | Clear | [5 empty] | 03/18/2020 | Sample Port | 8.000000 | [5 empty] | Attached to this report |  | [Lab Comments]: Results Normal [Comments]: Pump Settings: Off 3hrs on 3min ETM-687.34Hr Cycle COunt-32498 Sludge/Scum Accumulations: Septic Tank- 10"/1" Pump Tank-2"/0" VENIS File Names: 10213 Supinlick Ridge Rd 3-18-20.pdf | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/06/2020 | 02:45 PM
08/26/2020 |  | Follow-Up | SD-01-604 | Culpeper | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | 8/10/20 Advantex pod was run over by truck. Cut out broken rod holders and custom made new holes and ordered new lid and seal. Installed new AX-20 pod lid and seal. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
07/16/2020 |  | RoutineScheduled | 179-19-0158-SWP | Stafford | This AOSS is not functioning as designed or in accordance with the performance/Maintenance requirements | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation"] |  | NA | [15 empty] | Will be sent separately | Inspected | There is an area in the dispersal field next to the manifold that is not ponding water, but is wet. We have contacted the installed. | This AOSS is not functioning as designed or in accordance with the performance/Maintenance requirements |  | 04/09/2021 | 03:25 PM
11/19/2020 |  | RoutineScheduled |  | Rockingham | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Control Operation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"SludgeScum Accumulation"] | ["Auxiliary Filter" ,"Control Operation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"SludgeScum Accumulation"] | NA | [7 empty] | 11/19/2020 | [7 empty] | Will be sent separately | Inspected | All tanks cleaned at time of service Replaced Discharge Pump Repaired RSV and pressure gauge NEW OWNER PLEASE CONTACT US !!!!! | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance |  | 04/26/2021 | 09:04 AM
01/16/2020 |  | RoutineScheduled | {FIPSCode}-STS-5420 | Buchanan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | DEEL, DENNY M | 1942001097 | DENNY | DEEL |  |  | Jet ATU | None | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection"] |  | Musty | Clear | [15 empty] | [Comments]: 5 Blue Crystal added | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 02/05/2020 | Jan 1 1900 3:04PM
12/08/2020 | Alternative | RoutineScheduled | 115-14-0009 | Campbell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Advantex AX20 |  | Pump | Pressure | Drip | Not Applicable |  | [] | ["Distribution Pump Operation","Effluent Screens"] | NA | Musty | [15 empty] | Inspected | Sludge levels-Scum layer 1-2" in. and 8" sludge in Septic tank #1 -Septic zone 1-2" scum and 5" Sludge. 1" Scum and 18" Sludge in Discharge zone of tank, May need to pump this portion. Upper tank effluent screen was backed up again and i reccomend replacing it with a larger effluent screen. Both Pumps are functional one drawing 13.4a and the other 12.8 amps, a bit high but functioning ok. pulled and cleaned both pumps, biofilter, brushed manifold, tested floats. Cleaned RSV and Flushed system. Reccomend pumping just the advantex system again 1500g, you can arrange pumping by calling Foutz septic 540 525 4505 and also letting us know. We also need to be onsite to remove components to allow access to pump out the discharge zone and reassemble the unit after pumping. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12/28/2020 | 05:30 PM
03/18/2020 |  | Routine, Scheduled |  | Loudoun County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | None | None | Gravity | Distribution Box | Gravel-Less Bed | [5 empty] | YES | YES | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/12/2020 | 02:21 PM
12/09/2020 |  | RoutineScheduled | 179-12-0086-SWP | Stafford | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Clearstream | none | Gravity | Gravity | Trenches | Not Applicable |  | ["Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Level Sensor Operation" ,"BlowerCompressorAerator Operation"] | ["Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Level Sensor Operation" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
10/05/2020 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump | Drip | Elevated Sand Mound | UV Light |  | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  | 4.72 | 6.960000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 10/05/2020 | Jan 1 1900 11:00AM
12/16/2020 |  | RoutineScheduled | 2031-96-153 | Prince William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Prince William | Wastemaster Inc |  | Timothy | Jenkins |  |  | Sequencing Bat Reactor | Sandfilter |  |  | Discharge | Chlorination |  | [] | [] |  | Musty | Clear | 7.700000 |  |  | 2.200000 | [11 empty] | Sandfilter pump has failed | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. |  | 12/16/2020 | 01:30 PM
12/01/2020 |  | RoutineScheduled | SD-91-119 | Clarke | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax |  |  | Michael | Edmonson | 1.000000 | 1000 | Septic tank only | none | Pump | Pressure | Trenches | Not Applicable |  | ["Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 01/01/2021 | 01:00 PM
12/08/2020 |  | Routine, Scheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Biomicrobics MicroFAST |  |  |  |  | UV Light |  | ["Blower/Compressor/Aerator Operation"] | ["Blower/Compressor/Aerator Operation"] |  | Acceptable | Clear | [15 empty] | Spin filter cleaned. Pump Amps 5.53 ETM 281 hrs 48 mins Cycles 3775 Water Meter Reading 67000 Septic Sludge 6" Scum 4" ATU Sludge 13" Scum 0 Pump Sludge 3" Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 12/08/2020 | Jan 1 1900 3:25PM
05/27/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | SES MidAtlantic LLC | 1942001236 | S. Michael | Lynn | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Disinfection"] |  | NA | [15 empty] | Will be sent separately | Inspected | UV Bulb Needs to be replaced. Owner will pay SES to replace | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 |  | 04/15/2021 | 09:00 AM
12/07/2020 |  | RoutineScheduled | 179-13-0174-SWP | Stafford | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Control Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Level Sensor Operation"] | ["Attached Growth Medium" ,"Control Operation" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Recirculation Pump"] | YES | [15 empty] | Will be sent separately | Inspected | 3 lines at distribution box have roots, we removed what we could get to. Check valve needs to be installed on discharge pump and root kill applied. BOD collected, waiting on results. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
07/17/2020 |  | RoutineScheduled | 179-STS-86725 | Spotsylvania | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | 90 DAY INSPECTION | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/09/2021 | 03:25 PM
04/23/2020 |  | RoutineScheduled | 10-100-0068 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Bundick Well & Pump | 1942001051 | Peter | Duer | 1.000000 | 1250 | Septic Tank | Purflo | Pump | Pressure | Pad | Not Applicable | 600.000000 | ["None"] | ["None"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 06/30/2020 | 03:50 PM
07/22/2020 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  |  | Drip | Elevated Sand Mound | UV Light |  | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  |  | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 07/22/2020 | Jan 1 1900 10:30AM
07/10/2020 |  | Follow-Up |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Lord Fairfax | Aquarobic Services | 1934000142 | Michael | Blake |  |  | none | none | Pump | Gravity | Mound | Not Applicable |  | ["Distribution Pump Operation"] | ["Distribution Pump Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Existing fiberglass manway removed and replaced with larger one. Removed loaner pump and installed new Goulds pump model LSP0711F. Pump discharge piping modified for a maintenance friendly application. Sample port added for testing effluent. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 07/01/2022 | 10:30 AM
07/06/2020 |  | RoutineScheduled | 179-06-0156-SWP | Stafford | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Distribution Pump Operation" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Recirculation Pump" ,"Distribution Pump Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/09/2021 | 03:25 PM
08/26/2020 |  | RoutineScheduled |  | Rockingham | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Pad | Chlorination |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Repaired compressor air supply line at time of service No Lab available | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/26/2021 | 09:04 AM
09/12/2020 |  | Routine/Scheduled |  | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  |  |  | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  |  | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 09/12/2020 | Jan 1 1900 11:00AM
06/19/2020 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 3.000000 |  | Septic Tank | Pump Tank for Puraflo | Pump | Gravity | Trenches | Not Applicable |  | ["Level Sensor Operation","Attached Growth Medium"] | ["Level Sensor Operation","Attached Growth Medium"] | NO | [17 empty] | Septic tank-8"sludge/ Pump tank to Puraflo-2"sludge/ Discharge pump tank-2"sludge/ System does not need a pump out/ Replaced faulty off float in discharge pump tank/ Puraflo peat fluffed/ Puraflo Counts: cc1-54511 ETM-4142.29/ cc2-34525 ETM-4496.75/ Discharge pump counts: cc1-6307 ETM-183.90/cc2-6294 ETM-1207.39/ No breakout or spongy areas on the drainfield. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  |  | 12:00 AM
07/28/2020 |  | Routine/Scheduled | Legacy | James City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Peninsula | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | Puraflo | None | Pump | None | Aggregate Bed | None | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | Musty | Clear | [15 empty] | Routine service conducted. Primary Septic Tank - no access riser present - excavated and serviced effluent screen. Pump Tank - normal operating level - pump, float sensors and controls operating properly. PuraFlo Modules - FOUR - Peatmoss biofilter racked out and reported to be in good condition. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 07/29/2020 | Jan 1 1900 8:00AM
05/19/2020 |  | Follow-Up | 175-10-0317 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green | [9 empty] | ["None"] | ["None"] | [18 empty] | Replaced audible alarm & warning bulb. | This AOSS should now return to normal function after having provided the above state routine maintenance |  | 05/19/2020 | 04:00 PM
04/27/2020 | Alternative | Routine/Scheduled | 157-07-0302 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1250 | Clearstream ATU | None | Pump | Distribution Box | Aggregate Trench | None |  |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | Septic Tank Riser had root/dirt infiltration; Diffuser in Aeration Tank was clogged; the Plumbing and Floats in the Discharge Tank have exceeded their expected life, there was dirt entering where the cords entered the Riser, and the Riser had dirt/ground water leaking into the Tank; Air Pump has exceeded its life expectancy; | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/28/2020 | 02:03 PM
02/13/2020 |  | Routine, Scheduled | 099-14-0031-SR | King George County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001350 | Mike | Cook | 1.000000 |  | Ecoflo | None | Pump | Distribution Box | Aggregate Bed |  |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/25/2020 | 07:16 AM
11/11/2020 |  | Routine, Scheduled | 175-15-0461 | Prince William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Clearstream ATU |  |  |  |  | UV Light |  | ["Blower/Compressor/Aerator Operation","Disinfection"] | ["Blower/Compressor/Aerator Operation"] |  | Acceptable | Clear | [15 empty] | UV unit is bad. Spin filter cleaned. Pump Amps 10.40 ETM 693 hrs Cycles 6681 Water Meter Reading 312110 Septic Sludge 6" Scum 0 ATU Sludge 4" Scum 0 Pump Sludge 2" Scum 0 | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 11/11/2020 | 11:48 AM
10/03/2020 |  | RoutineScheduled | 175-10-0385 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Wastemaster Inc |  | Timothy | Jenkins | 2.000000 |  | ATU | Recirculating Sandfilter | Pump | Gravity | Discharge | UV |  | [] | [] |  | Musty | Clear | 7.700000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 09:15 AM
02/11/2020 |  | Routine, Scheduled |  | Loudoun County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | None | Pump | Distribution Box | Aggregate Trench | [23 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/02/2020 | 04:43 AM
12/24/2020 |  | RoutineScheduled | 154-05-1034 | Louisa | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Blue Ridge | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Pad | Not Applicable |  | ["Recirculation Pump" ,"Attached Growth Medium"] | ["Attached Growth Medium" ,"Recirculation Pump"] | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/09/2021 | 03:25 PM
01/10/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Biomicrobics MicroFAST |  |  |  |  | None |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] |  | Good | Good | [15 empty] | [Comments]: Pump Amps 9.88 ETM 173h 53m Cycles 7411Septic Sludge 7" Scum 10"ATU Sludge 8" Scum 0Pump Sludge 1" Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/10/2020 | Jan 1 1900 11:45AM
08/17/2020 |  | RoutineScheduled |  | Shenandoah | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | NA | [7 empty] | 08/17/2020 |  | 120.000000 | [5 empty] | Will be sent separately | Inspected | Repaired air vac and valve box System was off once arrived and was corrected | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance |  | 04/26/2021 | 09:04 AM
11/02/2020 |  | Reportable Incident | 175-07-0357 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green | [9 empty] | ["Blower/Compressor/Aerator Operation"] | ["Blower/Compressor/Aerator Operation"] | [18 empty] | Installed new compressor Mac80R. | This AOSS should now return to normal function after having provided the above state routine maintenance |  | 11/02/2020 | 04:00 PM
10/13/2020 | Alternative | Routine/Scheduled | 166-09-171 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 1.000000 | 1500 | Clearstream ATU |  | Pump | Distribution Box | Aggregate Bed |  |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 10/13/2020 | 02:30 PM
08/04/2020 |  | RoutineScheduled | 109-05-0252 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1000 | Whitewater |  | Pump | Pressure | Drip | Not Applicable |  | [] | [] | NA | [16 empty] | Inspected | Yearly inspection, found pump breaker tripped, pump Drew 35-48 amps on start and this caused breaker to trip, Replaced Effluent Pump with new Orenco Pump, now draws 11.75 amps on start, Returned for follow inspection due to sale of the property on 7/23/20 and on 8/4/2020 Replaced solenoid control valve, System is fully functional. Septic Tank minimum scum, 12" sludge, Treatment unit, good aeration, cleaned air filter, 2-3" scum and 6" sludge, pump tank 12" fine sludge. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 08/05/2020 | 09:30 AM
07/27/2020 |  | Routine, Scheduled | 175-17-0380 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Biomicrobics MicroFAST |  | Pump |  |  | UV Light |  | ["Blower/Compressor/Aerator Operation"] | ["Blower/Compressor/Aerator Operation"] |  | Good | Clear | [5 empty] | 07/27/2020 | Pump tank | 27.000000 |  | 1600.000000 | [5 empty] | Pump Amps 10.03 ETM 45 hrs 11 mins Cycles 338 Septic Sludge 10" Scum 10" ATU Sludge 8" Scum 0 Pump Sludge 2" Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 07/27/2020 | 12:40 PM
11/09/2020 |  | RoutineScheduled | SD-06-316 | Culpeper | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001060 | Rob | Martin | 2.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Effluent Screens"] | ["Effluent Screens" ,"Attached Growth Medium"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 |  | 04/09/2021 | 03:25 PM
10/02/2020 |  | RoutineScheduled | S-04-111-0118 | Botetourt | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1000 | EcoFlo |  | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | NA | [16 empty] | Inspected | Sludge levels-- No Scum- 2" sludge in Septic tank. Peat in good condition for age, Turn peat in all 4 quadrants, minior ponding in one which drained after breaking up the peat No roots observed. Pump Tank 2" sludge- Replaced one Float in the pump tank due to age. Both Pump and alarm are operational. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 10/30/2020 | Jan 1 1900 12:30PM
06/05/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 3.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/27/2021 | 01:26 PM
07/16/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | SES MidAtlantic LLC | 1942001203 | James | Green | 1.000000 |  | EcoPod | none | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/15/2021 | 09:00 AM
08/22/2020 |  | RoutineScheduled |  | Culpeper | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 | Pending Review | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001068 | David | Stewart | 2.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"BlowerCompressorAerator Operation" ,"Attached Growth Medium" ,"Level Sensor Operation" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | ["Level Sensor Operation" ,"Control Operation" ,"BlowerCompressorAerator Operation" ,"Attached Growth Medium" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | NA | [15 empty] | Will be sent separately | Inspected | Onsite for alarm and maintenance. Everything working fine. System was in high level, pumped it all the way down. Heavy flow from septic tank. Most likely hung toilet is culprit. Noticed lots of wipes in septic. Wipes need to not be flushed. Please check for a hung toilet. Media is clogged, we are scheduled to clean clogged media soon. | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
12/10/2020 |  | Routine, Scheduled | 175-19-0134 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Biomicrobics MicroFAST |  |  |  |  | None |  | ["Blower/Compressor/Aerator Operation"] | ["Blower/Compressor/Aerator Operation"] |  | Acceptable | Clear | [15 empty] | Spin filter cleaned. Pump Amps 11.41 ETM 256 hrs 05 mins Cycles 1482 Water Meter Reading 84500 Septic Sludge 13" Scum 1" ATU Sludge 13" Scum 0 Pump Sludge 2" Scum 0 On 11 mins 07 secs Off 3 hrs 49 mins | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 12/10/2020 | 10:38 AM
04/14/2020 |  | Routine, Scheduled |  | Albemarle County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Blue Ridge | CLARK, MICHAEL J | 1934000023 | MICHAEL | CLARK |  |  | Septic Tank Only | Septic Tank Only | None | None | None | None |  |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/19/2020 | 04:13 AM
02/27/2020 |  | Routine, Scheduled |  | Loudoun County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Loudoun | Triple R Construction Co., Inc. | 1934000238 | Charles | Seamon | 1.000000 |  | Biomicrobics MicroFAST | None | Pump | Distribution Box | Aggregate Trench |  |  | ["SludgeScum Accumulation"] | ["SludgeScum Accumulation"] | [18 empty] | [Comments]: Recommend pump out of the Septic/Microfast Tank in 3 months.Blower panel front door was faulty and we returned to replace and now functioning as designed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/26/2020 | 04:49 AM
07/01/2020 |  | Follow-Up |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Gravity | Gravity |  | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Loudoun County Health dept issued a repair permit to replace inlet T, add a riser on the outlet of the septic tank and replace entire conveyance line . There was a filter added to septic tank. the health dept came out 7/1/20 and inspected and passed the work that was done. At this time the septic system is in working condition. | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 |  | 04/14/2021 | 04:27 PM
11/17/2020 |  | RoutineScheduled | 98-197-A3 | Wise | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | Wise Health Dept |  | Rodney | Neece | 1.000000 |  | AtU Jet |  | Gravity | Gravity | Discharge | Chlorination |  |  |  |  | Septic | Cloudy | 6.200000 | 0.000000 |  | 0.000000 | Aerator not working, no tablets | [11 empty] | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 11/17/2020 | 12:00 AM
09/17/2020 |  | RoutineScheduled | 069051002 | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Greenway Engineering | 1942001008 | Jeremy | Ferguson | 1.000000 | 1500 | Microfast | none | Pump | Pressure | Drip | Not Applicable |  | ["Level Sensor Operation","SludgeScum Accumulation"] | ["Level Sensor Operation","SludgeScum Accumulation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 09/18/2020 | 10:30 AM
06/30/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/27/2021 | 01:26 PM
08/01/2020 |  | RoutineScheduled | 139-06-0680 | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | dovel enterprises | 1934000191 | jerry | dovel | 1.000000 |  | 1000 |  | Pump |  | Trenches |  |  | [] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
07/01/2020 |  | Follow-Up | SWP-04-722 | Spotsylvania | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Added riser to septic inlet. Resealed concrete riser joints on 2 tanks closest to the house. Resealed 1st pump tank inlet wedge lid. Replaced smart filter alarm box and sensor. Inspected concrete distribution box and resealed crack. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
06/10/2020 |  | RoutineScheduled | 177-06-0513-SP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump" ,"Dispersal System Operation" ,"Auxiliary Filter"] | ["Effluent Screens" ,"Recirculation Pump" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Auxiliary Filter"] | YES | [15 empty] | Will be sent separately | Inspected | Repaired discharge pump line which was leaking inside the riser. | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 |  | 04/09/2021 | 03:25 PM
11/02/2020 |  | Routine/Scheduled |  | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Gravity | Distribution Box |  | None |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | Replaced aerator | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 11/02/2020 | Jan 1 1900 1:30PM
02/19/2020 |  | Routine, Scheduled | 228-07-0329 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Virginia Beach | [8 empty] | Pump |  |  | None |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] |  |  |  | 7.550000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/19/2020 | Jan 1 1900 11:30AM
11/03/2020 |  | RoutineScheduled | 175-14-0303 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Wastemaster Inc |  | Timothy | Jenkins | 2.000000 |  | Recirculating Sand filter |  | Pump | Gravity | Discharge | UV |  | [] | [] |  | Musty | Clear | 6.500000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 11/20/2020 | 12:15 PM
03/03/2020 |  | Routine, Scheduled | 03-165-0208 | Northampton County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Eastern Shore | DUER, PETE C | 1942001051 | PETE | DUER | 1.000000 | 1250 | Septic Tank Only | Puraflo | Pump | None | None | None |  | ["None"] | ["None"] | [18 empty] | [Comments]: Aoss Inspection. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/27/2020 | 12:11 PM
02/04/2020 |  | Routine, Scheduled |  | Prince William County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Prince William | SEAMON, CHARLIE L | 1942001108 | CHARLIE | SEAMON |  |  | Septic Tank Only | Puraflo | Pump | Manifold | Aggregate Bed | None |  | ["Attached Growth Medium"] | ["Attached Growth Medium"] | [18 empty] | [Comments]: Performance Inspection: Puraflo Pad System Septic Tank-8"sludge 0"scum/ Pump Tank-1"sludge. No pump out needed at this time. Pump1 cnts-5877 ETM-58h 24m/ Pump2 cnts-5855 ETM-58h 10m/ Peak-14/ High-15. Pumps Zoeller E-185 (230V) @ 63.7gpm Effluent filter does not need cleaning at this time. Media fluffed. Pad area good at this time. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/10/2020 | 06:32 AM
11/02/2020 |  | RoutineScheduled | SWP-02-634 | Stafford | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Puraflo | Puraflo | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Effluent Screens"] | ["Attached Growth Medium" ,"Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected | We recommend treating the area around the Puraflo modules for ants. | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 |  | 04/09/2021 | 03:25 PM
11/27/2020 |  | Follow-Up |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Orenco Advantex | Orenco Advantex | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Sheets were removed, the unit was cleaned and new sheets were installed. System appears to be functioning as designed. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/27/2021 | 01:26 PM
07/28/2020 |  | RoutineScheduled | 099-15-0088 SWP | King George | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 |  | 04/09/2021 | 03:25 PM
02/20/2020 | Alternative | RoutineScheduled | 115-02-0128 | Campbell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | COLLINS, MELVIN J | 1942001044 | MELVIN | COLLINS | 1.000000 | 1500 | Septic Tank |  | Pump | Pressure | Trenches | Not Applicable | 450.000000 | ["None"] | ["None"] | [18 empty] | [Comments]: septic tank ok, pump ok, LPD has small growth with 1/2" pines | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 02/21/2020 | 07:35 AM
04/14/2020 |  | Routine, Scheduled |  | Albemarle County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Blue Ridge | CLARK, MICHAEL J | 1934000023 | MICHAEL | CLARK |  |  | Septic Tank Only | Septic Tank Only | None | None | None | None |  |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/19/2020 | 04:15 AM
11/24/2020 |  | RoutineScheduled |  | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Central Shenandoah | Onsite Wastewater Services - May Supply | 1942001627 | Drew | Shull | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Attached Growth Medium"] | ["Auxiliary Filter" ,"Attached Growth Medium"] | NO | None | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/01/2022 | 12:13 PM
06/09/2020 |  | Routine/Scheduled |  | Chesapeake | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  |  | Drip | Elevated Sand Mound |  |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  |  | 7.000000 | 5.000000 | [13 empty] | UV is not working. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 06/09/2020 | Jan 1 1900 2:00PM
12/21/2020 |  | RoutineScheduled |  | Augusta | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NO | [15 empty] | Will be sent separately | Inspected | Repaired vent on lid | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/26/2021 | 09:04 AM
07/29/2020 |  | Routine/Scheduled | 07-142-0182 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Old Dominion Onsite, Inc. | 1942001503 | Jason | Hackler | [9 empty] | ["Blower/Compressor/Aerator Operation","Dispersal System Operation"] | ["Blower/Compressor/Aerator Operation","Dispersal System Operation"] | N/A | [17 empty] | Cleaned air filter, checked splash box and distribution box for roots. Lots of roots found, need to move water catcher so we can access both boxes for removal. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 07/29/2020 | Jan 1 1900 1:25PM
05/15/2020 |  | RoutineScheduled | SD-10-315 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Soils, Inc. | 1940001392 | Markham | Smith | 2.000000 | 1500 | Puroflo |  | Pump | Gravity | Pad | Not Applicable | 62.500000 | [] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | NA | [17 empty] | Septic Tank 1 scum 12 sludge Pump Chamber 0 scum 4 sludge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 07/13/2020 | 12:00 AM
10/09/2020 |  | Follow-Up | 03-197-A9 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco |  |  |  |  | 1.000000 |  | ATU |  | Gravity | Gravity | Drip | Chlorination |  |  |  |  | None | Clear | 6.000000 | 5.000000 |  |  | Chlorine Effluent (0) | [11 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 10/09/2020 | Jan 1 1900 4:15PM
02/13/2020 |  | Routine, Scheduled | 181-01-0042 (LEGACY ALT. SYSTEM) | Rockbridge County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Central Shenandoah |  |  |  |  | 1.000000 | 1000 |  | None | Pump | Manifold | Aggregate Trench | None |  | ["None"] | ["None"] | [18 empty] | [Comments]: Filter checked and cleaned. Control panel functioning properly. System did not need to be pumped. No apparent leaks in system or drain field area. Lid properly secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/23/2020 | 30-12-1899 12:13 AM
08/21/2020 |  | Reportable Incident |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | SES MidAtlantic LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation"] | ["Distribution Pump Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced Z140 effluent pump. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/15/2021 | 09:00 AM
06/15/2020 |  | RoutineScheduled | 15-100-0366 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Bundick Well & Pump | 1942001051 | Peter | Duer | 1.000000 | 1000 | Septic Tank | Clearstream ATU | Pump | Pressure | Pad | UV | 450.000000 | ["None"] | ["None"] | YES | [16 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 07/15/2020 | 02:10 PM
06/26/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/27/2021 | 01:26 PM
07/13/2020 |  | Routine/Scheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | POWELLS PLUMBING, INC. | 1942001036 | Kurt | Holthaus | 1.000000 | 1000 | Sandfilter, Recirculating |  | Pump | Distribution Box | Aggregate Trench |  | 450.000000 | ["None"] | ["None"] | N/A | [17 empty] | Annual Inspection - No repairs or service needed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 07/17/2020 | 01:30 PM
07/23/2020 |  | RoutineScheduled | 107-09-0059 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Onsite Wastewater Services - May Supply | 1942001022 | Sara | Tusing | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Pressure | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | INSPECTION BY DS | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 05/28/2021 | 05:41 AM
08/25/2020 |  | Reportable Incident | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance | Approved | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green | [9 empty] | ["Distribution Pump Operation"] | ["Distribution Pump Operation"] | [18 empty] | Installed E294/230v effluent pump. (3) Control floats. | This AOSS should now return to normal function after having provided the above state routine maintenance |  | 08/25/2020 | Jan 1 1900 2:00PM
03/18/2020 |  | RoutineScheduled | {FIPSCode}-STS-26941 | Frederick | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Lord Fairfax | Onsite Wastewater Services - May Supply | 1942001022 | Sara | Tusing | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/28/2021 | 05:41 AM
08/20/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Breaker for control panel supply repeatedly tripped and the panel was not functioning. The system could not be fully inspected due to the panel not functioning. Levels high in both tanks. Blower not functioning. | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 |  | 05/27/2021 | 01:26 PM
12/21/2020 |  | Routine/Scheduled |  | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump | Distribution Box |  | UV Light |  | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | Replaced UV Bulb | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 12/21/2020 | Jan 1 1900 12:30PM
01/22/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Paid | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Biomicrobics MicroFAST |  |  |  |  | UV Light |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] |  | Good | Brown | [7 empty] | 208.000000 |  | 16000.000000 | [5 empty] | [Comments]: System was in alarm.Pump Amps 8.33Water Meter Reading 468700Septic Sludge 10" Scum 0ATU Sludge 12" Scum 0Pump Sludge 6" Scum 0 | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 01/22/2020 | Jan 1 1900 3:00PM
06/23/2020 |  | RoutineScheduled | 179-17-0475-SWP | Stafford | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Norweco Singulair ATU | none | Gravity | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Dispersal System Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Effluent Screens" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | YES | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/09/2021 | 03:25 PM
05/15/2020 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Aquarobic Services | 1934000142 | Michael | Blake |  |  | none | none | Pump | Gravity | Mound | Not Applicable |  | ["Auxiliary Filter" ,"Level Sensor Operation"] | ["Auxiliary Filter" ,"Level Sensor Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Routine inspection. Air pre-filter cleaned. Removed debris that was clinging to timer float switch. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 07/01/2022 | 10:30 AM
03/28/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Orenco Advantex |  |  |  |  | None |  | ["Effluent Screens"] | ["Effluent Screens"] |  | Good | Good | [15 empty] | [Comments]: Pump Amps 11.80 5.79/5.84Septic Sludge 7" Scum 6"ATU Sludge 6" Scum 0Pump Sludge 1" Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/28/2020 | Jan 1 1900 1:59PM
12/26/2020 |  | RoutineScheduled | 196-05-787 | Westmoreland | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Assure Plumbing & Septic | 1942001502 | Wayne | Fishel | 2.000000 | 1000 | 1000 |  | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Attached Growth Medium","Effluent Screens"] | YES | None | Clear | [15 empty] | Raked and added peat. Parged inside seam of effluent tank. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12/26/2020 | 05:00 AM
06/09/2020 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Eco Virginia | 1942001235 | William | Poindexter |  |  | none | none | Pump | Gravity | Mound | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 |  | 06/03/2021 | 05:53 AM
09/23/2020 |  | RoutineScheduled | 154-07-0108 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark |  |  |  |  | Gravity | Gravity | Trenches |  |  | [] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 04:35 AM
05/15/2020 |  | Routine/Scheduled | 03-142-0262 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chickahominy | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. |  |  | Orenco Advantex |  | Pump | Drip |  |  |  | ["Attached Growth Medium","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump","Sludge/Scum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump","Sludge/Scum Accumulation"] | N/A | [17 empty] | Need to replace motor contractor on next visit | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 05/15/2020 | Jan 1 1900 11:00AM
01/25/2020 |  | Routine, Scheduled |  | Northumberland County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Three Rivers | BEASLEY, THOMAS W | 1934000450 | THOMAS | BEASLEY | 3.000000 | 2600 | Clearstream | Septic Tank Only | None | None | None | None |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [5 empty] | 50.000000 | [12 empty] | [Comments]: Replaced blower motor, pumped clearstream tank | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/25/2020 | 03:00 PM
09/24/2020 |  | Reportable Incident | SWT-03-344 | Stafford | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Repaired broken clean-out just prior to d-box (broken by lawn service). Recommend replace both concrete lids. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
01/28/2020 |  | Follow-Up |  | Loudoun County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | None | None | Gravity | [24 empty] | [Comments]: The header line that was crushed was dug up and repaired. At this time the septic system is in working condition. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/02/2020 | 04:43 AM
04/14/2020 |  | Reportable Incident |  | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump | Drip | Elevated Sand Mound | UV Light |  | ["Blower/Compressor/Aerator Operation","Control Operation"] | ["Blower/Compressor/Aerator Operation","Control Operation"] | N/A | [17 empty] | Replaced aerator | This AOSS should now return to normal function after having provided the above state routine maintenance |  | 04/14/2020 | Jan 1 1900 12:05PM
10/14/2020 | Alternative | Routine/Scheduled | 151-12-0010 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 2.000000 | 2000 | Ecoflo |  | Pump | Manifold | Aggregate Bed |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 10/14/2020 | 05:00 PM
11/03/2020 |  | RoutineScheduled | 179-14-0069-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Recirculation Pump" ,"Attached Growth Medium"] | ["Effluent Screens" ,"Recirculation Pump" ,"Attached Growth Medium"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 |  | 04/09/2021 | 03:25 PM
07/31/2020 |  | Routine/Scheduled | 16-120-0502AR | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. |  |  | Norweco Singulair ATU |  | Pump | Distribution Box |  |  |  | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 07/31/2020 | Jan 1 1900 12:00PM
10/08/2020 |  | RoutineScheduled | 2059-99-153 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Prince William | Wastemaster Inc |  | Timothy | Jenkins | 2.000000 |  | ATU | Sequencing Bat Reactor |  | Gravity | Discharge |  |  | ["SludgeScum Accumulation"] | [] | [18 empty] | Found Sand Filter pump tripping overload. Impeller shaft broken. Must be replaced. Installed new pump and checked operation. All operating normally. All tank levels normal. Recommend pumping system. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 10/15/2020 | 12:10 PM
06/03/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Sale inspection on a advantex septic system. The mother board on the septic control panel is not working and will need replace. There is 2 pvc cleanouts near the house. The pvc sewer line was camera snaked and was clear. The septic tank was inspected The advantex pod needs to be cleaned out from debris. Also the hydraulic arms will need to be replaced. The pumps and floats were not able to be tested due to the mother board not work. The 9 port plastic d-box is in good condition the lid is broken and will need to be replaced. the header lines were camera snaked and are clear. The drain field was probed and was dry. At time of inspection septic system was not in working condition. | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 |  | 04/14/2021 | 04:27 PM
05/18/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/14/2021 | 04:27 PM
12/07/2020 |  | Follow-Up | SWP-05-130 | Stafford | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Added septic tank inlet riser to make watertight and provide future access. Sealed pump tank wedge lid and outlet pipe. Replaced concrete lid on septic tank. Septic and pump tank pumped out by others. Resealed inside joint on septic tank and pump tank concrete risers (saw a few small roots). | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
07/31/2020 |  | RoutineScheduled | 033-17-0119-SP | Caroline | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Pad | Not Applicable |  | ["Attached Growth Medium" ,"Effluent Screens" ,"Recirculation Pump"] | ["Effluent Screens" ,"Recirculation Pump" ,"Attached Growth Medium"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 |  | 04/09/2021 | 03:25 PM
11/03/2020 | Alternative | RoutineScheduled | 166-14-029 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Church View Septic Service Inc. | 1942001302 | Charles | Langford | 1.000000 | 1500 | Microfast |  | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation"] | [] | YES | [17 empty] | Light for blower works audio does not work. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 11/18/2020 | 12:00 AM
12/30/2020 |  | RoutineScheduled | 175-17-0346 | Prince William | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Recirculation Pump" ,"Attached Growth Medium"] | ["Attached Growth Medium" ,"Effluent Screens" ,"Recirculation Pump"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 |  | 04/09/2021 | 03:25 PM
04/16/2020 |  | Follow-Up |  | Prince William County | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Paid | EHD - Prince William | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Puraflo | None | Pump | Distribution Box | [15 empty] | 519223.000000 |  |  | 11028.000000 |  |  |  |  | [Comments]: Influent sample results came back very high: BOD 519 mg/L, TSS 110 mg/L. As these samples were collected in the the pump tank, it can be assumed that the wastewater strength would have been even higher had it been collected at the inlet end of the septic tank. Effluent results: BOD 223 mg/L, TSS 28 mg/L. May need to add an additional septic tank or additional treatment if owners cannot adjust their lifestyle to lower waste strength. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 04/27/2020 | 04:14 AM
05/12/2020 |  | RoutineScheduled | 109-04-0683 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 300 | Microfast |  | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | NA | [16 empty] | Inspected | Septic zone 6-8" Scum & Full of Sludge. Fast unit 1" scum 18" sludge, a bit clear on top, Alarm working on blower, cleaned blower filter, Reccomended to pump, Foutz came to pump system next day. added 1 Rootx treatment. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 05/13/2020 | 09:30 AM
03/10/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Fairfax | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Orenco Advantex | None | Pump | Distribution Box | Aggregate Trench | [23 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/16/2020 | Jan 1 1900 11:28AM
08/11/2020 |  | Reportable Incident | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance | Approved | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green | [9 empty] | ["Disinfection"] | ["Disinfection"] | [18 empty] | Installed new JET UV Bulb. | This AOSS should now return to normal function after having provided the above state routine maintenance |  | 08/11/2020 | Jan 1 1900 8:30AM
03/09/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS should now return to normal function after having provided the above stated routine maintenance. | Paid | EHD - Fairfax | SEAMON, CHARLIE L | 1942001108 | CHARLIE | SEAMON |  |  | Septic Tank Only | Puraflo | Pump | Manifold | Aggregate Bed | None |  | ["Attached Growth Medium"] | ["Attached Growth Medium"] | [10 empty] | 204.000000 | [5 empty] | Attached to this report |  | [Comments]: Performance Inspection and BOD Sample:Puraflo Pad System. Septic tank-10"sludge 0"scum/Pump tank-3"sludge needs pump out,close to the pump intake. Puraflo media fluffed during inspection and is in good condition.No breakout or spongy areas on the pad site.Counts:P1-12031 ETM-57.44/P2-11952 ETM-105.61 | This AOSS should now return to normal function after having provided the above stated routine maintenance. |  | 04/07/2020 | Jan 1 1900 3:36PM
08/05/2020 |  |  | {FIPSCode}-STS-9546 | Dickenson | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 08/05/2020 |  | 19.500000 | [5 empty] | Attached to this report |  | TSS: BDL | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 08/05/2020 | 12:00 AM
10/02/2020 | Alternative | RoutineScheduled | 115-10-0091 | Campbell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Taylor's Septic Service, Inc | 1942001028 | Penny | Taylor | 4.000000 | 8000 | septic | Advantex | Pump | Gravity | Trenches | Not Applicable | 3600.000000 | ["SludgeScum Accumulation","Effluent Screens"] | ["Attached Growth Medium","Control Operation","Effluent Screens","SludgeScum Accumulation","Level Sensor Operation"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 10/02/2020 | 02:30 PM
12/03/2020 | Alternative | RoutineScheduled | 124-STS-2379 | Charles City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Chickahominy | Wastemaster Inc |  | Timothy | Jenkins |  |  | ATU |  |  |  | Discharge | Chlorination |  | [] | [] |  | Musty | Clear | 7.600000 |  | 30.000000 | 2.200000 | [12 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12/09/2020 | Dec 30 1899 3:30PM
05/15/2020 |  | Routine, Scheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Puraflo |  |  |  |  | None |  | ["Effluent Screens"] | ["Effluent Screens"] | [18 empty] | Pump 1 Amps 11.04 ETM 246.67 Cycles 13519 Pump 2 Amps 11.16 ETM 251.80 Cycles 13513 Septic Sludge 4" Scum 2" Pump Sludge 1" Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 05/15/2020 | Jan 1 1900 11:31AM
03/24/2020 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump | Distribution Box | Aggregate Bed |  |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  | 1.83 | 7.820000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/24/2020 | Jan 1 1900 1:00PM
04/28/2020 | Alternative | Initial Visit | 157-17-0017 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [9 empty] | 3.000000 |  | 1.000000 | [5 empty] | Serviced system. Checked the pump, panel, & floats (ok). Cleaned the filter in the Clearstream, cleaned the filter in the aerator, and cleaned the UV light bulb. Changed the diffuser in the Clearstream. The timer is set to 4 minutes every 2 hours. Took initial BOD & Fecal samples. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 04/28/2020 | 12:00 PM
08/05/2020 |  | RoutineScheduled | 196-10-015 | Westmoreland | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers |  |  | joel | pinnix | [9 empty] | [] | [] | [18 empty] | Rewired control panel to run off timer as designed. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  |  | 12:00 AM
03/16/2020 |  | Routine, Scheduled | SD-03-151 | Madison County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Biomicrobics MicroFAST | None | Pump | Drip | Drip Tubing | [23 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/06/2020 | 02:45 PM
03/17/2020 |  | Routine, Scheduled | 179-10-0023-SP | Stafford County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | None | None | Pump | Distribution Box | Aggregate Trench |  |  | ["Attached Growth Medium","Effluent Screens","None","SludgeScum Accumulation"] | ["Attached Growth Medium","Effluent Screens","None"] | [18 empty] | [Comments]: We ecommend pumping the Septic Tank due to scum & sludge accumulation! | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/06/2020 | 02:45 PM
10/28/2020 |  | RoutineScheduled |  | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Joe Blevins Equipment Rental, Inc | 2705013926 | Joel | Blevins | 2.000000 | 1250 | EZ Treat 600 |  | Gravity | Gravity | Trenches | Not Applicable |  | ["None"] | ["None"] |  | None | Clear |  |  |  |  | none | 10/28/2020 | Pump Chamber | 51.000000 | [7 empty] | Manufacturer is going out to make adjustments to the system. We cleaned the sprayers and Zabel A-300 filter. The ditches are dry. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 10/28/2020 | Jan 1 1900 8:55AM
06/23/2020 |  | RoutineScheduled | 13-120-0449AR | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Stamie E. Lyttle Co. | 1942001470 | Eric | Tambourine | [9 empty] | [] | [] | [19 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 06/23/2020 | 12:00 AM
03/10/2020 |  | Routine, Scheduled | 95-192-211 | Tazewell County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Cumberland Plateau | DEEL, DENNY M | 1942001097 | DENNY | DEEL |  |  | Jet ATU | None | Gravity | None | Alternative Discharge | Chlorine | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection"] |  | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/16/2020 | Jan 1 1900 12:55PM
12/18/2020 |  | Routine/Scheduled | 2009-143-0063 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Henrico | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1500 | Hoot |  | Pump | Distribution Box | Aggregate Trench | None | 600.000000 |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | Musty | Clear | [15 empty] | Routine Service Trash Tank - normal level Aeration Tank - normal level - compressor serviced Pump Tank - normal level - pump, sensor probe & controls operating. Distribution box - concrete - intact - all laterals accepting effluent. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 12/21/2020 | 07:30 AM
08/14/2020 |  | Initial Visit | 06-1370324 | Goochland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chickahominy | Miller's Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1500 | Orenco Advantex | None | Pump | Distribution Box | Aggregate Trench | None | 600.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | None | Clear | [15 empty] | Initial visit - Unknown previous service provider Processing tank at normal operating level - RSV, Effluent Screen & recirc. pump serviced. AdvanTex Module - media drapes and spray grid serviced. Discharge Tank - at normal operating level - pump, float sensors and controls operating properly. Distirbuion Box - normal operating level - minor root infiltration removed, all laterals accepting effluent. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 07/17/2020 | Jan 1 1900 7:15AM
05/30/2020 |  | RoutineScheduled | -STS-20150 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | WasteMaster |  | Timothy | Jenkins | 2.000000 |  | ATU | Spray Irr | Pump | Gravity | Discharge | Chlorination |  | [] | [] |  | Musty | Clear | 7.500000 | 6.900000 |  | 1.400000 |  | 05/30/2020 |  | 1.500000 |  |  | 3.600000 |  |  | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 10:55 AM
08/06/2020 | Alternative | Routine/Scheduled | 073-STS-104677 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 4.000000 | 4600 |  |  | Pump | Manifold | Aggregate Bed |  |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump","Septic Tank Baffles","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 08/05/2020 | 05:00 PM
01/20/2020 |  | Reportable Incident | 109-18-0505 | Bedford | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Advantex AX25RT |  | Pump | Gravity | Trenches | Not Applicable |  | ["Level Sensor Operation"] | ["Level Sensor Operation"] | NA | [16 empty] | Inspected | Called for septic alarm after renters checked out. At first an apperant high water flow due to high high water useage but after investigation into computer record of water use and alarms, we found the system indicating a bad clog. We called Orenco to determine possible causes and one idea they indicated it could be from a loose media sheet blocking the splitter valve. We returne tthe next day to pump high water to see the splitter valve and imdetdly got stuck with a an extra media locted inside the treatment tank which apparently stoped the operation of an important valve (splitter valve) from operating when called on and this eventually caused the vocal alarm. No media was missing from the main area of treatment but there was one empty slot remaining at the very end of the tank, past treatment zone and in a location obstructed by pump and controls. At time of our intial inspection the system was full of water and if such media was inside the tank we were unable to observe it at the time and nothing indicated a problem until about two week ago. The intial alert began about two weeks ago when the system went from normal operation into vaction mode due to lack of water. It took another two weeks at which time water was spilling over the baffle wall and to the computer appearing as a bad filter clog. It is unlikley the installer would have noticed this extra media sheet at the time of installation especially as this AX25 unit is full of media from end to almost the other end of the tank. Typically these sheets are all factory installed would not require removal of sheets during the install unless the installer accidently shifted the media during install. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 01/21/2020 | 05:30 PM
06/05/2020 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Eco Virginia | 1942001235 | William | Poindexter | 1.000000 |  | Orenco Advantex | Orenco Advantex | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Effluent Screens"] | ["Effluent Screens" ,"Attached Growth Medium"] | YES | [15 empty] | Will be sent separately | Inspected | Replaced lid | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 |  | 06/03/2021 | 05:53 AM
06/09/2020 |  | RoutineScheduled |  | Shenandoah | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation" ,"Dispersal System Operation" ,"SludgeScum Accumulation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation" ,"Dispersal System Operation" ,"SludgeScum Accumulation"] | NA | [7 empty] | 06/09/2020 |  | 74.000000 | [5 empty] | Will be sent separately | Inspected | Repaired leak in drainfield Will be pumping of all tanks and installing a riser on tank | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance |  | 04/26/2021 | 09:04 AM
01/21/2020 |  | Routine, Scheduled | 14-172-0262A | Powhatan County | This AOSS should now return to normal function after having provided the above stated routine maintenance. | Approved | EHD - Chesterfield | Chapin, Ben |  | Ben | Chapin |  |  | Septic Tank Only | Septic Tank Only | None | None | None | None | [21 empty] | VENIS File Names: 2406 Emanuel Church Rd.jpeg, ATTMGZF9.jpeg | This AOSS should now return to normal function after having provided the above stated routine maintenance. |  | 02/25/2020 | Jan 1 1900 1:15PM
08/11/2020 |  | RoutineScheduled |  | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001301 | Joshua | Hott | [9 empty] | ["None"] | ["None"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
06/26/2020 | Alternative | Initial Visit | 151-12-0012 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | Clearstream |  | Pump | Distribution Box | Aggregate Trench | None | 450.000000 | ["Blower/Compressor/Aerator Operation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | Musty | Clear | [15 empty] | Initial visit - full service / inspection conducted. Septic tank buried with inspection port only. Aeration operating - compressor serviced - diaphragms replaced. Discharge tank in normal operation level Distribution box located - at normal operating level - 3 laterals present. Unknown when / if laboratory samples obtained by previous operator. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 06/29/2020 | 08:00 AM
04/22/2020 |  | RoutineScheduled | 107-10-0114 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Inboden Environmental Services, Inc | 1942001083 | Terry | Inboden | [8 empty] | 4146.000000 | ["None"] | ["None"] |  |  |  | 7.790000 | 6.400000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
06/09/2020 |  | RoutineScheduled | 11-142-0304 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | Microfast | Puraflo | Pump | Gravity | Trenches | Not Applicable |  |  | ["Attached Growth Medium","Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | NA | [17 empty] | The Discharge Pump & Floats have exceeded their life expectancy, and the Floats are not properly secured; the Puraflo Biofilter in all Modules has severely deteriorated and is not longer filtering water properly; | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 06/16/2020 | Jan 1 1900 11:03AM
07/16/2020 |  | Pump-Out Only | LEGACY | James City |  |  | EHD - Peninsula | Parsley Septic |  |  |  | 1.000000 | [32 empty] | 12:00 AM
05/13/2020 |  | RoutineScheduled | SWP-02-365 | Stafford | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Pad | Not Applicable |  | ["Attached Growth Medium" ,"Effluent Screens" ,"Recirculation Pump"] | ["Effluent Screens" ,"Recirculation Pump" ,"Attached Growth Medium"] | YES | [15 empty] | Will be sent separately | Inspected | Installed 4" sanitary tee on inlet pipe in Septic Tank. | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 |  | 04/09/2021 | 03:25 PM
07/30/2020 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  | None |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  |  | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 07/30/2020 | Jan 1 1900 10:45AM
03/11/2020 |  | Routine, Scheduled |  | Prince William County | This AOSS should now return to normal function after having provided the above stated routine maintenance. | Paid | EHD - Prince William | SEAMON, CHARLIE L | 1942001108 | CHARLIE | SEAMON |  |  | Septic Tank Only | EZ Treat Sandfilter | Pump | Manifold | Drip Tubing | None |  | ["Dispersal System Operation"] | ["Dispersal System Operation"] | [10 empty] | 73.000000 | [5 empty] | Attached to this report |  | [Comments]: Performance Inspection And BOD Sample: EZ-Treat to American Drip. Septic tank-6"sludge 0"scum/Pump tank-6"sludge (a lot of regrowth). Recommend pump out of the pump tank.Pump cnts-2656 ETM-422h 54m/ Peak-4(n/a)ETM-0/Zone1 cnts-1331/ Zone2 cnts-1318 Replaced faulty check valve for zone #2. Septic filter does not require cleaning at this time. VENIS File Names: Lady Slippers Lane 6035.pdf | This AOSS should now return to normal function after having provided the above stated routine maintenance. |  | 04/07/2020 | 07:39 AM
09/17/2020 |  |  |  | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | McKim Construction | 1942001330 | Michelle | McKim |  |  |  |  | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 11/13/2020 | Jan 1 1900 10:40AM
02/24/2020 |  | Follow-Up |  | Prince William County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Prince William | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Puraflo | None | Pump | Distribution Box | [23 empty] | [Comments]: Repaired inside alarm. Inspected drain piping for proper fall OK. Cleaned out distribution boxes. Augered peat. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/25/2020 | 07:16 AM
06/23/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Pump tank high water alarm is not functioning White water alarm is not functioning | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/27/2021 | 01:26 PM
10/19/2020 |  | RoutineScheduled |  | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 2705051738 | Joshua | Hott | 1.000000 | 1500 | Septic Tank | Puraflo | Pump | Gravity | Trenches | Not Applicable | 500.000000 | ["Effluent Screens"] | ["Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
10/09/2020 |  | Routine/Scheduled | 136-00-746 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1500 | Hydro-Action ATU |  | Pump | Distribution Box | Aggregate Trench | None | 450.000000 |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | Pungent | Cloudy | [15 empty] | Initial visit Trash Tank - normal operating level Aeration Tank - normal operating level - air compressor not operational - requires replacement - ordered. Pump Tank - normal operating level - pump, float sensors and controls functioning, but aged and deteriorating. Distribution box - minor roots - removed - all laterals accepting effluent. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 10/14/2020 | 07:30 AM
03/04/2020 |  | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | SEAL’S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal | 1.000000 |  | tank only | FAST | Pump | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation","Auxiliary Filter"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 03/04/2020 | 12:00 AM
08/18/2020 |  | Routine/Scheduled | 154-18-0379 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Blue Ridge | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. |  |  | Clearstream ATU |  | Pump |  |  |  |  | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 08/18/2020 | 12:00 PM
08/26/2020 |  | RoutineScheduled | SD-09-320 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Wastemaster Inc |  | Timothy | Jenkins | 3.000000 |  | PuraFlo |  | Pump | Pressure | Drip |  |  | [] | ["Other"] | [18 empty] | Replaced Broken Tank Lid | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 09/15/2020 | 01:40 PM
07/23/2020 |  | RoutineScheduled | 107-99-0389 (LEGACY ALT. SYSTEM) | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Onsite Wastewater Services - May Supply | 1942001022 | Sara | Tusing | 1.000000 |  | none | none | Pump | Gravity |  | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | INSPECTION BY DS | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 05/28/2021 | 05:41 AM
06/15/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Not a defiance Informed home owner that they need to maintain drain field | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/14/2021 | 04:27 PM
06/12/2020 |  | RoutineScheduled | 154-07-0418 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark | [9 empty] | [] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 06/26/2020 | 04:50 AM
12/29/2020 |  |  | VAG408220 | Rockingham |  | Rejected | EHD - Central Shenandoah | [16 empty] | None | Clear | 7.350000 |  |  |  | flow-n, trc-nd;; | [14 empty] | 12:00 AM
03/09/2020 |  | Routine, Scheduled |  | Loudoun County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | None | Pump | Distribution Box | Aggregate Trench | [23 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/16/2020 | 11:28 AM
04/15/2020 |  | Pump-Out Only |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | POWELLS PLUMBING, INC. | 1942001036 | Kurt | Holthaus |  |  | Puraflo | [6 empty] | ["Sludge/Scum Accumulation"] | ["Sludge/Scum Accumulation"] | N/A | [17 empty] | Pumped septic. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 07/10/2020 | 01:45 PM
10/09/2020 |  | RoutineScheduled | 179-17-0366-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump" ,"Auxiliary Filter" ,"Attached Growth Medium"] | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Auxiliary Filter" ,"Attached Growth Medium" ,"Effluent Screens" ,"Recirculation Pump"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 |  | 04/09/2021 | 03:25 PM
05/27/2020 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump | Distribution Box |  | None |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  |  | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 05/27/2020 | Jan 1 1900 12:15PM
05/06/2020 |  | RoutineScheduled | {FIPSCode}-STS-64040 | Spotsylvania | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation" ,"Level Sensor Operation" ,"Control Operation"] | ["Level Sensor Operation" ,"Distribution Pump Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Routine inspection. Effluent level was down to the pump intake due to timer float being stuck on internally. Replaced both float switches. Little to no flow in last pod (furthest from driveway). Removed 57 stone that was wedged up against orifice plate next to union. Pods also appear to be leaning towards 1 corner. Grids can be leveled to compensate. A couple of pods had pockets of standing water that went away with raking. Peat is close to 15 years old, but appears to be in good enough shape to last another year. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
05/05/2020 |  | Reportable Incident |  | Warren | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Lord Fairfax | POWELLS PLUMBING, INC. | 1942001036 | Kurt | Holthaus |  |  | Orenco Advantex | [6 empty] | ["Dispersal System Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Dispersal System Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | Repaired flex line for drip tubing in drainfield. Rewired floats and pumped Advantex. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 08/07/2020 | 01:41 PM
03/31/2020 |  | Routine, Scheduled |  | Loudoun County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | None | None | Pump | Manifold | [23 empty] | [Comments]: Sale inspection on a alternative septic system. The state law requires the septic system be inspected every year between Jan 1 -July 1 and filed with the state and county. The interior septic control panel is demand dose. There was 1 pvc cleanout. The concrete septic tank was pumped out and the filter was cleaned. The pump tank, pump, floats and force main were inspected. The drain field was probed and was dry. At this time all components are in working condition | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/12/2020 | 02:21 PM
09/11/2020 |  | RoutineScheduled | 182-04-0599 | Rockingham | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Central Shenandoah | Onsite Wastewater Services - May Supply | 1942001627 | Drew | Shull | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Pressure | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/28/2021 | 05:41 AM
03/09/2020 |  | Routine, Scheduled | {FIPSCode}-STS-2862 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesapeake | R & K Septic, Inc. |  | John | Butt, Jr |  |  | Clearstream ATU |  | Pump | Distribution Box |  | None |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] |  |  | 6.89 | 7.540000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/09/2020 | Jan 1 1900 10:45AM
07/11/2020 |  | RoutineScheduled | {FIPSCode}-STS-13220 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Wastemaster Inc |  | Timothy | Jenkins | 2.000000 |  | Sequencing Bat Reactor |  | Pump | Gravity | Discharge | UV |  | [] | [] |  | Musty | Clear | 7.200000 |  | 19.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 11:05 AM
05/18/2020 |  | Follow-Up |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | krain fixed and reinspected drainfield when it had not rained for a week . Drain field is dry at this time. Saw no issues. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/14/2021 | 04:27 PM
03/27/2020 |  | RoutineScheduled | 043-14-0142 | Clarke | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Greenway Engineering | 1942001008 | Jeremy | Ferguson | 1.000000 | 1500 | Microfast | none | Pump | Pressure | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Level Sensor Operation","SludgeScum Accumulation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 07/21/2020 | 11:55 AM
04/27/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | SES MidAtlantic LLC | 1942001203 | James | Green | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter" ,"Dispersal System Operation"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. Hydraulic unit leaking. | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 |  | 04/15/2021 | 09:00 AM
08/03/2020 |  | RoutineScheduled | 099-19-0007 SRSA | King George | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Recirculation Pump"] | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/09/2021 | 03:25 PM
05/01/2020 |  | RoutineScheduled |  | Rockingham | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | ["Distribution Pump Operation" ,"Level Sensor Operation" ,"Auxiliary Filter" ,"Control Operation"] | NA | [7 empty] | 05/01/2020 |  | 51.000000 | [5 empty] | Will be sent separately | Inspected | Replaced 2 timers Replaced 2 floats Replaced discharge pump Replaced switches Need to have access to septic tank exposed before next inspection | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance |  | 04/26/2021 | 09:04 AM
12/12/2020 |  | RoutineScheduled | 124-STS-2379 | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Rejected | EHD - Fairfax | Wastemaster Inc |  | Timothy | Jenkins |  |  | ATU |  |  |  | Discharge | Chlorination |  | [] | [] | [18 empty] | No discharge. RAS not functioning | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. |  | 01/14/2021 | Jan 1 1900 9:15AM
07/06/2020 |  | RoutineScheduled | SWP-05-154 | Stafford | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Distribution Pump Operation" ,"Dispersal System Operation" ,"Attached Growth Medium" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"SludgeScum Accumulation"] | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Attached Growth Medium" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | We recommend pumping the septic tank & aerobic treatment unite due to scum & sludge accumulation. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/09/2021 | 03:25 PM
06/15/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 3.000000 |  | Biomicrobics MicroFAST | Whitewater ATU | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Recommend pumping the first trash tank. Recommend pumping scum from treatment units. There are two lids that have superficial damage, but we recommend replacing them. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/27/2021 | 01:26 PM
12/29/2020 |  |  | 185-STS-17544 | Tazewell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 12/29/2020 |  | 20.000000 |  |  | 1.700000 |  |  | Attached to this report |  | BOD: 20.0 TSS: 1.70 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12/29/2020 | Jan 1 1900 2:10PM
01/30/2020 |  | Routine, Scheduled | SP-05-57 | Stafford County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | None | Pump | Drip | Drip Tubing |  |  | ["Attached Growth Medium","Auxiliary Filter","Dispersal System Operation","Recirculation Pump"] | ["Attached Growth Medium","Auxiliary Filter","Dispersal System Operation","Recirculation Pump"] | [18 empty] | [Comments]: Replaced 5" Spin Filter. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/02/2020 | 11:52 AM
08/10/2020 | Alternative | Reportable Incident | 151-16-0007 | Lancaster | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | obsidian onsite services |  | joel | pinnix | [9 empty] | [] | ["Control Operation"] | [18 empty] | Replaced faulty float switch. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  |  | 12:00 AM
07/30/2020 | Alternative | Routine/Scheduled | 157-04-073 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | PremierTech, EFX | None | Pump | None | Aggregate Bed | None | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | Musty | Clear | [15 empty] | Annual service conducted. Primary Septic Tank at normal operating level - effluent screen serviced and noted that it has fractured and is in two parts. Pump Basin - at normal operating level - pump, float sensors and controls operating properly. Biofilter - Peatmoss biofilter noted to be in good condition - raked and turned - | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 07/31/2020 | 07:45 AM
06/30/2020 |  | Reportable Incident | 175-18-0327 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon |  |  |  |  | Pump | Pressure | Drip | Not Applicable |  | ["Dispersal System Operation"] | ["Dispersal System Operation"] | NA | [17 empty] | Checked drip field after 2 trees fell on top and found tubing broken in 2 places. Made the repair and checked drip rates. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  |  | 12:00 AM
02/12/2020 |  | Pump-Out Only | 234-13-73 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesapeake | R & K Septic, Inc. |  | Tina | Van Holten | [30 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/12/2020 | Jan 1 1900 8:00AM
07/23/2020 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Fairfax | FIVE STAR SEPTIC INC | 1942001248 | AARON | GOINS | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 07/23/2020 | 12:00 AM
05/21/2020 |  | Routine/Scheduled |  | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  |  |  | Aggregate Bed |  |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  |  | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 05/21/2020 | Jan 1 1900 8:00AM
10/01/2020 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | Aquarobic Services | 1934000142 | Michael | Blake |  |  | none | none | Pump | Gravity | Mound | Not Applicable |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | Annual inspection. Replaced element for canister filter as preventative maintenance. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 07/01/2022 | Jan 1 1900 10:30AM
09/10/2020 | Alternative | Reportable Incident | 136-16-0059 | Gloucester | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | Owner called due to the red light being on. Serviced system. Checked the pump, panel, & floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. Installed a re-build kit on the aerator. Replaced the lid on the Clearstream - 20" Tuf-Tite lid. The timer is set to 2 minutes every 2 hours. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 09/10/2020 | 12:00 PM
05/06/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | D-box closest to house is broken and will need replaced | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 |  | 04/14/2021 | 04:27 PM
04/21/2020 |  | Routine, Scheduled | -STS-43175 | Roanoke County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Alleghany-Roanoke | WAUGH, IAIN C | 1942001512 | IAIN | WAUGH | 1.000000 | 1500 | Septic Tank Only | Delta Environmental Products, DF Series | Pump | Drip | Drip Tubing | None | 175.000000 | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | [18 empty] | [Pumpout Comments]: Pumped out last year by Halls Septic not needed this year. [Comments]: Cleaned Blower filter and cleaned Drip Spin Filter DF unit minimal scum 1" Good Aeration, Clear Effluent Septic tank 1" scum 12" newish sludge, wipes visible floating in tank, be careful they can block up system pipes and create havoic and cost$$ Pump tank 12" fine sludge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/22/2020 | Jan 1 1900 10:56PM
02/21/2020 |  | Routine, Scheduled | SD-96-343 | Culpeper County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | Brown, Jason W | 1942001049 | Jason | Brown | 1.000000 | 1200 | Septic Tank Only | Puraflo | Pump | None | Elevated Sand Mound | None |  |  |  |  | none | [16 empty] | VENIS File Names: O&M Log feb 21 2020 Campbell.odt | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/23/2020 | 04:25 PM
06/02/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Roots were observed in the septic tank. It is very deep and it's not possible to see where they are coming in from. Homeowner has company coming to look and we will report back. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/27/2021 | 01:26 PM
06/30/2020 |  | RoutineScheduled | 10-113-039 | Buchanan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Effluent Screens"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
10/15/2020 |  | RoutineScheduled | 175-15-0116 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Pressure | Drip | UV |  | ["Attached Growth Medium","BlowerCompressorAerator Operation","Disinfection"] | ["BlowerCompressorAerator Operation","Attached Growth Medium","Disinfection"] | NA | [9 empty] | 14.000000 | [7 empty] | Septic-12"sludge 0"scum/Microfast-12"sludge (Media is clogged and needs chemical cleaning) Pump tank-2"sludge/ Blower air filter cleaned. system needs UV bulb, cord and sleeve. No breakout or spongy areas on the drip field. Drip rates Z1-6.7/Z2-6.5/Z3-6.5/ All repairs Jet UV-Light and cleaning were completed on 10/21/2020. Counts on 10/21: Pump start-9916/ Pump run-1129/ H-6/ HL-94 | This AOSS should now return to normal function after having provided the above state routine maintenance. |  |  | 12:00 AM
10/21/2020 |  | RoutineScheduled | 085-STS-31566 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Lyttle Service Co., LLC dba Stamie E. Lyttle Co | 1942001332 | Benjamin | Chapin | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
02/24/2020 | Alternative | Routine, Scheduled | 10-103-0020 | Amelia County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Piedmont | Dominion Septic, Inc | 1942001350 | Mike | Cook | 1.000000 |  | None | None | Pump | Distribution Box | Aggregate Bed |  |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/03/2020 | Dec 30 1899 5:36AM
10/07/2020 |  | RoutineScheduled | SD-06-33 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Soils, Inc. | 1940001392 | Markham | Smith | 2.000000 | 1500 | PuroFlo |  | Pump | Gravity | Trenches | Not Applicable | 43.700000 | [] | ["SludgeScum Accumulation","Septic Tank Baffles","Level Sensor Operation","Attached Growth Medium","Control Operation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 10/09/2020 | 08:10 AM
12/09/2020 |  | RoutineScheduled | 17-100-0507 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Environmental Systems Service | 1942001050 | Troy | Jenkins | [9 empty] | [] | [] |  | None | Discolored | 7.810000 |  |  |  |  | 12/09/2020 | Sample Tap | 20.000000 |  | 387.000000 | 4.000000 | 26.380000 |  | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12/21/2020 | 12:00 AM
04/09/2020 |  | RoutineScheduled | 107-04-0494 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Onsite Wastewater Services - May Supply | 1942001022 | Sara | Tusing | 1.000000 |  | none | none | Pump | Gravity | Pad | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 05/28/2021 | 05:41 AM
12/02/2020 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Fairfax | FIVE STAR SEPTIC INC | 1944001248 | AARON | GOINS | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
11/24/2020 |  | Reportable Incident |  | Frederick | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Lord Fairfax | POWELLS PLUMBING, INC. | 1942001036 | Kurt | Holthaus |  |  | Orenco Advantex | [6 empty] | ["Control Operation","Recirculation Pump","Sludge/Scum Accumulation"] | ["Control Operation","Recirculation Pump","Sludge/Scum Accumulation"] | N/A | [17 empty] | Replaced recirculation pump, contactor and pumped trash side of Advantex. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12/31/2020 | 01:09 PM
01/07/2020 |  | Follow-Up |  | Loudoun County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | None | None | Gravity | [24 empty] | [Comments]: installed new d-box lid. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/15/2020 | 06:36 AM
03/26/2020 |  | Routine, Scheduled |  | Loudoun County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | None | None | Pump | Distribution Box | Aggregate Trench | [23 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/12/2020 | 02:21 PM
03/10/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Fairfax | Hott, Joshua D. | 1942001301 | Joshua | Hott | 1.000000 | 1500 | Septic Tank Only | Puraflo | Pump | Distribution Box | Aggregate Trench | None |  | ["None"] | ["None"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/14/2020 | Jan 1 1900 1:27PM
07/28/2020 |  | Reportable Incident |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES MidAtlantic LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Gravity | Gravity |  | Not Applicable |  | ["Distribution Pump Operation" ,"Level Sensor Operation"] | ["Level Sensor Operation" ,"Distribution Pump Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced effluent pump & 3 floats. | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 |  | 04/15/2021 | 09:00 AM
05/18/2020 |  | RoutineScheduled | SD-13-64 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Soils, Inc. | 1940001392 | Markham | Smith | 2.000000 | 1500 | MicroFAST 0.75 |  | Pump | Gravity | Drip | Not Applicable | 50.000000 | [] | ["SludgeScum Accumulation","BlowerCompressorAerator Operation","Control Operation","Attached Growth Medium","Level Sensor Operation"] | NA | [17 empty] | Audio Not function to the ATU | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 07/13/2020 | 03:50 PM
03/02/2020 |  | Routine, Scheduled | 234-12-85 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesapeake | R & K Septic, Inc. |  | Robbie | Van Holten |  |  | Clearstream ATU |  | Pump | Distribution Box |  | None |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] |  |  |  | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/02/2020 | Jan 1 1900 12:45PM
08/18/2020 |  | Routine/Scheduled | 124-STS-2379 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Rejected | EHD - Chickahominy | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 100 | Delta Environmental Products, UC Series | None | Pump | Drip | Drip Tubing | None | 450.000000 |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | Musty | Clear | [15 empty] | Routine service conducted. Primary septic tank in normal operating level. Processing tank - in normal operating level - aeration operating - blower unit serviced. Discharge / Pump Tank - normal operating level - discharge pump serviced - float sensor and controls operating properly. Drip field - automatic headworks - Controls and headworks operating properly - drip disk filters serviced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 08/25/2020 | Jan 1 1900 1:45PM
01/06/2020 |  | Routine, Scheduled | {FIPSCode}-STS-18002 | Bland County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Mount Rogers | DEEL, DENNY M | 1942001097 | DENNY | DEEL |  |  |  | None | Gravity | Distribution Box | Aggregate Bed | None | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Effluent Screens"] |  | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/05/2020 | Jan 1 1900 3:42PM
09/08/2020 |  | Routine/Scheduled | 109-09-0451 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Central | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Delta Environmental Products, DF Series |  | Gravity | Distribution Box |  | None |  | ["None"] | ["Blower/Compressor/Aerator Operation","Sludge/Scum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 09/08/2020 | 02:45 PM
10/07/2020 |  | RoutineScheduled | 107-03-0582 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Onsite Wastewater Services - May Supply | 1942001022 | Sara | Tusing | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Inspection DKS | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 05/28/2021 | 05:41 AM
04/23/2020 |  | RoutineScheduled |  | Fairfax | This AOSS is functioning as designed and in accord | Approved | EHD - Fairfax | Great Falls Septic Service | 1942001301 | Joshua | Hott | 1.000000 | 1875 |  | Puraflo | Pump | Distribution Box | Aggregate Trench | None | 500.000000 | ["Effluent Screens"] | ["Effluent Screens"] |  | Low | [17 empty] | This AOSS is functioning as designed and in accord |  |  | 12:00 AM
10/30/2020 |  | Routine/Scheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | POWELLS PLUMBING, INC. | 1942001036 | Kurt | Holthaus | 1.000000 | 1500 |  |  | Pump | Manifold | Aggregate Trench |  | 600.000000 | ["Effluent Screens"] | ["Effluent Screens"] | N/A | [17 empty] | Annual Inspection - Serviced effluent screen(s). | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 11/04/2020 | 01:07 PM
05/07/2020 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | SES MidAtlantic LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 |  | 04/15/2021 | 09:00 AM
12/02/2020 |  | Reportable Incident | 800-STS-14427 | Suffolk | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | Owner called due to the red light being on for about a week or so. Serviced system. Checked the pump, panel & floats (ok). Cleaned the filter in the Clearstream and cleaned the disc filter. Changed the diffuser in the Clearstream and changed the filter in the aerator. Replaced the UV ballast, replaced the buzzer, and replaced the mute button. Pumping company pump out the pump tank and cleaned it and pump the trash off the top and bottom of the Clearstream tank. The pump tank is leaking and the sealer is in the bottom of the tank. The timer is set to 8 minutes every 2 hours. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. |  | 12/02/2020 | Jan 1 1900 12:00PM
10/02/2020 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Pump | Distribution Box |  | None |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Recirculation Pump","Sludge/Scum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Recirculation Pump","Sludge/Scum Accumulation"] | N/A |  | 2.83 | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 10/02/2020 | Jan 1 1900 10:00AM
04/01/2020 |  | Routine, Scheduled | 175-02-0377 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Orenco Advantex |  |  |  |  | None |  | ["Effluent Screens","Recirculation Pump"] | ["Effluent Screens","Recirculation Pump"] |  | Good | Clear | [15 empty] | Pump 1 Amps 12.66 ETM 422836 m Cycles 847297 Pump 2 Amps 11.35 ETM 3469 Cycles 8871 Septic Sludge 7" Scum 1" ATU Sludge 10" Scum 0 Pump Sludge 3" Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/01/2020 | 02:45 PM
09/22/2020 |  | RoutineScheduled | {FIPSCode}-STS-20610 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Lenowisco | Wise Co Health Dept |  | Rodney | Neece | 1.000000 | 1 | ATU |  | Gravity | Gravity | Discharge | Chlorination |  |  |  |  | None | Clear | 6.200000 | 8.000000 |  | 0.000000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 09/22/2020 | 12:00 AM
12/18/2020 |  | RoutineScheduled | SD-09-254 | Fauquier | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001068 | David | Stewart |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Attached Growth Medium" ,"Auxiliary Filter" ,"Control Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | ["Distribution Pump Operation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Control Operation" ,"Dispersal System Operation" ,"Attached Growth Medium" ,"Auxiliary Filter"] | YES | [15 empty] | Will be sent separately | Inspected | Recirc inlet riser broken above grade. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
12/29/2020 |  |  | 18-192-140 | Tazewell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 12/29/2020 |  | 5.880000 |  |  | 4.400000 |  |  | Attached to this report |  | BOD: 5.88 TSS: 4.40 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12/29/2020 | Jan 1 1900 5:25PM
12/19/2020 |  | RoutineScheduled | {FIPSCode}-STS-58318 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Wastemaster Inc |  | Timothy | Jenkins | 1.000000 |  | Sand Mound |  |  |  | Mound | Chlorination |  | [] | [] |  | Musty | Clear | 6.200000 |  |  | 2.200000 | [11 empty] | Mound and Tank below grade | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 01/14/2021 | 09:55 AM
07/27/2020 |  | RoutineScheduled | 069040218 | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | ["None"] | ["None"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 07/28/2020 | 12:00 AM
02/24/2020 |  | Routine, Scheduled | 234-13-129 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesapeake | R & K Septic, Inc. |  | John | Butt, Jr |  |  | Clearstream ATU |  | Pump | Distribution Box | Aggregate Bed | None |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] |  |  | 27.9 | 8.040000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/24/2020 | Jan 1 1900 3:30PM
09/03/2020 |  | Reportable Incident |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | SES MidAtlantic LLC | 1942001203 | James | Green | 1.000000 |  | Multiflo FTB | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Replaced electric box on pump tank. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/15/2021 | 09:00 AM
12/02/2020 | Alternative | Routine/Scheduled | 151-04-405 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | PremierTech, EFX |  | Pump | None | Aggregate Bed | None | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | Musty | Clear | [15 empty] | Routine Service Primary Septic Tank - normal level - effluent screen serviced. Pump Basin - normal level - pump, float sensors & controls operating. Biofilter - Fiberglass - peatmoss in poor condition - ponding - raked / turned - recommend peat replacement. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 12/03/2020 | 08:00 AM
10/20/2020 |  | Routine/Scheduled | 15-163-0057 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chickahominy | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1500 | Norweco Singulair ATU |  | Pump | Distribution Box | Aggregate Trench | None | 450.000000 |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | Musty | Clear | [15 empty] | Routine Service Trash Tank - normal operating level - Aeration Tank - normal operating level - Aspirator serviced. Clarifier - normal operating level - effluent screen serviced. Pump Tank - normal operating level - pump, float sensors and controls operating properly. D-Box - normal level - all laterals accepting effluent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 10/21/2020 | Jan 1 1900 9:30AM
01/10/2020 |  | Routine, Scheduled | 177-14-0213 | Spotsylvania County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | None | Pump | Distribution Box | Aggregate Trench |  |  | ["Attached Growth Medium","Effluent Screens","Recirculation Pump"] | ["Attached Growth Medium","Effluent Screens","Recirculation Pump"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/04/2020 | 07:46 AM
03/13/2020 |  | Routine, Scheduled | SD-04-063 | Orange County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | CLARK, MICHAEL J | 1934000023 | MICHAEL | CLARK |  |  | Septic Tank Only | Septic Tank Only | None | None | None | None |  |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/17/2020 | 04:37 AM
01/02/2020 |  | Reportable Incident | 179-10-0308-SR | Stafford County | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson |  |  | Orenco Advantex | None | Pump | Drip | Drip Tubing |  |  | ["Distribution Pump Operation"] | ["Distribution Pump Operation"] | [18 empty] | [Comments]: Replaced piece of flex hose in headworks that had split (next to filter cap) and was leaking effluent. Pressure initially did not build on return line gauge during test cycle. Checked for leaks in dripfield that would cause a pressure loss and did observe about 4 wet spots that were only 2" in diameter. All wet spots were in lower 1/4th of dripfield. Dug up one wet spot and didn’t find a problem with the emitter, but there was only 3-4" of cover over the tubing. Removed a couple of small pebbles from field flush valve that were preventing it from fully closing. Pressure then built to 30 psi. Recommended owner contact AOSE for further evaluation. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 01/15/2020 | 10:52 AM
10/05/2020 |  | RoutineScheduled | 043-12-0077 | Clarke | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Greenway Engineering | 1942001008 | Jeremy | Ferguson | 1.000000 | 1500 | Microfast | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","SludgeScum Accumulation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 10/05/2020 | 11:00 AM
07/24/2020 |  | RoutineScheduled | 2006-143-0353 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Advantex |  | Pump | Gravity | Trenches |  |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | ["Attached Growth Medium","Recirculation Pump","Distribution Pump Operation"] | YES | [16 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
09/15/2020 |  | RoutineScheduled | 179-07-0108-SWP | Stafford | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | ["Level Sensor Operation" ,"Control Operation" ,"Distribution Pump Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced vertical reed switch to correct repeat alarms from smart filter panel. Pump tank effluent was down to pump intake. Timer float had settled on top of the pump in the on position. Repositioned the float bar to prevent future occurrences. Septic tank will need pumped out before next year's inspection. Owner to make arrangements. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
12/03/2020 | Alternative | Routine/Scheduled | 166-11-093 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 3.000000 | 3000 | Microfast |  | Pump | Distribution Box | Aggregate Bed |  |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12/03/2020 | 05:00 PM
08/24/2020 |  | RoutineScheduled |  | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 2705051738 | Joshua | Hott |  |  | Septic | Puraflo | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [8 empty] | 08/26/2020 | Sample Chamber | [6 empty] | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
04/30/2020 |  | RoutineScheduled | 185-STS-17543 | Tazewell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. |  | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Effluent Screens"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
05/13/2020 |  | RoutineScheduled | SD-06-78 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Soils, Inc. | 1940001392 | Markham | Smith | 2.000000 | 1500 | Effluent pump | Peat filter Puraflo (6 pods ) | Pump | Gravity | Trenches | Not Applicable | 65.600000 | ["Attached Growth Medium","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Effluent Screens","Septic Tank Baffles","SludgeScum Accumulation"] | [] | YES | Musty | Cloudy | [15 empty] | Floats look corroded Trash compartment 2in scum 8in sludge Pump chamber 2 in sludge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 07/09/2020 | 01:35 PM
05/01/2020 |  | RoutineScheduled | 109-04-0797 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1000 | Multiflo |  | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | NA | [16 empty] | Inspected | Septic Tank 1" scum, 10" sludge, Pump Tank 6" sludge.Discharge pump had burned up, Replaced the pump, Added ROOTX treatment. New pump We0515H Goulds 220v 1/2hp 6.4amp draw added handle to filter. Pod 4 had most worn peat and 1 was driest. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 05/12/2020 | 09:30 AM
12/15/2020 |  | Reportable Incident |  | Frederick | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Lord Fairfax | POWELLS PLUMBING, INC. | 1942001036 | Kurt | Holthaus |  |  | Puraflo | [6 empty] | ["Control Operation","Level Sensor (Float) Operation"] | ["Control Operation","Level Sensor (Float) Operation"] | N/A | [17 empty] | Replaced float and adjusted timer. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12/31/2020 | 10:47 AM
07/03/2020 |  | RoutineScheduled | SD-05-122 | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Wastemaster Inc |  | Timothy | Jenkins | 2.000000 |  | ATU | Polishing Sandfilter | Gravity | Gravity | Discharge | Chlorination |  | [] | [] |  | Musty | Clear | 6.600000 |  | 30.000000 | 1.800000 | [12 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 07/23/2020 | 03:45 PM
04/27/2020 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump | Drip | Elevated Sand Mound | UV Light |  | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  |  | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/27/2020 | Jan 1 1900 9:00AM
06/23/2020 |  | Routine/Scheduled |  | Frederick | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Review | EHD - Lord Fairfax | POWELLS PLUMBING, INC. | 1942001036 | Kurt | Holthaus |  |  | Microfast |  | Pump | Drip | Drip Tubing |  | 300.000000 | ["Blower/Compressor/Aerator Operation","Control Operation","Level Sensor (Float) Operation"] | ["Blower/Compressor/Aerator Operation"] | N/A | [17 empty] | Real Estate Sale Inspection - Need to repair control panel and repair alarm float. Need septic system plans to verify all system components. Serviced blower. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. |  | 07/09/2020 | 12:35 PM
01/08/2020 |  | Routine, Scheduled | 177-07-0413-SWP | Spotsylvania County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Puraflo | None | Pump | Distribution Box | Aggregate Trench |  |  | ["Attached Growth Medium","Effluent Screens","None"] | ["Attached Growth Medium","Effluent Screens","None"] | [18 empty] | [Comments]: We recommend replacing the EZ Set lid on the Pump Tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/04/2020 | 07:46 AM
09/11/2020 |  | RoutineScheduled | 107-07-0232 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter | [9 empty] | ["None"] | ["None"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 06/02/2021 | 12:00 AM
04/02/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Loudoun | SES MidAtlantic LLC | 1942001203 | James | Green | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/15/2021 | 09:00 AM
07/13/2020 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump | Distribution Box | Aggregate Bed | None |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  |  | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 07/13/2020 | Jan 1 1900 2:45PM
07/24/2020 |  | Pump-Out Only |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | POWELLS PLUMBING, INC. | 1942001036 | Kurt | Holthaus |  |  | Microfast | [6 empty] | ["Sludge/Scum Accumulation"] | ["Sludge/Scum Accumulation"] | N/A | [17 empty] | Pumped Microfast | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 10/08/2020 | 03:24 PM
06/23/2020 |  |  | 10-192-161 | Tazewell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 06/23/2020 |  | 16.500000 |  |  | 11.200000 |  |  | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 06/23/2020 | 12:00 AM
06/03/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | SES MidAtlantic LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | Puraflo | Gravity | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/15/2021 | 09:00 AM
03/04/2020 |  | Follow-Up |  | Prince William County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Prince William | SEAMON, CHARLIE L | 1942001108 | CHARLIE | SEAMON |  |  | Septic Tank Only | Microfast | Pump | Manifold | Drip Tubing | None |  | ["SludgeScum Accumulation"] | ["SludgeScum Accumulation"] | [18 empty] | [Comments]: Follow up from Performance Inspection done on March 02,2020: All repairs done-12x24 riser and 24" lid installed. Flag heater installed in the drip hydraulic unit. Pump out of the Microfast unit done on 3/3/2020 by SeptiClean. System now functioning as designed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/04/2020 | 08:22 AM
03/18/2020 |  | Routine, Scheduled | 099-12-0071-SP | King George County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Ware, Michele P | 1942001165 | Michele | Ware |  |  | Septic Tank Only | Septic Tank Only | None | None | None | None |  |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | [8 empty] | 03/18/2020 | [7 empty] | Attached to this report |  | VENIS File Names: R0345542.pdf | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/25/2020 | 07:42 AM
06/23/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Sale inspection on a alternative septic system. The state law requires that all alternative septic systems must be inspected EVERY year between Jan 1 and July 1 and filed with the state and the local county. The exterior septic control panel is a timed dose. There are 2 pvc clean outs. The pvc sewer line was camera snaked and was clear. The concrete septic tank has a plastic riser on the outlet side of the tank. The septic and DF 60 aeration tanks were both pumped out and inspected for any leaks or cracks none were found. The air blower was working and there was vigorous bubbling in the atu tank. The pump tank, pump, floats and force main were inspected. Per the realtor no d-boxes were dug up. The drain field was probed and dry. At time of inspection all components were in working condition. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/14/2021 | 04:27 PM
03/16/2020 |  | Routine, Scheduled | 181-10-0003 | Rockbridge County | This AOSS should now return to normal function after having provided the above stated routine maintenance. | Approved | EHD - Central Shenandoah |  |  |  |  | 1.000000 | 1500 |  | Orenco Advantex | Pump | Distribution Box | Aggregate Trench | None |  | ["Control Operation","Distribution Pump Operation"] | ["Control Operation","Distribution Pump Operation"] |  | Musty | Clear | [5 empty] | 03/16/2020 |  | 99.000000 | [5 empty] | Attached to this report |  | [Comments]: Replaced Recirc Pump Recirc Pump Settings: Off 19.7min On .3min ETM-159.8Hr Cycle Count-31824 Sludge/Scum Accumulations: Comp.1-2"/0" Comp.2- 4"/0" VENIS File Names: 130 Ridgemore 3-16-20.pdf | This AOSS should now return to normal function after having provided the above stated routine maintenance. |  | 04/06/2020 | 30-12-1899 04:24 PM
09/10/2020 |  | Routine/Scheduled | 15-120-199AR | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. |  |  | Aqua Klear |  | Pump |  |  |  |  | ["Control Operation","Distribution Pump Operation"] | ["Control Operation","Distribution Pump Operation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 09/10/2020 | Jan 1 1900 10:00AM
09/26/2020 |  | Follow-Up | 2031-96-153 | Prince William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Prince William | Wastemaster Inc |  | Timothy | Jenkins | 2.000000 |  | Sequencing Bat Reactor |  |  | Gravity | Discharge | Chlorination |  | [] | [] |  | Musty | Clear | 6.400000 |  | 40.000000 | 1.300000 | [11 empty] | System in high level alarm. Alarm has been silenced. Aerator running but not aerating. Sand Filter blinded. Temporary pump installed by others with flow directed back to bio reactor. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. |  | 09/26/2020 | 12:25 PM
11/09/2020 |  | RoutineScheduled | 061-16-250 | Fauquier | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 5.000000 |  | Bio Barrier | Bio Barrier | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation"] | ["Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Biweekly inspection. Peak count for surge tank now at 1,034 (45 new cycles). In the past 12 days, an average of 2,747.1 gals per day at 274.7 gals per dose (avg.) was pumped to the dripfield for a total of 32,966 gallons. System is considered not operating as designed due to not meeting nitrogen limits. | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
11/02/2020 |  | RoutineScheduled | 107-06-0336 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Pump | Pressure | Drip | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 06/02/2021 | 12:00 AM
06/01/2020 |  | RoutineScheduled | 179-12-0159-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump" ,"Attached Growth Medium"] | ["Attached Growth Medium" ,"Effluent Screens" ,"Recirculation Pump" ,"Distribution Pump Operation"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 |  | 04/09/2021 | 03:25 PM
03/05/2020 | Alternative | RoutineScheduled | 115-06-0486 | Campbell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | WAUGH, IAIN C | 1942001512 | IAIN | WAUGH | 1.000000 | 1500 | Septic Tank | Ecoflo | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","Effluent Screens"] | ["Attached Growth Medium","Effluent Screens"] | [18 empty] | [Comments]: Septic Tank 2" Scum 10" Sludge, Pump Basin 1" scum 3" sludge, Pump Opperational, Alarm opperational, Turned peat in treatment tanks. Condition Poor, Dry in 3 quadrants ponding in 1. Broke up and drained, Effluent filter had backed up 4 " above outlet, Cleaned tipping tray, owner wants to get peat replaced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 03/07/2020 | 09:44 AM
09/10/2020 |  | Pump-Out Only |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU | [8 empty] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 09/10/2020 | Jan 1 1900 8:00AM
06/22/2020 |  | Reportable Incident | 175-05-0899 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green | [9 empty] | ["Dispersal System Operation"] | ["Dispersal System Operation"] | [18 empty] | Replaced air relief valves. | This AOSS should now return to normal function after having provided the above state routine maintenance |  | 06/22/2020 | 09:30 AM
09/01/2020 |  | Routine/Scheduled | 18-142-0272 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chickahominy | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. |  |  | Clearstream ATU | [6 empty] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 09/01/2020 | Jan 1 1900 2:30AM
09/17/2020 |  | Routine, Scheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Biomicrobics MicroFAST |  |  |  |  | None |  | ["Blower/Compressor/Aerator Operation"] | ["Blower/Compressor/Aerator Operation"] |  | Good | Clear | [15 empty] | Pump Amps 10.32 ETM 8 hrs 48 mins Cycles 172 Pump Amps 9.90 ETM 8 hrs 48 mins Cycles 171 Septic Sludge 10" Scum 2" ATU Sludge 6" Scum 0 Pump Sludge 2" Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 09/17/2020 | Jan 1 1900 1:03PM
05/04/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | The electric box cover needs to be replaced. Wires exposed to the elements | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 |  | 04/14/2021 | 04:27 PM
11/16/2020 |  | RoutineScheduled |  | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001301 | Joshua | Hott | [9 empty] | [] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
04/03/2020 |  | Reportable Incident | 175-14-0220 | Prince William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Prince William | SES Mid Atlantic | 1942001236 | S. Michael | Lynn | 1.000000 | 500 | EcoPod | None | Pump | Drip | Drip Tubing | UV Light | 300.000000 | ["Dispersal System Operation"] | ["Dispersal System Operation"] |  | good | Good | [15 empty] | Landscaper noticed wet area just below drip field. Needs further investigation to determine if effluent is moving laterally or there is a leaking pipe. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 04/03/2020 | 05:03 PM
04/29/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | krain leaking and drain field oversaturated | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 |  | 04/14/2021 | 04:27 PM
05/07/2020 |  | Reportable Incident | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance | Approved | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green | [9 empty] | ["Dispersal System Operation"] | ["Dispersal System Operation"] | [18 empty] | Replaced 2 check valves in D/F. | This AOSS should now return to normal function after having provided the above state routine maintenance |  | 05/07/2020 | Jan 1 1900 2:00PM
09/11/2020 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Gravity | Distribution Box |  | None |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  |  | 5.790000 | 5.200000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 09/11/2020 | Jan 1 1900 11:15AM
06/03/2020 |  | RoutineScheduled | 099-18-0121 C-SWP | King George | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart |  |  | Orenco Advantex | none | Pump | Gravity | Drip | UV |  | ["Distribution Pump Operation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Attached Growth Medium" ,"Auxiliary Filter" ,"Control Operation" ,"Dispersal System Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | ["Effluent Screens" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"Attached Growth Medium" ,"Auxiliary Filter" ,"Control Operation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"SludgeScum Accumulation"] | YES | [15 empty] | Will be sent separately | Inspected | BOD and Fecal collected, waiting on results. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
03/24/2020 |  | Routine, Scheduled | 109-07-0791 | Bedford County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Central | WAUGH, IAIN C | 1942001512 | IAIN | WAUGH | 1.000000 | 1500 | Septic Tank Only | Multiflo ATU | Pump | Drip | Drip Tubing | None |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | [18 empty] | [Pumpout Comments]: No Pumping needed [Comments]: Septic Tank 2-3" scum 5" sludge Treatment tank- Good Aeration, Deck minimal build up on socks, it was pumped last year, Pump is good backwashed system and flushed drip lines. cleaned spin/Drip filter. Alarm test good, Drain field appears dry and unremarkable Pump tank 10-12" light sludge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/24/2020 | 10:15 PM
01/30/2020 |  | Routine, Scheduled |  | Louisa County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Blue Ridge | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | None | Pump | Distribution Box | Aggregate Trench |  |  | ["Attached Growth Medium","Distribution Pump Operation","Effluent Screens","Recirculation Pump"] | ["Distribution Pump Operation","Effluent Screens","Recirculation Pump"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/02/2020 | 11:52 AM
11/20/2020 |  | RoutineScheduled | 145-03-0066 | Highland | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1500 | Retrofast |  | Pump | Pressure | Drip |  |  | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | NO | [17 empty] | The system did not need to be pumped. The blower was not working so it was assessed and replaced. The spin filter was cleaned. The controls were operating as designed. The field pressures were working as designed. There were no visible leaks in the drip field. The lids were secured. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12/28/2020 | 09:53 PM
04/01/2020 |  | Routine, Scheduled | VAG408292 | Rockingham County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Central Shenandoah |  |  |  |  | 1.000000 |  |  | Microfast | Gravity | None | Alternative Discharge | Chlorine |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/22/2020 | 30-12-1899 06:39 PM
09/02/2020 |  | Reportable Incident |  | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | [9 empty] | ["Level Sensor Operation"] | ["Level Sensor Operation"] | [18 empty] | Replaced faulty alarm float/ Counts: Pump 1-657 ETM-26h 44m/ Pump 2-645 ETM-26h 16m/ Peak-11/ High-10 | This AOSS should now return to normal function after having provided the above state routine maintenance. |  |  | 12:00 AM
01/13/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Biomicrobics MicroFAST |  | Pump | Drip | Drip Tubing | UV Light |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] |  | Good | Good | [15 empty] | [Comments]: Spin filter cleaned.Pump Amps 10.21 ETM 694h Cycles 5334Water Meter Reading 119120Septic Sludge 12" Scum 2"ATU Sludge 13" Scum 0Pump Sludge 13" Scum 0Pump Sludge 0 Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/13/2020 | Jan 1 1900 11:40AM
07/09/2020 |  | Initial Visit | 147-11-0112 | James City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Peninsula | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | Biomicrobics MicroFAST | None | Gravity | Distribution Box | Aggregate Trench | None | 450.000000 |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | Musty | Clear | [15 empty] | Initial service / inspection. Septic tank at normal operating level BioMicrobics FAST operating properly - compressor serviced. Absorption field reported to be deep install - 136" below grade. No indication of surfacing. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 07/10/2020 | Jan 1 1900 1:30PM
05/20/2020 |  |  |  | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | [8 empty] | 05/20/2020 | Sample Chamber | 17.000000 | [7 empty] | Septic/ATU had 6" sludge and 2" scum. Atu HAD 4" SLUDGE.Cleaned air filter for blower Pump tank had 2" sludge. Replaced alarm buzzer and light. Replaced current sensor in panel. Pump cnts- 20377 ETM-200h 27m Peak-0 H/L-1 W/M- 019202 | This AOSS should now return to normal function after having provided the above state routine maintenance. |  |  | 12:00 AM
03/20/2020 |  | Routine, Scheduled |  | King & Queen County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Three Rivers | Madison Environmental LLC | 1934 000061 | Larry | Madison, Jr. |  |  | SludgeHammer |  | Pump | Distribution Box |  |  |  | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/20/2020 | 10:00 AM
11/24/2020 |  | Follow-Up |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintanence requirements | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Gravity | Gravity |  | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | New T's in the septic tank have been installed and a new conveyance line. LCH inspected these components | This AOSS is not functioning as designed or in accordance with the performance/maintanence requirements |  | 04/14/2021 | 04:27 PM
05/11/2020 | Alternative | RoutineScheduled | 2006-143-0188 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Advantex |  | Pump |  | Trenches |  |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 09/11/2020 | 12:00 AM
01/21/2020 |  | Routine, Scheduled | 093-07-0102 | Isle of Wight County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Western Tidewater | R & K Septic, Inc. |  | John | Butt, Jr |  |  |  |  | Pump | Distribution Box |  | None |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] |  |  |  | 7.780000 | 2.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/21/2020 | Jan 1 1900 10:30AM
12/08/2020 |  | RoutineScheduled | 139-05-0554 | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | None | Clear | 7.520000 |  |  |  |  | 12/08/2020 |  | 8.000000 |  |  | 9.500000 | [5 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12/21/2020 | 03:00 PM
06/20/2020 |  | RoutineScheduled | ST-04-491 | King George | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  | ["Attached Growth Medium" ,"Control Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | ["Control Operation" ,"Distribution Pump Operation" ,"Attached Growth Medium" ,"Effluent Screens" ,"Level Sensor Operation" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | YES | [15 empty] | Will be sent separately | Inspected | Infiltration on pump tank wedge lid and septic tank inlet pump needs replaced. System needs pump out. Please contact pumper for pump out of tanks. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
05/11/2020 |  | RoutineScheduled | SD-00-111 | Fauquier | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation" ,"Distribution Pump Operation"] | ["Dispersal System Operation" ,"Distribution Pump Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Routine inspection. No way to verify settings or cycle counts on old Mitsubishi cpu. Separate counters showing 134 high level alarms, and 12,681 peak cycles. Replaced zone 2 remote solenoid. LB for solenoid connections is half buried and holding water. Should be replaced and re-positioned. High drip rate on zone 2. No effluent to surface seen. Check valves or zone valve diaphragms may be getting weak. Flush rate was low, but measured before cleaning pump vault filter (replaced sock). Will reevaluate next year. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
12/16/2020 |  | Follow-Up | 175-06-0016 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green | [9 empty] | ["None"] | ["None"] | [18 empty] | Remounted electric box. Installed new strip heater. | This AOSS should now return to normal function after having provided the above state routine maintenance |  | 12/16/2020 | 04:00 PM
06/19/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/27/2021 | 01:26 PM
11/23/2020 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump | Distribution Box |  | None |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  |  | 7.680000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 11/23/2020 | Jan 1 1900 2:30PM
08/25/2020 |  | Follow-Up |  | Culpeper | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 | Pending Review | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 2.000000 |  | none | none | Pump | Gravity |  | UV |  |  |  | NA | [9 empty] | 28.000000 |  | 2419.600000 | 12.000000 |  |  | Will be sent separately | Inspected | DO 4.18 Effluent sampling only | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 |  | 04/09/2021 | 03:25 PM
08/18/2020 |  | RoutineScheduled |  | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Catoctin Environmental |  | Cameron | Creighton | 2.000000 | 2000 | Microfast |  | Pump | Pressure | Mound | UV |  | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
10/09/2020 |  | RoutineScheduled | 02-113-304 | Buchanan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
01/29/2020 |  | Routine, Scheduled |  | Albemarle County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Blue Ridge | CLARK, MICHAEL J | 1934000023 | MICHAEL | CLARK |  |  | Septic Tank Only | Septic Tank Only | None | None | None | None |  |  | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/09/2020 | 05:00 AM
12/09/2020 |  | Follow-Up | SD-05-424 | Orange | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Dispersal System Operation"] | ["Auxiliary Filter" ,"Dispersal System Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced spin filter, water meter, and EZ Set riser lid on pump tank. | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 |  | 04/09/2021 | 03:25 PM
03/23/2020 |  | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Greenway Engineering | 1942001008 | Jeremy | Ferguson | 1.000000 | 1000 | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","Level Sensor Operation","SludgeScum Accumulation","Effluent Screens"] | ["Attached Growth Medium","Level Sensor Operation","SludgeScum Accumulation","Effluent Screens"] | YES | [17 empty] | some ponding in peat due to high water use. Will check condition next year. System is operational. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 09/29/2020 | 10:45 AM
05/19/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/14/2021 | 04:27 PM
09/23/2020 |  | Routine/Scheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Loudoun | POWELLS PLUMBING, INC. | 1942001036 | Kurt | Holthaus | 1.000000 | 1250 | Puraflo |  | Pump | Distribution Box | Aggregate Trench |  | 600.000000 | ["Effluent Screens"] | ["Effluent Screens"] | N/A | [17 empty] | Annual Inspection - Serviced effluent screen(s). | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 09/30/2020 | 02:33 PM
01/24/2020 |  | Routine, Scheduled |  | Loudoun County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | Clearstream | None | Pump | Distribution Box | Gravel-Less Trench | [5 empty] | YES | YES | [15 empty] | [Comments]: Sale inspection on a alternative septic system. The timed dose exterior control panel was inspected. There a 2 pvc cleanouts. The septic tank has risers on the inlet and outlet. The tank was pumped out and inspected for any leaks or cracks. The atu air blower is working as it should. The pump tank, pump, floats, and force main were inspected. The splitter and both d-boxes were dug up they were about 10" in the ground and all 3 were concrete and in working condition. The header lines were camera snaked and the drain field was probed. At this time all components were in working condition. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/02/2020 | 04:43 AM
11/10/2020 | Alternative | Routine/Scheduled | 157-12-0074 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 2000 | Clearstream |  | Pump | Manifold | Aggregate Bed | UV Light | 450.000000 |  | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | Musty | Clear | [15 empty] | Real Estate Inspection Trash Tank - normal operating level Aeration Tank - normal operating level - compressor serviced. Orenco UV - functioning - quartz sleeve serviced. Pump Tank - normal operation level - pump serviced, float sensors and controls operating properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 11/11/2020 | 07:30 AM
12/08/2020 |  | RoutineScheduled | 154-08-0188 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Randy's Complete Water & Wastewater Services | 1942001335 | Randy | Gray | 1.000000 | 1000 | Biomicrobics |  | Pump | Pressure | Drip | Not Applicable | 75.000000 | ["None"] | ["Other"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 05:25 PM
10/02/2020 |  | Routine/Scheduled | 136-16-0045 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 2000 | Clearstream |  | Pump | Drip | Drip Tubing | UV Light | 450.000000 |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | [17 empty] | Pumped and refilled aeration tank. Real Estate Inspection Trash Tank - normal operating level Aeration Tank - normal operating level - compressor serviced. Pump Tank - normal operating level - pump serviced - float sensors and controls operating properly. Obsidian U.V. - Bulb burned - needs replaced. Drip Dispersal - drip screen serviced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 10/16/2020 | 09:45 AM
07/30/2020 |  | RoutineScheduled | 027-STS-15415 | Buchanan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Effluent Screens"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
10/01/2020 |  | RoutineScheduled | SD-13-63 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Soils, Inc. | 1942001004 | Markham | Smith | 2.000000 | 1500 | PuroFlo |  | Pump | Gravity | Pad | Not Applicable | 58.800000 | [] | ["Attached Growth Medium","SludgeScum Accumulation","Septic Tank Baffles","Control Operation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 10/09/2020 | 07:55 AM
01/02/2020 |  | Routine, Scheduled |  | Louisa County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Blue Ridge | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | None | None | Gravity | Distribution Box | Aggregate Trench |  |  | ["Attached Growth Medium","BlowerCompressorAerator Operation","Dispersal System Operation","Effluent Screens","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Dispersal System Operation","Effluent Screens","Septic Tank Baffles","SludgeScum Accumulation"] |  | YES | YES | [7 empty] | 8.000000 | [7 empty] | [Comments]: BOD collected. Relocated blower to top of ATU. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/15/2020 | 10:52 AM
07/01/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Sale inspection on a alternative septic system. The state requires all alternatives to be inspected every year between Jan 1 to July 1 and filed with the state and local county. The septic control panel is a exterior timed dose. There is 1 pvc clean out near the house. The pvc sewer line was camera snaked and was clear. The septic tank was pumped out and inspected. The air blower filter was cleaned. The pump tank, pump, floats and force main were inspected. The 8 port concrete surge box was dug up and the 15 port concrete d-box was dug up and all 7 header lines were camera snaked and were clear. The drain field was probed and dry. at time of inspection all components were in working condition. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/14/2021 | 04:27 PM
08/28/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | The inlet tee on the Microfast tank is pitched upward. There is settling around the tanks and it is not clear whether the sewer line has settled or not. Along with the settling around and inbetween the tanks, the soil around the blower has erroded and the cinderblock base is exposed. The gaskets on the pump tank riser for the supply and return have partially popped out and need to be reseated and sealed. The air release valve vertical pipe is high enough that the valve box sits on top and hangs freely with several inches under before there is soil. These should be lowered or fill brought up to prevent damage and protect from freezing of the manifold. Homeowner is contacting builder for repairs. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/27/2021 | 01:26 PM
02/27/2020 |  | Routine, Scheduled | 228-11-0559 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Virginia Beach | [7 empty] | Septic Tank Only | None | None | None | None | [11 empty] | 02/27/2020 |  | 12.000000 |  | 76.000000 | 1.000000 | 32.860000 |  | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/27/2020 | Jan 1 1900 8:30AM
03/17/2020 |  | RoutineScheduled |  | Warren | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Lord Fairfax | Onsite Wastewater Services - May Supply | 1942001022 | Sara | Tusing | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/28/2021 | 05:41 AM
03/07/2020 |  | Routine, Scheduled | 171-10-0376 | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Lord Fairfax | DOVEL, JERRY A | 1942001116 | JERRY | DOVEL | 1.000000 |  |  | Septic Tank Only | None | Drip | None | None | [22 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/07/2020 | 07:36 PM
08/07/2020 |  | RoutineScheduled | SWP-05-438 | Stafford | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 2.000000 |  | Best 1 | none | Pump | Gravity | Trenches | Not Applicable |  | ["Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Control Operation" ,"BlowerCompressorAerator Operation"] | ["Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Control Operation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"BlowerCompressorAerator Operation"] | YES | [15 empty] | Will be sent separately | Inspected | Roots at septic tank inlet wedge lid. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
12/08/2020 |  | Routine/Scheduled | 199-07-0049 | York | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Peninsula | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | Clearstream |  | Pump | Distribution Box | Aggregate Trench | None | 450.000000 |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | Musty | Clear | [15 empty] | Septic tank pumped for Real Estate Inspection Real Estate Inspection (REI) Full service conducted 09/22/2020 Septic tank - normal level - pumped for inspection. Aeration Tank - normal level - compressor re-serviced Pump tank - normal level - pump, float sensors & controls operating. Distribution box - concrete - all laterals accepting effluent. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 12/09/2020 | Jan 1 1900 10:15AM
12/15/2020 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Puraflo |  | Pump |  |  | None |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 12/15/2020 | Jan 1 1900 7:00AM
08/11/2020 | Alternative | Reportable Incident | 103-STS-92590 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | None | None | Gravity | Distribution Box | Aggregate Trench | None | 450.000000 |  | ["Dispersal System Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | [17 empty] | Replaced damaged / failed distribution box. Conveyance line spliced. Header lines spliced New 8 port concrete distribution box installed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 08/12/2020 | 11:15 AM
04/11/2020 |  | Routine, Scheduled | SD-10-66 | Culpeper County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | JENKINS, TIMOTHY R | 1942001062 | TIMOTHY | JENKINS | 1.000000 |  | Biomicrobics MicroFAST | Sandfilter, Non-recirculating | Pump | Drip | Alternative Discharge | Chlorine |  | ["None"] | ["None"] |  | Musty | Clear | 6.900000 |  | 25.000000 | 2.200000 | [11 empty] | [Comments]: Post Aeration | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/22/2020 | 02:30 AM
04/01/2020 |  | Routine, Scheduled |  | Loudoun County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim |  |  | Biomicrobics MicroFAST | None | Pump | Drip | Drip Tubing | [23 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/12/2020 | 02:21 PM
06/18/2020 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump | Distribution Box |  | None |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  |  | 7.160000 | 3.100000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 06/18/2020 | Jan 1 1900 9:00AM
11/16/2020 | Alternative | Reportable Incident | 151-04-488 | Lancaster | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | Serviced system. Cleaned the filter in the Clearstream and cleaned the in line screen. Changed the diffuser on the Clearstream, red hose assembly for the diffuser, and changed the filter in the aerator. Replaced the pump, pump float, and alarm float. The mute button on the Clearstream panel does not work. Pumped out trash out of the Clearstream tank. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 11/16/2020 | 12:00 PM
03/08/2020 |  | Routine, Scheduled | 113-19-018 | Madison County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | GRAY, RANDY L | 1942001335 | RANDY | GRAY | 2.000000 |  | Biomicrobics MicroFAST | Septic Tank Only | None | Drip | None | None |  | ["None"] | ["None"] |  |  |  | 5.100000 | 6.200000 |  |  |  | 03/08/2020 | Eff | 19.000000 |  |  | 3.560000 | 27.050000 |  | Attached to this report |  | [Pumpout Comments]: No pumping needed at this time. [Comments]: System is operating as designed VENIS File Names: winery sample results 3 20.pdf | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/23/2020 | 08:07 AM
07/22/2020 |  | RoutineScheduled | 109-06-0072 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Taylor's Septic Service, Inc | 1942001028 | Penny | Taylor | 1.000000 | 1500 | septic tank | Microfast | Pump | Gravity | Trenches |  | 450.000000 | ["SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 07/22/2020 | 12:00 AM
06/12/2020 |  | Follow-Up |  | Loudoun | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | New concrete lid was instaled on PT#2 and the broken force main was dug up and fixed. But the PT#2 has ground waster getting in around the force main and will need fixed when its dry. | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 |  | 04/14/2021 | 04:27 PM
08/13/2020 |  | Follow-Up | SD-15-15 | Fauquier | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [9 empty] | 5.000000 | [5 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
09/14/2020 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump | Drip | Elevated Sand Mound | UV Light |  | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  | 6.58 | 6.580000 | 4.900000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 09/14/2020 | Jan 1 1900 9:45AM
06/25/2020 | Alternative | RoutineScheduled | 124-STS-2379 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Rappahannock-Rapidan | Soils, Inc. | 1940001392 | Markham | Smith | 2.000000 | 1500 top seam | Textile: Adantex AX20 Orenco Ax20-2 | Drip irrigation 2 mirc mounds | Pump | Pressure | Drip | Not Applicable |  | [] | ["Control Operation","Attached Growth Medium","Level Sensor Operation","Effluent Screens","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 07/29/2020 | 12:00 AM
08/18/2020 |  | Reportable Incident |  | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  |  |  |  | UV Light |  | ["Disinfection"] | ["Disinfection"] | N/A | [17 empty] | Replaced UV Cord & UV Bulb | This AOSS should now return to normal function after having provided the above state routine maintenance |  | 08/18/2020 | Jan 1 1900 4:30PM
07/23/2020 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintanence requirements | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Gravity | Gravity |  | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | This was a sale inspection on a conventional gravity septic system. The state requires that the septic tank must be pumped out EVERY 5 years and filed with the state and county. There is 1 clean out near the house. The sewer line was camera snaked and was clear. The septic tank has a riser on the outlet side of the tank. The septic tank was pumped out and inspected for cracks or leaks and none were found. The 7 port plastic splitter box was dug up it was 3 feet in the ground. The first 9 port plastic d-box was dug up it was 3 feet in the ground. The header lines were camera snaked but all 5 lines were blocked 3-5 feet out side the d-box. The next 9 port plastic d-box was also 3 feet under the ground. All 5 header lines were camera snaked and were clear. The drain field was probed and was dry. At time of inspection all components were not in working condition. | This AOSS is not functioning as designed or in accordance with the performance/maintanence requirements |  | 04/14/2021 | 04:27 PM
09/11/2020 | Alternative | Routine/Scheduled | 166-06-531 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | Puraflo | None | Pump | None | Aggregate Bed | None | 600.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | Musty | Clear | [15 empty] | Routine Service Septic tank - normal operating level - effluent screen serviced. Pump Tank - normal operating level - pump, float sensors and controls operating PurFlo Modules - minor roots noted - peatmoss turned and raked. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 09/14/2020 | 10:30 AM
11/17/2020 |  | RoutineScheduled | 179-15-0184-SWP | Stafford | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Recirculation Pump" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Control Operation" ,"Attached Growth Medium" ,"Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Level Sensor Operation"] | ["Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Control Operation" ,"Dispersal System Operation" ,"Attached Growth Medium" ,"Auxiliary Filter"] | YES | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
08/01/2020 |  | RoutineScheduled | 133 17 0301 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1000 | Advantex |  | Gravity | Gravity | Trenches |  |  | ["None"] | ["None"] | [18 empty] | 6" of solids in septic tank. Flushed treatment unit spray manifold. Cleaned septic tank filter. Tested floats, pump and alarm. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 10/13/2020 | 07:00 PM
12/15/2020 | Alternative | RoutineScheduled | 159-99-280 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Church View Septic Service Inc. | 1942001302 | Charles | Langford | 9.000000 | 5000 | sandfilter Recirculating | Sandfilter Recirculating | Gravity |  |  | Not Applicable |  | ["Distribution Pump Operation"] | ["Distribution Pump Operation"] | [17 empty] | Pumped Out | 2 broken pipe at Sandfitler recirculating pump and discharge pump repaired immediately. 5 lines in sandfilter bed needs cleaning and repair. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 01/15/2021 | 12:00 AM
05/21/2020 |  | Routine, Scheduled | 175-05-0215 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Delta Environmental Products, DF Series |  |  |  |  | None |  | ["Blower/Compressor/Aerator Operation"] | ["Blower/Compressor/Aerator Operation"] |  | Good | Good | [15 empty] | Spin filter cleaned. Pump Amps 9.85 ETM 39 h Cycles 55265 Water Meter Reading 685900 Septic Sludge 10" Scum 0.50 ATU Sludge 12" Scum 0.50 Pump Sludge 5" Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 05/21/2020 | 04:50 PM
05/23/2020 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Eco Virginia | 1942001235 | William | Poindexter | 1.000000 |  | Clearstream | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 |  | 06/03/2021 | 05:53 AM
03/24/2020 |  | Routine, Scheduled | 179-18-0444-SP | Stafford County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Norweco Singulair ATU | None | Pump | Distribution Box | Aggregate Trench | [22 empty] | [Comments]: 90-Day Inspection | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/06/2020 | 02:46 PM
08/24/2020 |  | RoutineScheduled | 175-03-0343 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | Aquarobic Services | 1934000142 | Michael | Blake |  |  | none | none | Pump | Gravity | Mound | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Tank level close to high level alarm on arrival. Higher water level created greater back pressure and revealed an air leak at the upper hose connection. Re-seated the hose and torqued hose clamp to 60 inch-pounds. Cycled off blower to allow settling, then ran pump manually to drop the water level to normal level. Air pre-filter cleaned. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 07/01/2022 | 10:30 AM
06/04/2020 |  | RoutineScheduled | 033-17-0072-SP | Caroline | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Norweco Singulair ATU | none | Gravity | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"BlowerCompressorAerator Operation"] | ["Effluent Screens" ,"BlowerCompressorAerator Operation"] | YES | [15 empty] | Will be sent separately | Inspected | Owner reported odor concern prior to inspection. Our inspection confirmed the system is working as designed. | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 |  | 04/09/2021 | 03:25 PM
07/10/2020 |  | RoutineScheduled |  | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Soils, Inc. | 1940001392 | Markham | Smith | 2.000000 | 1500 | 2 Effluent Pumps | Zoner (3 zones) | Pump | Pressure | Drip | Not Applicable |  | [] | ["Septic Tank Baffles","SludgeScum Accumulation","Distribution Pump Operation"] | NA | [17 empty] | Septic Tank 1in scum 18in sludge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 07/31/2020 | Jan 1 1900 8:15AM
06/25/2020 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Hoot |  | Pump | Drip | Elevated Sand Mound | UV Light |  | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  |  | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 06/25/2020 | Jan 1 1900 8:30AM
12/15/2020 |  | RoutineScheduled | 124-STS-2379 | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Lord Fairfax | dovel enterprises |  | jerry | dovel | 1.000000 | 1000 |  |  | Pump | Pressure | Trenches |  |  | [] | [] | YES | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12/15/2020 | 12:00 AM
12/02/2020 |  | Initial Visit | 800-STS-13879 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [9 empty] | 2.000000 |  | 1.000000 | [5 empty] | Serviced system. Checked the pump, panel, & floats (ok). Cleaned the filter in the Clearstream and cleaned the UV light bulb. Changed the diffuser in the Clearstream, changed the filter in the aerator, and changed the mesh screen in the spinfilter. Replaced the test button. The timer is set to 4.25 minutes every 2 hours. Took initial BOD & Fecal samples. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12/02/2020 | Jan 1 1900 12:00PM
06/12/2020 |  | Initial Visit | 45143 | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | SEAL’S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | tank only | Puraflo | Pump | Gravity | Trenches |  |  | ["Attached Growth Medium","Septic Tank Baffles","Dispersal System Operation"] | ["Attached Growth Medium","Septic Tank Baffles","Dispersal System Operation"] | [17 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 06/12/2020 | 12:00 AM
09/01/2020 |  | Routine/Scheduled |  | Frederick | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Review | EHD - Lord Fairfax | POWELLS PLUMBING, INC. | 1942001036 | Kurt | Holthaus | 1.000000 | 1000 | Ecoflo |  | Gravity | Distribution Box | Aggregate Trench |  | 450.000000 | ["Attached Growth Medium","Effluent Screens"] | ["Effluent Screens"] | N/A | [17 empty] | Annual Inspection - Media needs to be replaced, pump septic tank to check condition of tank and need septic engineering plans. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. |  | 10/02/2020 | 02:14 PM
10/29/2020 |  | Reportable Incident |  | Virginia Beach | This AOSS should now return to normal function after having provided the above state routine maintenance | Pending Payment | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | EZ Treat Sandfilter | [8 empty] | N/A | [17 empty] | Replaced timer enable float and override float in pump tank. | This AOSS should now return to normal function after having provided the above state routine maintenance |  | 10/29/2020 | Jan 1 1900 8:00AM
03/27/2020 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump | Drip | Elevated Sand Mound | UV Light |  | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  | 2.05 | 7.400000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/27/2020 | Jan 1 1900 4:00PM
03/19/2020 |  | Routine, Scheduled | 099-07-0105-SP | King George County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | None | Pump | Distribution Box | Aggregate Trench |  |  | ["Attached Growth Medium","None","Recirculation Pump"] | ["Attached Growth Medium","None","Recirculation Pump"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/06/2020 | 02:45 PM
07/30/2020 | Alternative | RoutineScheduled | {FIPSCode}-STS-66061 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Wastemaster Inc |  | Timothy | Jenkins | 2.000000 |  | ATU |  | Pump | Pressure | Drip |  |  | [] | [] | [5 empty] | 45.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 09/02/2020 | 02:15 PM
03/21/2020 |  | Routine, Scheduled | 171-18-0111 | Pittsylvania County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Pittsylvania-Danville | WAUGH, IAIN C | 1942001512 | IAIN | WAUGH | 1.000000 | 1000 | Septic Tank Only | EZ Treat Sandfilter | Gravity | None | Alternative Discharge | UV Light |  | ["Effluent Screens"] | ["Effluent Screens","SludgeScum Accumulation"] |  | None |  | 7.980000 | 5.570000 |  |  |  |  | Sample Port | 16.100000 |  | 0.000000 | 13.200000 |  |  | Attached to this report |  | [Pumpout Comments]: Does not Need Pumping [Comments]: Septic 1" Scum 4" Sludge, Recirc tank 1" scum 9" Sludge Blower rebuilt by owner, UV light changed by owner Pump tested good, Alarm good, Blower good. Sprayers have good spray pattern in filter box. Media was cleaned off by owner VENIS File Names: March-2020 HERNDON.pdf | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 03/21/2020 | 05:51 PM
01/29/2020 |  | RoutineScheduled | 07-113-124 | Buchanan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | DEEL, DENNY M | 1942001097 | DENNY | DEEL |  |  | Norweco Singulair ATU | None | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens"] |  | Musty | Clear | [15 empty] | [Comments]: 5 Blue Crystal 10 Bio Max Added | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 02/05/2020 | Jan 1 1900 2:30PM
04/07/2020 |  | RoutineScheduled | 182-04-0217 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Pump | Pressure | Drip | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
04/29/2020 |  | Routine/Scheduled | C 800-17-0245 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | Serviced system. Checked the pump, panel, & floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. The aerator should be raised up. The timer is set to 2 minutes every 2 hours. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 04/29/2020 | Jan 1 1900 12:00PM
10/15/2020 | Alternative | Routine/Scheduled | 166-15-172 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 1.000000 | 1500 | Microfast |  | Gravity | Distribution Box | Aggregate Bed |  |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 10/15/2020 | 05:00 PM
06/30/2020 |  |  | 069080628 | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 2705110225 | Larry | Royston | [9 empty] | ["None"] | ["None"] | YES | [16 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 08/17/2020 | 12:00 AM
08/27/2020 |  | RoutineScheduled | 14-125-091 | Dickenson | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | ELGEN |  | Gravity | Gravity | Mound | Not Applicable | 200.000000 | ["Control Operation","Effluent Screens"] | ["Control Operation","Effluent Screens"] | NO | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
03/27/2020 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump | Drip | Elevated Sand Mound | UV Light |  | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  | 7.46 | 5.250000 | 5.000000 | [13 empty] | Replaced UV Cord & UV Bulb | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/27/2020 | Jan 1 1900 3:00PM
11/02/2020 |  | RoutineScheduled | 179-17-0418-VU | Stafford | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Attached Growth Medium" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Level Sensor Operation"] | ["Attached Growth Medium" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Control Operation"] | YES | [15 empty] | Will be sent separately | Inspected | media is degraded but still ok. sewer line has a break in it. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
12/31/2020 |  | Routine, Scheduled | 175-05-0168 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Delta Environmental Products, DF Series |  |  |  |  | None |  | ["Blower/Compressor/Aerator Operation"] | ["Blower/Compressor/Aerator Operation"] |  | Acceptable | Clear | [15 empty] | System alarms during rain events. Spin filter cleaned. Pump Amps 9.87 ETM 0 Cycles 85793 Water Meter Reading 840640 Septic Sludge 2" Scum 0 ATU Sludge 4" Scum 0 Pump Sludge 0 Scum 0 On 20 mins Off 54 mins | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 12/31/2020 | 09:20 AM
10/27/2020 |  | Initial Visit | 16-174-0080 | Prince George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Crater | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | Orenco Advantex |  | Pump | Distribution Box | Aggregate Trench | None | 600.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | None | Clear | [15 empty] | Initial Visit Primary Septic Tank - normal operating level - effluent screen serviced. Treatment Module - media drapes & spray grid serviced - recirc pump serviced, float sensors and controls operating properly. Pump Tank - normal operating level - discharge pump serviced, float sensors & controls operating properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 10/29/2020 | Jan 1 1900 10:00AM
01/15/2020 |  | Routine, Scheduled | 196.04.314 | Westmoreland County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers | BEASLEY, THOMAS W | 1934000450 | THOMAS | BEASLEY | 2.000000 | 2000 | Puraflo | Septic Tank Only | Pump | Manifold | Aggregate Bed | None |  | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [5 empty] | 20.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/15/2020 | 04:00 PM
11/19/2020 |  | RoutineScheduled | 01-197-137 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | Wise Health Dept |  | Rodney | Neece | 1.000000 |  | Atu Jet |  | Gravity | Gravity | Discharge | Chlorination |  |  |  |  | Musty | Cloudy | 6.000000 | 5.000000 |  | 0.000000 | [12 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 11/18/2020 | 12:00 AM
12/21/2020 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump | Drip | Elevated Sand Mound | UV Light |  | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  | 8 | 8.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 12/21/2020 | Jan 1 1900 11:50AM
05/14/2020 |  | Routine/Scheduled | 06-120-0036A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesterfield | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1500 | Orenco Advantex | None | Pump | Distribution Box | Aggregate Trench | None |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | [17 empty] | Septic Tank has minor root infiltration around the Outlet Pipe, and the Filter is aged; the Floats in the Processing Tank have exceeded their expected life | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 05/26/2020 | Jan 1 1900 5:20PM
06/22/2020 |  |  | SWP-04-266 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | DCM Septic LLC | 1942001350 | Michael | Cook | 2.000000 | 1250 | 1-9 |  | Pump | Gravity | Trenches |  | 600.000000 | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | YES | None | Clear |  |  | 18.000000 | [11 empty] | Inspected | system functioning properly at this time. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 06/22/2020 | 07:50 PM
04/22/2020 |  | Routine/Scheduled | 175-07-0069 | Southampton | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Western Tidewater | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | [11 empty] | N/A | [17 empty] | At the time of maintenance, the service expert reported that all tanks were at normal level. He tested the pump and floats and confirmed that they were functioning properly. When inspecting the distribution box, he found that there was minor root intrusion. The roots were removed during this visit. Upon completion, the service expert confirmed that all components were functioning properly and the system was operational. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/22/2020 | Jan 1 1900 11:48AM
07/06/2020 |  | RoutineScheduled | 175-09-0363 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Ecopod | Pump Tank | Pump | Pressure | Drip | Not Applicable |  | ["SludgeScum Accumulation","BlowerCompressorAerator Operation","Dispersal System Operation"] | ["Dispersal System Operation"] | NA | [17 empty] | Septic-6"sludge 0"scum/ Ecopod-10"sludge/ Pump tank-3"sludge (Both tanks need pump out due to paint which coats the media and drip tubing) Blower air filter cleaned/ System needs new back flush valve . Valve was replaced on 7/8/2020/ Water meter-0146719/ System back to functioning normally. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  |  | 12:00 AM
06/27/2020 |  | RoutineScheduled | SD-08-49 | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Wastemaster Inc |  | Timothy | Jenkins | 2.000000 |  | ATU | Polishing Sand Filter | Gravity | Gravity | Discharge | Chlorination |  | [] | [] | [18 empty] | No Discharge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 03:45 PM
06/12/2020 |  | Routine/Scheduled | 05-160-0370 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Delta Environmental Products, DF Series |  | Pump | Distribution Box |  | None |  | ["None"] | ["Blower/Compressor/Aerator Operation","Sludge/Scum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 06/12/2020 | 11:00 AM
06/03/2020 |  | RoutineScheduled | 099-10-0003-SP | King George | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Distribution Pump Operation" ,"Level Sensor Operation" ,"Attached Growth Medium" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation" ,"Dispersal System Operation" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | ["Level Sensor Operation" ,"Septic Tank Baffles" ,"Attached Growth Medium" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"SludgeScum Accumulation"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced timer float (was stuck on), replaced bad emitter & drip filter. Media is clogged (poor treatment), needs chemical treatment, media cleaned and tanks pumped out. Recommend homeowner remove small saplings around headworks by wood line. Proposal to be sent to homeowner. | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
12/18/2020 |  | Routine/Scheduled | 137-17-022 | Orange | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Old Dominion Onsite, Inc. | 1942001134 | John | Ewing | 1.000000 | 1000 | Orenco Advantex |  | Pump | Distribution Box | Aggregate Trench | None | 150.000000 | ["Control Operation","Dispersal System Operation","Effluent Screens","Recirculation Pump"] | ["Control Operation","Dispersal System Operation","Effluent Screens","Recirculation Pump"] | N/A | [17 empty] | No pump overrides in past 30 days. Effluent filter was cleaned and the manifold was flushed. No problems were observed with drainfield. Recirculation off time (36.1 min)was not changed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12/18/2020 | 10:18 AM
10/04/2020 |  | RoutineScheduled |  | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Rappahannock-Rapidan | Soils, Inc. | 1942001004 | Markham | Smith | 2.000000 | 1500 | Puraflo |  | Pump | Gravity | Trenches | Not Applicable |  | ["None"] | ["Attached Growth Medium","Level Sensor Operation","SludgeScum Accumulation","Septic Tank Baffles"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12/04/2020 | 01:45 PM
09/25/2020 |  | Routine/Scheduled | 136-06-0109 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | Puraflo |  | Pump | None | Aggregate Bed | None | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | Musty | Clear | [15 empty] | Real Estate Inspection / Service Primary Septic Tank - normal operating level - pumped - effluent screen serviced. Pump Tank - normal operating level - knockout in side of tank pushed inwards from tree roots - recommend parging inside / outside to reseal. Pump, float sensors and controls operating properly. PuraFlo Modules - FOUR - Peatmoss Biofilter in good condition - raked / turned | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 10/06/2020 | 08:15 AM
11/25/2020 |  | Routine/Scheduled | 234-13-337 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | Serviced system. Checked the pump, panel, & floats (ok). Cleaned the filter in the Clearstream, cleaned the disc filter, and cleaned the UV light bulb. Changed the diffuser in the Clearstream and changed the filter in the aerator. The timer is set to 8 minutes every 2 hours. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 11/25/2020 | Jan 1 1900 12:00PM
04/16/2020 |  | Routine, Scheduled | 11-120-0245A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesterfield | Madison Environmental LLC |  | Larry | Madison, Jr. |  |  | Norweco Singulair ATU |  | Pump |  |  |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Lab results not reported by Operator, EHS chose "No" in order to allow saving updated entry. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/16/2020 | Jan 1 1900 1:30AM
07/10/2020 |  | Routine/Scheduled | 11-163-0068 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chickahominy | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1500 | Norweco Singulair ATU | None | Pump | Distribution Box | Aggregate Trench | None | 450.000000 |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | Musty | Clear | [15 empty] | Annual service conducted. Trash tank at normal operating level - Aeration / processing tank at normal level - aspirator serviced. Clarifier at normal operating level - effluent screen serviced. Discharge tank at normal operating level - pump, float sensors and control panel operating properly. Distribution box located - timed properly - all laterals accepting effluent. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 07/13/2020 | Jan 1 1900 7:00AM
07/27/2020 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | The dwelling was model home until recently. Had little to no use during time as model. Will not need to be pumped for aprox 3-5 years as it is essentially just now being used as designed. | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 |  | 05/27/2021 | 01:26 PM
02/11/2020 |  | Routine, Scheduled | 179-14-0264-SR | Stafford County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Orenco Advantex | None | Pump | Distribution Box | Aggregate Trench |  |  | ["Attached Growth Medium","Distribution Pump Operation","Effluent Screens","Recirculation Pump"] | ["Attached Growth Medium","Distribution Pump Operation","Effluent Screens","Recirculation Pump"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/02/2020 | 11:52 AM
02/20/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Puraflo |  |  |  |  | None |  | ["Effluent Screens"] | ["Effluent Screens"] | [18 empty] | [Comments]: Septic Sludge 6" Scum 0Pump Sludge 0.50 Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/20/2020 | Jan 1 1900 10:13AM
08/20/2020 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 2705051738 | Joshua | Hott | 1.000000 | 1500 | Septic | Puraflo | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
06/26/2020 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Eco Virginia | 1942001235 | William | Poindexter | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"SludgeScum Accumulation"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected | Septic tank needs to be pumped | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 |  | 06/03/2021 | 05:53 AM
10/12/2020 |  | RoutineScheduled | 18-142-0088 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Lyttle Service Co., LLC dba Stamie E. Lyttle Co | 1942001332 | Benjamin | Chapin | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
07/09/2020 |  | RoutineScheduled |  | Warren | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Pumping will be completed in August | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/26/2021 | 09:04 AM
03/16/2020 |  | Routine, Scheduled | 2016-143-0209 | Henrico County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Henrico |  |  |  |  | 1.000000 | 1250 |  |  | Pump | Manifold | Aggregate Bed | None |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation"] | [18 empty] | [Comments]: Filter cleaned, etm 789.21, ct 545655. Peat checked. System appears to be operating normally. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/16/2020 | 12:44 PM
07/08/2020 | Alternative | Reportable Incident | 128-15-061 | Essex | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers |  |  | joel | pinnix | [9 empty] | ["Auxiliary Filter"] | ["Auxiliary Filter"] | [18 empty] | High water alarm due to clogged ATU filter. Cleaned filter. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  |  | 12:00 AM
11/04/2020 |  | RoutineScheduled | 107-18-0198 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Pump | Pressure | Drip | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 06/02/2021 | 12:00 AM
08/10/2020 |  | Reportable Incident | 15-137-0070 | Goochland | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chickahominy | Old Dominion Onsite, Inc. | 1942001503 | Jason | Hackler | [9 empty] | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation"] | N/A | [17 empty] | 8/3/2020:Lightening struck a tree near the control panel and pump discharge tank. The control Panel was found to be functioning only for the Multiflo aeration. The pump discharge to the dripfield was not functioning. The control panel needs to be replaced. The discharge pump and control/alarm floats may need replacing, too. 8/6/2020 Control Panel Replaced, electrician should be there before the weekend to connect power. 8/10/2020 wired control panels and fixed broken force main. Reset programming for discharge. everthing appears to be operating. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 08/11/2020 | Jan 1 1900 7:30AM
11/18/2020 |  | RoutineScheduled | 98-197-A1 | Wise | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | Wise Health Dept |  | Rodney | Neece | 1.000000 |  | Atu jet |  | Gravity | Gravity | Discharge | Chlorination |  |  |  |  | Musty | Clear | 6.600000 | 7.000000 |  | 0.000000 | No tablets | [11 empty] | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 11/18/2020 | 12:00 AM
10/06/2020 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump | Drip | Elevated Sand Mound | UV Light |  | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  | 5.1 | 7.880000 | 4.400000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 10/06/2020 | Jan 1 1900 1:45PM
09/10/2020 |  |  | 2015-143-0010 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Ecopod |  | Gravity | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 09/25/2020 | 12:00 AM
10/20/2020 |  | Reportable Incident |  | Isle Of Wight | This AOSS should now return to normal function after having provided the above state routine maintenance | Pending Payment | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream | [6 empty] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation"] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation"] | N/A | [17 empty] | Replaced pump | This AOSS should now return to normal function after having provided the above state routine maintenance |  | 10/20/2020 | Jan 1 1900 5:30PM
11/18/2020 |  | RoutineScheduled | SD-13-210 | Culpeper | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | EcoPod | none | Pump | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"SludgeScum Accumulation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | We replaced the defective blower. We recommend pumping the pump tank due to sludge accumulation. | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 |  | 04/09/2021 | 03:25 PM
07/28/2020 |  | Pump-Out Only |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | POWELLS PLUMBING, INC. | 1942001036 | Kurt | Holthaus |  |  | Puraflo | [6 empty] | ["Sludge/Scum Accumulation"] | ["Sludge/Scum Accumulation"] | N/A | [17 empty] | Pumped pump chamber and part of septic tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 10/08/2020 | 02:32 PM
01/02/2020 |  | Routine, Scheduled |  | Albemarle County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Blue Ridge | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | None | Pump | Drip | Drip Tubing |  |  | ["Attached Growth Medium","Auxiliary Filter","Recirculation Pump"] | ["Attached Growth Medium","Auxiliary Filter","Recirculation Pump"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/04/2020 | 07:46 AM
06/08/2020 |  | Routine/Scheduled | 2005-143-0060 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Henrico | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1500 | Orenco Advantex | None | Pump | Distribution Box | Aggregate Trench | None |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | [17 empty] | The Recirculation Pump & Floats have met/exceeded their life expectancy; the support Struts on the Advantex Media Unit Lid have failed, and the Media Sheets have exceeded their life expectancy; the Discharge Pump has exceeded its life expectancy; the Control Panel has exceeded its life expectancy | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 06/16/2020 | 10:44 AM
01/22/2020 |  | Routine, Scheduled | SWP-05-270 | King George County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Ware, Michele P | 1942001165 | Michele | Ware |  |  | Septic Tank Only | Septic Tank Only | None | None | None | None |  |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/28/2020 | 05:25 PM
04/10/2020 |  | RoutineScheduled | 139-03-0041 | Page | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Lord Fairfax | Onsite Wastewater Services - May Supply | 1942001022 | Sara | Tusing | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/28/2021 | 05:41 AM
11/03/2020 |  | RoutineScheduled | 03-192-032c | Tazewell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Trenches | Not Applicable | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","Effluent Screens"] | ["BlowerCompressorAerator Operation","Control Operation","Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
02/24/2020 |  | Routine, Scheduled | 181-13-0075 | Rockbridge County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Central Shenandoah |  |  |  |  | 1.000000 | 1500 |  | Biomicrobics MicroFAST | Gravity | None | Aggregate Trench | None |  | ["Attached Growth Medium","None"] | ["None"] | [18 empty] | [Comments]: Filter checked and cleaned. Control panel operating properly. No apparent leaks in system or drain field area. Lids properly secured. Media overgrowth noted. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/29/2020 | 30-12-1899 07:37 PM
08/06/2020 |  |  | 05-113-031 | Buchanan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 08/06/2020 |  | 10.200000 |  |  | 1.500000 |  |  | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 08/06/2020 | 12:00 AM
09/30/2020 |  | Routine/Scheduled | 07-163-0126 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chickahominy | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. |  |  | Bionest |  | Gravity | Distribution Box |  |  |  | ["Attached Growth Medium","Blower/Compressor/Aerator Operation","Control Operation","Effluent Screens","Recirculation Pump","Septic Tank Baffles","Sludge/Scum Accumulation"] | ["Attached Growth Medium","Blower/Compressor/Aerator Operation","Control Operation","Effluent Screens","Recirculation Pump","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 09/30/2020 | Jan 1 1900 4:00AM
03/30/2020 |  | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Greenway Engineering | 1942001008 | Jeremy | Ferguson | 1.000000 | 1520 | Microfast | none | Pump | Pressure | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Level Sensor Operation","SludgeScum Accumulation"] | NA | [7 empty] | 03/30/2020 | Sample Tap | 18.700000 | [5 empty] | Attached to this report |  | Would not allow me to attach sample results. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 07/21/2020 | 11:00 AM
07/22/2020 |  |  | {FIPSCode}-STS-1948 | Dickenson | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 07/22/2020 |  | 16.900000 |  |  | 1.300000 |  |  | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 07/22/2020 | 12:00 AM
10/01/2020 | Alternative |  | 166-10-222 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Church View Septic Service Inc. | 1942001302 | Charles | Langford | 1.000000 | 1000 | Microfast | [6 empty] | ["Effluent Screens"] | ["Effluent Screens"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
06/23/2020 |  | Follow-Up | SP-05-445 | Spotsylvania | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Replace internal splice box with exterior Orenco box. Replace pod struts. Replace alarm float. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
11/20/2020 |  | RoutineScheduled | SP-05-212 | Spotsylvania | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  | ["Dispersal System Operation" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Attached Growth Medium" ,"BlowerCompressorAerator Operation"] | ["Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Attached Growth Medium" ,"BlowerCompressorAerator Operation" ,"Dispersal System Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
07/29/2020 | Alternative | Routine/Scheduled | 151-15-0100 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001063 | K.R. Trapper | Davis | 2.000000 | 2000 | Biomicrobics MicroFAST | None | Pump | Distribution Box | Aggregate Trench | None | 600.000000 |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | Musty | Clear | [15 empty] | Routine service conducted. Primary septic tank - Residence - normal operating level Pump tank - Residence - normal operating level - pump, float sensors and controls operating properly. Secondary Septic Tank - Garage - normal operating level BioMicrobics - Normal operating level - blower serviced. Pump Tank - normal operating level - pump, float sensors and controls operating properly. Remote absorption fields - heavily overgrown - not inspected. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 07/30/2020 | 01:15 PM
07/07/2020 |  | RoutineScheduled | 179-06-0396-SWP | Stafford | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Attached Growth Medium" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | ["Effluent Screens" ,"Level Sensor Operation" ,"Control Operation" ,"Distribution Pump Operation" ,"Attached Growth Medium" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | YES | [15 empty] | Will be sent separately | Inspected | Roots on inlet wedge lid on septic tank and pump tank (to DF). Pump tank to drainfield was in H/L (up in riser). Bumped up the floats, started working. Filter alarm is stuck in on position. Alarm bulb is burnt out (this has always been problematic, owner does not want to repair at this time.) | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
03/02/2020 |  | Routine, Scheduled | 234-18-150 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesapeake | R & K Septic, Inc. |  | Robbie | Van Holten |  |  | Clearstream ATU |  | Pump | Distribution Box | Aggregate Bed | None |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] |  |  |  | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/02/2020 | Jan 1 1900 9:00AM
09/21/2020 |  | Pump-Out Only |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | POWELLS PLUMBING, INC. | 1942001036 | Kurt | Holthaus |  |  | Puraflo | [6 empty] | ["Sludge/Scum Accumulation"] | ["Sludge/Scum Accumulation"] | N/A | [17 empty] | Pumped septic tank and pump chamber. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 10/08/2020 | 12:19 PM
08/06/2020 |  | RoutineScheduled |  | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 2705051738 | Joshua | Hott |  |  | Septic | Puraflo | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
04/16/2020 | Alternative | Routine/Scheduled | 157-12-0123 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | Serviced system. Checked the pump, panel, & floats (ok). Cleaned the filter in the Clearstream and cleaned the filter in the aerator. Changed the diffuser in the Clearstream and changed the mesh screen in the spinfilter. The spinfilter screen was stopped up and the pump screen was stopped up. The UV has been fixed. Spinfilter return line was below the water level in the trash tank - fixed. The septic tank needs pumping (water level is low). The timer is set to 6 minutes every 2 hours. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 04/16/2020 | 12:00 PM
05/20/2020 |  | RoutineScheduled |  | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Microfast |  |  |  | Drip |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
03/16/2020 |  | Routine, Scheduled | 107-16-0186 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Cubbage, Harrison Lee, II | 1942001021 | Harrison | Cubbage | 1.000000 | 1500 | Septic Tank Only | Biomicrobics MicroFAST | Gravity | Distribution Box | Aggregate Trench | None |  | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] |  | Musty | Clear | [5 empty] | 03/16/2020 | Fast Chamber | 7.000000 | [5 empty] | Attached to this report |  | [Lab Comments]: Lab Results Normal [Comments]: Sludge/Scum Accumulations: Comp.1-14"/2" Comp.2-14"/0" VENIS File Names: 535 Barren Ridge 3-16-20.pdf | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 04/06/2020 | 01:17 PM
07/06/2020 |  | Routine, Scheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Biomicrobics MicroFAST |  |  |  |  | None |  | ["Blower/Compressor/Aerator Operation"] | ["Blower/Compressor/Aerator Operation"] |  | Good | Brown | [15 empty] | Pump 1 Amps 9.92 ETM 191.5 Cycles 38845 Pump 2 Amps 9.36 ETM 183.6 Cycles 39400 Water Meter Reading 1999810 Septic Sludge 13" Scum 4" Pump Sludge 2" Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 07/06/2020 | Jan 1 1900 10:06AM
01/14/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Fairfax | BLEVINS, JOEL R, SR | 1934000415 | JOEL | BLEVINS |  |  | Microfast | Septic Tank Only | None | None | None | None |  | ["None"] | ["None"] | [18 empty] | [Comments]: Cleaned the air filter. The compressor is strong and the ditches are dry. There is 8" of sludge in the bottom of the tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/14/2020 | Jan 1 1900 3:22PM
11/06/2020 | Alternative | RoutineScheduled | 10-167-038 | Nottoway | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Piedmont | Bryant Farms | 1965005795 | Raymond | BRYANT JR. |  |  |  |  | Gravity | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | None | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 11/06/2020 | Dec 30 1899 10:00AM
05/06/2020 |  | RoutineScheduled |  | Fairfax | This AOSS is functioning as designed and in accord | Approved | EHD - Fairfax | J&G Septic service | 1942001280 | James | Kleindl | 2.000000 | 1500 |  |  | Pump | Gravity | Trench |  |  | [] | [] | [19 empty] | This AOSS is functioning as designed and in accord |  | 05/11/2020 | 12:00 AM
05/11/2020 |  | Routine/Scheduled |  | Frederick | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Review | EHD - Lord Fairfax | POWELLS PLUMBING, INC. | 1942001036 | Kurt | Holthaus | 1.000000 | 1000 | Puraflo |  | Pump | Manifold | Aggregate Trench |  | 450.000000 | ["Control Operation","Effluent Screens"] | ["Effluent Screens"] | N/A | [17 empty] | Annual Inspection - Replace wire from house to pump chamber. Serviced effluent screen(s). | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. |  | 05/20/2020 | 12:51 PM
06/10/2020 |  | Routine/Scheduled | 03-120-0371A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesterfield | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1500 | Orenco Advantex | None | Pump | Distribution Box | Aggregate Bed | None |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | [17 empty] | In the Processing Tank, the Recirculation Pump and Floats have exceeded their expected life; the Advantex Media Sheets have exceeded their expected life, and the support Struts on the Lid of the Unit have failed; the Discharge Pump and Floats (which are not properly secured) have exceeded their expected life; the Control Panel has exceeded its expected life; | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 06/16/2020 | Jan 1 1900 3:37PM
01/17/2020 | Alternative | RoutineScheduled | 171-16-007 | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Combs Wastewater Management LLC | 1942001353 | Amy | Combs | 2.000000 | 1060 |  |  | Pump | Gravity | Drip | Not Applicable | 450.000000 | [] | ["Auxiliary Filter","Control Operation","BlowerCompressorAerator Operation","Distribution Pump Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12/28/2020 | 12:00 AM
03/19/2020 |  | Routine, Scheduled |  | Loudoun County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | None | Gravity | Distribution Box | Aggregate Trench | [22 empty] | [Comments]: A large tree has fallen below the drainfield. Only the top branches are near the lower line. It does not appear to have any impact on the drainfield. Recommend trimming limbs back. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/19/2020 | 08:35 AM
01/31/2020 |  | Routine, Scheduled | 033-17-0249-SP | Caroline County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | None | None | Pump |  |  |  |  | ["Attached Growth Medium","Auxiliary Filter","Effluent Screens","None"] | ["Attached Growth Medium","Auxiliary Filter","Effluent Screens","None"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/02/2020 | 11:52 AM
06/15/2020 |  | Initial Visit | 175-04-0044 | Southampton | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Western Tidewater | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | Delta Environmental Products, DF Series |  | Gravity | Distribution Box | Aggregate Trench | None | 450.000000 | ["Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | Musty | Clear | [15 empty] | Initial visit - full service conducted Septic tank in normal operating level - concrete inlet baffle ATU functioning - shows heavier than normal sludge and solids - recommending pumpout and refill during next service. Compressor operates on a "Piggy Back" set up, vs. being wired through proper controls. Distribution box not located - FOIA filed for permit documents. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 06/18/2020 | Jan 1 1900 7:30AM
02/12/2020 |  | Routine, Scheduled | 033-18-0060-SP | Caroline County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Ware, Michele P | 1942001165 | Michele | Ware |  |  | Septic Tank Only | Septic Tank Only | None | None | None | None |  |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/13/2020 | 07:58 AM
06/02/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/27/2021 | 01:26 PM
06/09/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | SES MidAtlantic LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity |  | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/15/2021 | 09:00 AM
11/02/2020 |  | RoutineScheduled | 175-10-0023 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Wastemaster Inc |  | Timothy | Jenkins | 2.000000 |  | Advantex |  |  | Pressure | Drip |  |  | ["SludgeScum Accumulation"] | [] | [18 empty] | In for service and inspection. Cleaned and tested Advantex System. All operating normally. Recommend having all tanks pumped out due to high level of solids. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 11/16/2020 | 11:35 AM
12/10/2020 |  | RoutineScheduled | 069051305 | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | None | Clear | 7.500000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12/17/2020 | 02:50 PM
03/13/2020 |  | Routine, Scheduled |  | Loudoun County | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Paid | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | None | Pump | Distribution Box | Aggregate Trench | [22 empty] | [Comments]: both pump tanks need pumped out | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 04/12/2020 | 02:21 PM
07/25/2020 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump | Drip | Elevated Sand Mound | UV Light |  | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  |  | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 07/25/2020 | Jan 1 1900 8:00AM
05/14/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/14/2021 | 04:27 PM
08/05/2020 |  | RoutineScheduled | SD-08-415 | Fauquier | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Distribution Pump Operation" ,"Control Operation" ,"Auxiliary Filter" ,"SludgeScum Accumulation"] | ["Control Operation" ,"Distribution Pump Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | Drip tank still in high level, control panel indicating extremely high override cycles in recirc tank which usually occurs during heavy inflow. Heavy rain recently, but no evidence of infiltration was found. Drip rate was slow due to crushed and dirty spin filter (replaced), and clogged drip pump intake. Pump is sitting in 10" of sludge, so pump tank needs pumped out asap. Owner to make arrangements. Replaced broken vent cap for Advantex pod. In the past 30 days, the drip pump has run an average of 8 dose cycles at 6.6 minutes per cycle. The maximum is 12 cycles at 8.0 minutes. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
02/17/2020 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 | Approved | EHD - Fairfax | Ace Contracting Services Inc | 1942001120 | Lawrence | Fellenz Jr. | 1.000000 |  | Puraflo | none | Pump | Gravity |  | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 |  | 06/29/2021 | Jan 1 1900 10:39PM
03/12/2020 |  | Routine, Scheduled | 179-14-0162-SWP | Stafford County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Orenco Advantex | None | Pump | Distribution Box | Aggregate Trench |  |  | ["Attached Growth Medium","Effluent Screens","None","Recirculation Pump"] | ["Attached Growth Medium","Effluent Screens","None","Recirculation Pump"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/06/2020 | 02:45 PM
03/30/2020 |  | Routine, Scheduled |  | Prince William County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Delta Environmental Products, DF Series | Sandfilter, Recirculating |  |  |  | Chlorine |  | ["BlowerCompressorAerator Operation","Disinfection"] | ["BlowerCompressorAerator Operation","Disinfection"] |  | Good | [6 empty] | 03/30/2020 |  | 5.000000 |  | 1.000000 | 2.000000 |  |  |  |  | [Comments]: Septic Sludge 6" Scum 1"ATU Sludge 4" Scum 2"Pump Sludge 2" Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/30/2020 | 01:16 PM
01/09/2020 |  | Reportable Incident | 234-17-0051 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesapeake | R & K Septic, Inc. |  | Craig | Van Holten | [9 empty] | ["Control Operation","Distribution Pump Operation"] | ["Control Operation","Distribution Pump Operation"] | [18 empty] | [Comments]: Replaced pump | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/09/2020 | Jan 1 1900 4:30PM
10/22/2020 |  | RoutineScheduled | 179-08-0197-SR | Stafford | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Level Sensor Operation" ,"Recirculation Pump"] | ["Control Operation" ,"Level Sensor Operation" ,"Recirculation Pump"] | NA | [15 empty] | Will be sent separately | Inspected | Routine inspection for new owner. Home has been vacant approximately 2 months. Grass in drainfield needs cut, old dead tree needs removed, and saplings/ brush at end of field need removed. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
08/07/2020 |  | RoutineScheduled | 15-113-096 | Buchanan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","Effluent Screens","Disinfection"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
07/06/2020 |  | RoutineScheduled | 069180495 | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 2705110225 | Larry | Royston | [9 empty] | ["None"] | ["None"] | YES |  |  | 8.000000 |  |  |  |  | 07/06/2020 | [8 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 09/02/2020 | 12:00 AM
03/18/2020 |  | Routine, Scheduled | 2017-143-0177 | Henrico County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Henrico |  |  |  |  | 1.000000 | 1000 |  | None | Pump | Drip | Drip Tubing | None | 450.000000 | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | [Comments]: System type is PuraSYS SBR - not on the pull down list to be selected Sludge = 3" Scum = 1 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/21/2020 | 11:00 AM
08/31/2020 |  | RoutineScheduled | 179-14-0212-SP | Stafford | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation" ,"Control Operation" ,"SludgeScum Accumulation"] | ["Control Operation" ,"Distribution Pump Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Measured excessive sludge in treatment half of septic tank (Microfast). Owner called and set up appointment for pumping with local pumper. Roots in d-box were causing unequal distribution. Removed as many as best possible, then added Root-Ex to kill remaining roots. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
11/17/2020 |  | Follow-Up | 085-STS-34484 | Hanover | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw | [9 empty] | ["Attached Growth Medium"] | ["Attached Growth Medium"] | [18 empty] | Changed peat moss | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 01/04/2021 | 12:00 AM
11/06/2020 |  | RoutineScheduled | 132-06-0263 | Fluvanna | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Carrington Pump & Irrigation | 1942001121 | John | Carrington | 2.000000 |  | Norweco |  | Pump | Pressure | Drip |  |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
06/16/2020 |  | RoutineScheduled | SD-09-311 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Soils, Inc. | 1940001392 | Markham | Smith | 2.000000 | 1500 | Peat pilter Manuacture puroFlo (6 Pods) |  | Pump | Gravity | Pad |  | 62.500000 | [] | ["Attached Growth Medium","Septic Tank Baffles","Dispersal System Operation","Distribution Pump Operation"] | YES | [17 empty] | The System is running at a proper rate Gpd 62.5 Septic compartment is at 6in sludge Pump chamber had 4in sludge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
06/19/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/14/2021 | 04:27 PM
09/19/2020 |  | Reportable Incident | 17-137-0065 | Goochland | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Chickahominy | Miller's Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | Hydro-Action ATU | None | Pump | Drip | Drip Tubing | UV Light | 450.000000 |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | Musty | Clear | [15 empty] | Alarm Event Septic tank & ATU in normal level Discharge tank in high level - serviced drip screen - lowermost drip field has surfacing present. NOTE - Lowermost zone of drip field has been surfacing since installation. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 10/02/2020 | Jan 1 1900 7:30AM
09/16/2020 |  | RoutineScheduled |  | Shenandoah | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/26/2021 | 09:04 AM
08/03/2020 |  | RoutineScheduled | 069190053 | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Greenway Engineering | 1942001008 | Jeremy | Ferguson | 1.000000 | 1500 | Microfast | none | Gravity | Gravity | Discharge | UV |  | ["BlowerCompressorAerator Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","SludgeScum Accumulation"] | NA | [7 empty] | 08/03/2020 | Sample Tap | 5.660000 |  | 9.800000 |  |  |  | Will be sent separately |  | Will not let me add lab report. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 08/13/2020 | 03:00 PM
03/04/2020 |  | Routine, Scheduled |  | Mathews County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Three Rivers | Farmer’s Septic Service, Inc. |  | Ross | Cole | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | [Comments]: Serviced system. Checked the pump, panel, & floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. The timer is set to 5 minutes every 2 hours. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/04/2020 | 12:00 PM
04/16/2020 | Alternative | Routine/Scheduled | 150-13-0002 | King William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1250 | Clearstream ATU | None | Pump | Drip | Drip Tubing | None |  |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | Alarm Float in the Processing Tank has met/exceeded expected life; the Floats in the Pump Tank have met/exceeded expected life, existing Floats are not properly secured in the Pump Tank, and the Vortex Filter was found damaged | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/17/2020 | 04:23 PM
06/19/2020 |  | Reportable Incident | C10-180-0013 | Roanoke | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Alleghany-Roanoke | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Advantex AX20 |  | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | NA | [16 empty] | Inspected | Recirculation Pump had shut down and discharge pump had burned up from rain water infiltration into system during rain events. Replaced pump, dried out junction boxes. Reccomended landscaping of french drain to move rain from area and contacted electrician for replacing the junction boxes to improve water resistance(the junction boxes are internal to the tank and are below grade) System returned to normal operation after new pump installed. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 06/28/2020 | Jan 1 1900 12:30PM
01/06/2020 |  | Routine, Scheduled |  | Northumberland County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Three Rivers | PINNIX, JOEL S | 1934000193 | JOEL | PINNIX |  |  | Septic Tank Only | Septic Tank Only | None | None | None | None | [22 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/13/2020 | 03:38 PM
08/05/2020 |  | RoutineScheduled | {FIPSCode}-STS-4735 | Frederick | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | [7 empty] | 08/05/2020 |  | 28.000000 | [5 empty] | Will be sent separately | Inspected | Lab Sample Normal Repaired air supply line | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance |  | 04/26/2021 | 09:04 AM
04/22/2020 | Alternative | RoutineScheduled | 151-16-0007 | Lancaster | This AOSS is functioning as designed and in accord | Approved | EHD - Three Rivers | [13 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accord |  |  | 12:00 AM
11/13/2020 |  | RoutineScheduled | 107-97-0178 (LEGACY ALT. SYSTEM) | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | Musty |  | 7.690000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12/09/2020 | 02:50 PM
08/28/2020 |  | Reportable Incident | 234-16-127 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | Owner called due to the alarm going off. Serviced system. Checked the pump, panel, & floats (ok). Cleaned the filter in the Clearstream and cleaned the UV light bulb. Installed a re-build kit on the aerator. Changed the diffuser in the Clearstream, changed the filter in the aerator, and changed the mesh screen in the spinfilter. There is visible wetness on the drainfield - most likely rain - need to keep an eye on it. The timer is set to 5 minutes every 2 hours. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 08/28/2020 | Jan 1 1900 12:00PM
05/13/2020 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 | Pending Payment | EHD - Loudoun | WasteMaster, Inc. | 1942001062 | Tim | Jenkins | 1.000000 |  | Delta Environmental Products, UC Series | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Peat is beginning to deteriorate | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 |  | 06/21/2021 | 10:37 AM
12/02/2020 |  | Routine/Scheduled | 03-120-0400A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesterfield | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1250 | Orenco Advantex |  | Pump | Distribution Box | Aggregate Trench | None | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | None | Clear | [15 empty] | Routine service Primary Septic Tank - normal operating level. Processing Tank - normal level - RSV, recirc pump & effluent screen serviced. Treatment Module - media drapes & spray grid serviced. Pump Tank - normal operating level - pump, float sensors & controls operating. Distribution box - intact - all laterals accepting effluent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 12/03/2020 | Jan 1 1900 7:30AM
04/18/2020 |  | Routine, Scheduled | 047-19-138 | Culpeper County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | JENKINS, TIMOTHY R | 1942001062 | TIMOTHY | JENKINS | 1.000000 |  | Sandfilter, Recirculating | None | Pump | Drip | Alternative Discharge | Chlorine |  | ["SludgeScum Accumulation"] | ["None"] |  | Musty | Clear | 6.900000 |  |  | 1.500000 | [11 empty] | [Comments]: System Requires Pumping | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/24/2020 | 02:44 PM
11/20/2020 |  | RoutineScheduled | 04-197-A17 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | Wise Health Dept |  | Rodney | Neece | 1.000000 |  | ATU JET |  | Gravity | Gravity | Discharge | Chlorination |  |  |  |  | None | Clear | 6.200000 | 5.000000 |  | 0.000000 | good | [11 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 11/20/2020 | 12:00 AM
06/29/2020 |  | RoutineScheduled | 139-07-176 | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | [6 empty] | tank only | PuraFlo | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","Septic Tank Baffles"] | ["Attached Growth Medium","Septic Tank Baffles"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 06/29/2020 | 12:00 AM
03/18/2020 |  | Follow-Up |  | Fairfax County | This AOSS should now return to normal function after having provided the above stated routine maintenance. | Paid | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green | [9 empty] | ["Distribution Pump Operation"] | ["Distribution Pump Operation"] | [18 empty] | [Comments]: Installed new Z 140 effluent pump & check valve. | This AOSS should now return to normal function after having provided the above stated routine maintenance. |  | 03/18/2020 | Jan 1 1900 1:30PM
05/22/2020 |  | RoutineScheduled | VAG408462 | Augusta | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Central Shenandoah | Onsite Wastewater Services - May Supply | 1942001022 | Sara | Tusing | 1.000000 |  | none | none | Gravity | Gravity | Pad | Chlorination |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/28/2021 | 05:41 AM
12/10/2020 |  | Follow-Up | 00-197-A3 | Wise | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | Wise County Health Dept |  | Rodney | Neece | 1.000000 |  | ATU |  | Gravity | Gravity | Discharge | Chlorination | [10 empty] | Tablets not installed in chambers | [11 empty] | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12/10/2020 | 12:00 AM
07/06/2020 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Eco Virginia | 1942001235 | William | Poindexter | 1.000000 |  | EcoPod | none | Gravity | Gravity | Trenches | UV |  | ["BlowerCompressorAerator Operation" ,"Disinfection"] | ["BlowerCompressorAerator Operation" ,"Disinfection"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced UV bulb | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 |  | 06/03/2021 | 05:53 AM
04/16/2020 |  | Routine, Scheduled | 14-120-0078AR | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesterfield | Madison Environmental LLC |  | Larry | Madison, Jr. |  |  | Norweco Singulair ATU |  | Gravity |  |  |  |  | ["BlowerCompressorAerator Operation","Control Operation","Effluent Screens","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Effluent Screens","SludgeScum Accumulation"] | [18 empty] | Lab results not reported by Operator, EHS chose "No" in order to allow saving updated entry. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/16/2020 | Jan 1 1900 3:00AM
04/20/2020 |  | RoutineScheduled | 06-192-065 | Tazewell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. |  | Denny | Deel |  |  | WHITEWATER |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","Disinfection"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
03/12/2020 |  | Routine, Scheduled | 14-125-075 | Dickenson County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Cumberland Plateau | DEEL, DENNY M | 1942001097 | DENNY | DEEL |  |  | Norweco Singulair ATU | None | Gravity | None | Alternative Discharge | Chlorine | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens"] |  | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/08/2020 | Jan 1 1900 1:36PM
07/15/2020 |  | RoutineScheduled | 108-05-0016 | Bath | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Central Shenandoah | Onsite Wastewater Services - May Supply | 1942001022 | Sara | Tusing | 1.000000 |  | Bio Barrier | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | INSPECTION BY DS | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/28/2021 | 05:41 AM
11/30/2020 |  | RoutineScheduled | 182-09-0046 | Rockingham | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Central Shenandoah | Onsite Wastewater Services - May Supply | 1942001627 | Drew | Shull | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | inspection by Ds | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/28/2021 | 05:41 AM
11/03/2020 |  | RoutineScheduled |  | Rockingham | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Ecoflo | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter"] | ["Control Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | Contact us if would like us to upgrade timer that may prevent future alarms | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/26/2021 | 09:04 AM
11/12/2020 |  | RoutineScheduled | {FIPSCode}-STS-62163 | Spotsylvania | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Dispersal System Operation" ,"Level Sensor Operation"] | ["Control Operation" ,"Level Sensor Operation"] | NA | [15 empty] | Will be sent separately | Inspected | On site for annual inspection and to investigate high level alarm. Very heavy rain last night. Groundwater infiltration observed at both ribcore risers on septic tank, buried inlet wedge lid on pump tank, and at concrete riser joint outlet end of pump tank. Both check valves for drip field are stuck open and need replaced. Will send repair proposal to owner. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
06/01/2020 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Eco Virginia | 1942001235 | William | Poindexter | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"SludgeScum Accumulation"] | ["Effluent Screens" ,"SludgeScum Accumulation"] | YES | [15 empty] | Will be sent separately | Inspected | pumped septic tank | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 |  | 06/03/2021 | 05:53 AM
10/07/2020 |  | Routine, Scheduled | 175-10-0121 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | EcoPod |  |  |  |  | None |  | ["Blower/Compressor/Aerator Operation"] | ["Blower/Compressor/Aerator Operation"] |  | Acceptable | Clear | [15 empty] | Pump Amps 10.97 ETM 13022 Cycles 6298 Septic Sludge 12" Scum 1" ATU Sludge 7" Scum 0 Pump Sludge 4" Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 10/07/2020 | 01:40 PM
11/24/2020 |  | RoutineScheduled | 154-06-0241 | Louisa | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Blue Ridge | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Ecoflo | none | Gravity | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Effluent Screens" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | ["Attached Growth Medium" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected | D-6 leaks a little. Roof vent on pod is cracked; no real issue. Raked peat, now OK. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
05/21/2020 |  | RoutineScheduled | 88-197-128 | Wise | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. |  | Denny | Deel | [8 empty] | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","Disinfection"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
03/02/2020 |  | Routine, Scheduled | {FIPSCode}-STS-3530 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesapeake | R & K Septic, Inc. |  | Robbie | Van Holten |  |  | Clearstream ATU |  | Pump | Distribution Box |  | None |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] |  |  |  | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/02/2020 | Jan 1 1900 11:00AM
10/20/2020 |  | RoutineScheduled | 179-07-0027-SR | Stafford | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Recirculation Pump"] | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/09/2021 | 03:25 PM
07/23/2020 |  | RoutineScheduled | SD-87-437 | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Wastemaster Inc |  | Timothy | Jenkins | 2.000000 |  | ATU |  | Pump | Gravity | Discharge | Chlorination |  | [] | [] | [18 empty] | No Discharge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 10:35 AM
08/19/2020 |  | Follow-Up | SD-05-416 | Culpeper | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity |  | Chlorination |  |  |  | NA | [9 empty] | 2.000000 |  | 2.000000 | 2.100000 |  |  | Will be sent separately | Inspected | DO 6.18 Effluent sampling only | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/09/2021 | 03:25 PM
03/04/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | Delta Environmental Products, DF Series | none | Gravity | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/14/2021 | 04:27 PM
11/20/2020 |  | RoutineScheduled | 107-16-0062 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Ken-Dig-It Services | 1942001128 | Kenneth | Ayres | 1.000000 | 1500 | Microfast |  | Pump | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NO | [17 empty] | The system is close to needing pumping due to wash over into treatment side of the tank. The alarm buzzer was working but was very faint. The return pipe does not have a pressure gauge on it to regulate the pressure on the drip field. It only has a ball valve so its just guess work. The spin filter was cleaned and the controls were operating as designed. There were no visible leaks in the drip field. The lids were secured. The pumping will be performed in the near future. I will also install a pressure gauge and a new alarm buzzer at the time of pumping. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12/28/2020 | 10:28 PM
09/21/2020 |  | Follow-Up |  | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | Wastemaster Inc |  | Timothy | Jenkins | 2.000000 |  | ATU |  |  |  | Discharge |  |  | [] | [] | [18 empty] | Replaced all 30 filters in multiflo ATY. Refilled tank with hose. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 10/08/2020 | Jan 1 1900 1:05PM
10/13/2020 |  | Follow-Up | SD-11-312 | Fauquier | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Distribution Pump Operation"] | ["Distribution Pump Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced both zone check valves. Ran test cycles to verify new check valves working correctly. Attempted to measure drip rate but could not due to limitations of design. Effluent level in discharge basin was above inlet pipe so that as the drip pump was running and dropping the level, more effluent was flowing into the pump basin from the Advantex RT pod. This made using a tape measure and stopwatch to measure drip rate impossible. System needs a flow meter and owner again declined the installation of one. Both mounds are saturated. Will revisit site in about 30 days to see if any improvement. | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
07/23/2020 |  | RoutineScheduled | SD-10-66 | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Wastemaster Inc |  | Timothy | Jenkins | 2.000000 |  | ATU | Polishing Sand Filter | Pump | Gravity | Discharge | Chlorination |  | [] | [] |  | Musty | Clear | 7.100000 |  |  | 2.200000 | [12 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 07/23/2020 | 03:20 PM
07/03/2020 |  | Reportable Incident |  | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [9 empty] | ["Blower/Compressor/Aerator Operation","Control Operation"] | ["Blower/Compressor/Aerator Operation","Control Operation"] | N/A | [17 empty] | Replaced aerator | This AOSS should now return to normal function after having provided the above state routine maintenance |  | 07/03/2020 | Jan 1 1900 1:30PM
02/19/2020 |  | Routine, Scheduled |  | Fluvanna County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Blue Ridge | CLARK, MICHAEL J | 1934000023 | MICHAEL | CLARK |  |  | Septic Tank Only | Septic Tank Only | None | None | None | None |  |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/24/2020 | 05:00 AM
08/07/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Recommend pumping | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/27/2021 | 01:26 PM
07/02/2020 |  | Routine/Scheduled | 06-120-0770A | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance | Approved | EHD - Chesterfield | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1500 | Orenco Advantex |  | Pump | Drip | Drip Tubing | None | 600.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | Musty | Clear | [15 empty] | System alarming high level - found drip screens clogged - serviced Allowed system to pumpout of high level condition on own accord. Noted what appears to be inflow from residence which may indicate toilet leak causing high level / excessive flows. | This AOSS should now return to normal function after having provided the above state routine maintenance |  | 07/07/2020 | Jan 1 1900 8:30AM
04/24/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Onsite Wastewater Services - May Supply | 1942001022 | Sara | Tusing | 2.000000 |  | Orenco Advantex | Orenco Advantex | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/28/2021 | 05:41 AM
06/25/2020 |  | Follow-Up |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Pad | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | replaced pod lid #3 | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/14/2021 | 04:27 PM
08/12/2020 |  | RoutineScheduled | 05-113-054 | Buchanan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Effluent Screens"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
09/04/2020 |  | Routine/Scheduled | 03-142-0122 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chickahominy | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1500 | Orenco Advantex | None | Pump | Distribution Box | Aggregate Trench | None | 600.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | None | Clear | [15 empty] | Routine service conducted. Processing Tank - normal operating level - RSV, recirc pump & effluent screen serviced. Treatment Module - media drapes and spray grid serviced. Discharge tank - Normal operating level - pump, float sensor and controls operating properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 09/08/2020 | Jan 1 1900 7:45AM
02/10/2020 |  | Routine, Scheduled |  | Warren County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Lord Fairfax | Cubbage, Harrison Lee, II | 1942001021 | Harrison | Cubbage | 1.000000 | 1000 | Septic Tank Only | Septic Tank Only | Pump | Manifold | Elevated Sand Mound | None |  | ["Control Operation"] | ["Control Operation"] |  | Musty | Clear | [15 empty] | [Comments]: Demand Dose Panel Cycle Count-7250 Sludge/Scum Accumulations: Septic Tank-12"/1" Pump Tank-6"/0" | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/11/2020 | 02:07 PM
07/08/2020 |  | RoutineScheduled | 177-06-0247-SWP | Spotsylvania | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | EcoPod | none | Gravity | Gravity |  | UV |  | ["Attached Growth Medium" ,"BlowerCompressorAerator Operation" ,"Disinfection" ,"SludgeScum Accumulation"] | ["Attached Growth Medium" ,"BlowerCompressorAerator Operation" ,"Disinfection"] | NA | [9 empty] | 2.000000 |  | 1.000000 | 82.500000 |  |  | Will be sent separately | Inspected | DO: 7.74 We recommend pumping the aerobic treatment unit due to scum & sludge accumulation. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/09/2021 | 03:25 PM
11/12/2020 |  | RoutineScheduled | SD-15-42 | Fauquier | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Level Sensor Operation" ,"Control Operation"] | ["Control Operation" ,"Level Sensor Operation"] | NA | [7 empty] | 11/12/2020 |  | 5.000000 | [5 empty] | Will be sent separately | Inspected | Owner had back up in September due to breakers being off. Added bleach to atu tank, then had local septic pumper empty the tank. Today, treatment looked very good, effluent level normal at splash plate. Strange growth that was reported last year is mostly gone. Heavy rain today, no sign of infiltration. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
06/08/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/27/2021 | 01:26 PM
10/12/2020 |  | RoutineScheduled |  | Rockingham | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"SludgeScum Accumulation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"SludgeScum Accumulation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | Microfast tank pumped at time of service | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/26/2021 | 09:04 AM
04/25/2020 |  | RoutineScheduled | 01-192-214 | Tazewell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. |  | Denny | Deel |  |  | WHITEWATER |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","Disinfection"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
04/02/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Fairfax | MCKIM, STEPHEN E | 1934000043 | STEPHEN | MCKIM |  |  | Septic Tank Only | Septic Tank Only | None | None | None | None |  |  | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/20/2020 | Jan 1 1900 10:18AM
06/03/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim |  |  | Best 1 | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/14/2021 | 04:27 PM
07/24/2020 |  | RoutineScheduled | 061-16-250 | Fauquier | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 5.000000 |  | Bio Barrier | Bio Barrier | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Control Operation" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | Biweekly inspection. Drip tank in high level alarm. Bad bearing noise coming from blower #1. Cut it off and restarted blower #2. Blower appeared to be running fine, but atu panel was alarming and could not be silenced. Circuit board in panel has some discoloration. New panel recommended as board is discontinued. Reduced recirculation back to septic tank by changing rest time from 20 min off to 40 min off. This should lower the D.O. level in the septic tank and potentially help with nitrogen reduction. Decreased peak rest time in the surge dosing tank from 1 hour to 45 min. Peak count has increased from 200 on 6/22 to 586 today. Substantially lower pressure combined with higher drip rate on zone 2 suggests a leak in tubing, but drip field grass was too high to be able to see any effluent surfacing. In the past 18 days, an average of 2,321.2 gals/day at 256.3 gals/dose (avg.) was pumped to the drip field for a total of 41,783 gallons. No infiltration see at the Tanncor lift station. Pump #1 etm 831.6, pump #2 etm 151.1. No infiltration seen at the Ross Industries lift station, but pump #2 overload was tripped. Reset, pump pulling 31 amps and not working. Pump #1 etm 2063.3, pump #2 857.5. Note: returned on 7/27/20 and pulled out pump. Spun impeller by hand and pump started. Started on its own several times. Possible bad spot in windings. | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
10/13/2020 |  | RoutineScheduled |  | Augusta | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Installed new timer | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/26/2021 | 09:04 AM
06/06/2020 |  | RoutineScheduled | 05-142-0227 | Hanover | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Chickahominy | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Ecoflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Attached Growth Medium"] | ["SludgeScum Accumulation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Septic Tank Baffles" ,"Distribution Pump Operation" ,"Attached Growth Medium"] | YES | [15 empty] | Will be sent separately | Inspected | Few roots on inlet wedge lid. Ponding on one side because of tip tray, we augered; OK now. Insultation panel fell onto tipping tray, we removed so tip try will work. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | Jan 1 1900 11:22AM
07/30/2020 |  | Follow-Up | 14-120-0192AM | Chesterfield | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Chesterfield | Old Dominion Onsite, Inc. | 1942001134 | John | Ewing | 1.000000 | 1000 | Clearstream ATU |  | Pump | Manifold | Elevated Sand Mound | None | 250.000000 | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation"] | ["Blower/Compressor/Aerator Operation","Control Operation"] | N/A | [17 empty] | There was not enough water in the discharge tank to flush the system. Significant wet spots and some standing water was noted around the sand mound. The air conditioning condensation drain needs to rerouted to rule out the possibility it is the cause of the wetness. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. |  | 07/29/2020 | Jan 1 1900 11:06AM
04/22/2020 |  | Routine/Scheduled |  | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex | [6 empty] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Recirculation Pump","Sludge/Scum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Recirculation Pump","Sludge/Scum Accumulation"] | N/A |  | 3.65 | 7.990000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/22/2020 | Jan 1 1900 8:00AM
11/06/2020 | Alternative | RoutineScheduled | 171-05-692 | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | [6 empty] | Advantex |  | Pump | Pressure | Drip |  |  | ["Attached Growth Medium","Auxiliary Filter","Septic Tank Baffles"] | ["Attached Growth Medium","Auxiliary Filter","Septic Tank Baffles"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 11/06/2020 | 12:00 AM
03/07/2020 |  | Routine, Scheduled | {FIPSCode}-STS-5274 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesapeake | R & K Septic, Inc. |  | Craig | Van Holten |  |  | Orenco Advantex |  | Pump | Distribution Box | Aggregate Bed | None |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/07/2020 | Jan 1 1900 8:30AM
02/10/2020 |  | Follow-Up |  | Culpeper County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 2.000000 |  | None | None | Pump |  |  | UV Light | [13 empty] | 17.000000 |  | 1.000000 | 14.800000 |  |  |  |  | [Comments]: DO 7.76 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/02/2020 | 11:52 AM
10/19/2020 |  | RoutineScheduled | 17-120-0080MA | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Lyttle Service Co., LLC dba Stamie E. Lyttle Co | 1942001332 | Benjamin | Chapin | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 10/19/2020 | 12:00 AM
07/28/2020 |  | Follow-Up |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | New pump was installed. System is in working condition | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/14/2021 | 04:27 PM
11/02/2020 |  | RoutineScheduled |  | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Wastemaster Inc |  | Timothy | Jenkins | 2.000000 |  | PuraFlo |  |  |  | Pad |  |  | [] | [] | [18 empty] | In for annual service and inspection. Puraflo peat in okay condition with compaction to distribution grid. System operating properly at this time. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 11/16/2020 | Jan 1 1900 11:15AM
06/24/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/14/2021 | 04:27 PM
03/02/2020 |  | Routine, Scheduled | 107-06-0679 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Rejected | EHD - Central Shenandoah | Cubbage, Harrison Lee, II | 1942001021 | Harrison | Cubbage | 4.000000 | 4000 | Septic Tank Only | Biomicrobics MicroFAST | Gravity | Manifold | Alternative Discharge | UV Light |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Effluent Screens","Level Sensor Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Effluent Screens","Level Sensor Operation"] |  | Musty | Dark | 8.000000 |  |  |  |  | 03/02/2020 | Aeration Port | 73.000000 |  |  | 49.000000 |  |  | Attached to this report |  | [Lab Comments]: E Coli 81 [Comments]: Sludge/Scum Accumulations: Comp.1-18"/0" Comp.2-6"/10" Comp.3-2"/0" Comp.4- 2"/0" Comp.5- 3"/2" VENIS File Names: 2366 Tinkling Springs Rd 3-2-20.pdf | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/14/2020 | 01:31 PM
09/08/2020 |  | Routine/Scheduled | C-05-111-0227 | Botetourt | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Alleghany-Roanoke | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Delta Environmental Products, DF Series |  | Pump | Drip | Drip Tubing | None |  | ["None"] | ["Blower/Compressor/Aerator Operation","Control Operation","Sludge/Scum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 09/08/2020 | Jan 1 1900 12:00PM
12/01/2020 |  | RoutineScheduled | 182-06-0471 | Rockingham | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Central Shenandoah | Onsite Wastewater Services - May Supply | 1942001627 | Drew | Shull | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Pressure | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | inspection by MS | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/28/2021 | 05:41 AM
07/23/2020 |  | RoutineScheduled | 107-00-0593 (LEGACY ALT. SYSTEM) | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Onsite Wastewater Services - May Supply | 1942001022 | Sara | Tusing | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | FIRST INSPECTION DONE BY DS H/O NOT HAPPY SO SET RE DID | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 05/28/2021 | 05:41 AM
04/07/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 | Approved | EHD - Loudoun | SES MidAtlantic LLC | 1942001203 | James | Green |  |  | Clearstream | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] |  | NA | [15 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. Needs compressor repair. BOB will be taken after repair of compressor. | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 |  | 04/15/2021 | 09:00 AM
12/03/2020 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Pump | Distribution Box |  | None |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Recirculation Pump","Sludge/Scum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Recirculation Pump","Sludge/Scum Accumulation"] | N/A |  |  | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 12/03/2020 | Jan 1 1900 3:30PM
09/08/2020 |  | RoutineScheduled | 13-100-0273 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Bundick Well & Pump | 1942001051 | Peter | Duer | 1.000000 | 1000 | Septic Tank | Delta Envir. DF | Pump | Pressure | Trenches | Not Applicable | 750.000000 | ["None"] | ["None"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 09/14/2020 | 02:15 PM
10/06/2020 |  | Follow-Up | 175-02-0474 | Manassas | This AOSS should now return to normal function after having provided the above state routine maintenance | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green | [9 empty] | ["Level Sensor (Float) Operation"] | ["Level Sensor (Float) Operation"] | [18 empty] | Replaced On & Off floats. | This AOSS should now return to normal function after having provided the above state routine maintenance |  | 10/06/2020 | 04:00 PM
09/29/2020 |  | Initial Visit | 136-07-0222 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | PremierTech, EFX |  | Pump | Distribution Box | Aggregate Bed | None | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | Musty | Clear | [15 empty] | Initial Visit Primary Septic Tank - normal operating level - effluent screen fractured / serviced - recommend replacement. Biofilter - slight ponding present - peatmoss in good condition - raked / turned. Pump Basin - normal operating level - pump, float sensors and controls functioning properly. Distribution Box - plastic - intact - both laterals accepting effluent. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 10/07/2020 | 08:00 AM
05/29/2020 |  | Follow-Up | SD-14-166 | Fauquier | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Chemically treated system and cleaned media. All tanks pumped out by Butler & Eicher Septic Cleaning. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
10/19/2020 |  | RoutineScheduled | 015-STS-334530 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Onsite Wastewater Services - May Supply | 1942001627 | Drew | Shull | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Pressure | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 05/28/2021 | 05:41 AM
06/03/2020 |  | Reportable Incident | 17-137-0119 | Goochland | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chickahominy | Stamie E. Lyttle Co. | 1942001470 | Eric | Tambourine | [9 empty] | [] | [] | [19 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 06/03/2020 | 12:00 AM
06/15/2020 |  | RoutineScheduled | 171-09-0393 | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | SEAL’S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | tank only | FAST | Pump | Pressure | Drip |  |  | ["BlowerCompressorAerator Operation","Auxiliary Filter","Dispersal System Operation"] | ["Dispersal System Operation","Auxiliary Filter","BlowerCompressorAerator Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 06/15/2020 | 12:00 AM
03/13/2020 |  | Routine, Scheduled | 069030152 | Frederick County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Lord Fairfax | Ferguson, Jeremy | 1942001008 | Jeremy | Ferguson | 1.000000 | 1250 | Microfast | Septic Tank Only | Pump | Drip | Drip Tubing | None |  |  | ["BlowerCompressorAerator Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | [Comments]: System is in compliance with approved plans and health department regulations. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/16/2020 | 01:13 PM
03/27/2020 |  | Follow-Up |  | Fairfax County | This AOSS should now return to normal function after having provided the above stated routine maintenance. | Paid | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green | [9 empty] | ["Dispersal System Operation"] | ["Dispersal System Operation"] | [18 empty] | [Comments]: Applied lime to affected area.Replaced solenoid, concrete casing & lid. | This AOSS should now return to normal function after having provided the above stated routine maintenance. |  | 03/27/2020 | Jan 1 1900 4:00PM
07/25/2020 |  | Routine/Scheduled |  | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump | Distribution Box |  | UV Light |  | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  |  | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 07/25/2020 | Jan 1 1900 1:45PM
06/22/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/14/2021 | 04:27 PM
04/29/2020 |  | RoutineScheduled | 07-184-5007 | Scott | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | Septic Inc |  | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
07/17/2020 |  | RoutineScheduled | 177-10-0158-SWP | Spotsylvania | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Effluent Screens"] | ["Attached Growth Medium" ,"Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/09/2021 | 03:25 PM
08/25/2020 |  | Pump-Out Only | {FIPSCode}-STS-83101 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Wastemaster Inc |  | Timothy | Jenkins | 2.000000 |  | ATU |  | Pump | Gravity | Discharge |  |  | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 09/15/2020 | 01:50 PM
04/24/2020 |  | Initial Visit | 175-19-0179 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Prince William | Dominion Septic, Inc | 1942001125 | Tom | Jackson |  |  | EZ Treat Sandfilter | none | Pump | Gravity | Drip | UV |  | ["Level Sensor Operation" ,"Control Operation"] | ["Level Sensor Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | The tested drip rate was much higher than design. Solenoid valves appear to be closing properly, but could be the reason for the higher rates. Tubing could also have some bad emitters. Advised owner to contact installer if any wet spots appear in dripfield. Will recheck drip rates at 180 day inspection. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
06/11/2020 |  | Follow-Up | 179-14-0311-SP | Stafford | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [9 empty] | 12.000000 | [5 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
05/08/2020 | Alternative | RoutineScheduled | 151-12-0160 | Lancaster | This AOSS is functioning as designed and in accord | Approved | EHD - Three Rivers | [13 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accord |  |  | 12:00 AM
01/09/2020 |  | Routine, Scheduled | 07-184-5004 | Scott County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Lenowisco | DEEL, DENNY M | 1942001097 | DENNY | DEEL |  |  | Norweco Singulair ATU | None | Gravity | None | Alternative Discharge | Chlorine | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens"] |  | Musty | Clear | [15 empty] | [Comments]: 6 Blue Crystal 15 Bio Max Added | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/05/2020 | Jan 1 1900 3:36PM
04/27/2020 |  | Routine, Scheduled | 175-18-0067 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Biomicrobics MicroFAST |  |  |  |  | UV Light |  | ["Blower/Compressor/Aerator Operation","Disinfection"] | ["Blower/Compressor/Aerator Operation","Disinfection"] |  | Good | Clear | [15 empty] | Pump Amps 10.02 ETM 922 h 23 m Cycles 6386 Septic Sludge 12" Scum 3" ATU Sludge 11" Scum 0 Pump Sludge 4" Scum 0.50 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/27/2020 | 05:31 PM
10/14/2020 |  | RoutineScheduled | 061-16-250 | Fauquier | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 5.000000 |  | Bio Barrier | Bio Barrier | Pump | Gravity | Drip | Not Applicable |  | ["Distribution Pump Operation" ,"Level Sensor Operation" ,"Control Operation"] | ["Distribution Pump Operation" ,"Level Sensor Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Biweekly inspection. Reduced standard rest time in surge dosing panel to help keep the tank out of peak mode. Peak count today 988. High level float in drip tank failed testing, replaced it. Female camlock for drip pump #2 was cracked and leaked during pump cycles for either pump, replaced it (pump closer to dripfield). In the past 19 days, an average of 1,682.4 gals/day at 184.7 gals/dose was pumped to the dripfield for a total of 31,967 gallons. Top concrete ring on secondary septic tank damaged by mower. Tank has been bypassed, but this could be a point of infiltration during rain. | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
04/21/2020 |  | Routine, Scheduled | SWP-04-206 | Stafford County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Puraflo | None | Pump | Distribution Box | Aggregate Trench |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [18 empty] | [Comments]: Pulled roots out of sample box and applied root kill. Massive roots in septic tank and pump tank. Proposal for repairs to be sent to homeowner. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/27/2020 | 04:14 AM
02/10/2020 |  | Reportable Incident | 228-13-0534 A | Virginia Beach | This AOSS should now return to normal function after having provided the above stated routine maintenance. | Approved | EHD - Virginia Beach | Farmer’s Septic Service, Inc. |  | Ross | Cole | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | [Comments]: Owner called due to a red light and alarm. Serviced system. Checked the pump, panel, & floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream, changed the filter in the aerator, changed the mesh screen in the spinfilter, replaced the timer override float, and replaced UV Salcor bulb. The pressure switch on the aerator is not hooked up. The septic tank needs pumping - company was coming out the following day to pump for the owner. The timer is set to 6 minutes every 2 hours. | This AOSS should now return to normal function after having provided the above stated routine maintenance. |  | 02/10/2020 | Jan 1 1900 12:00PM
11/13/2020 |  | Routine, Scheduled | 175-13-0134 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Biomicrobics MicroFAST |  |  |  |  | UV Light |  | ["Blower/Compressor/Aerator Operation","Disinfection"] | ["Blower/Compressor/Aerator Operation","Disinfection"] |  | Acceptable | Clear | [15 empty] | Spin filter cleaned. Pump Amps 11.04 ETM 1180 Cycles 10747 Water Meter Reading 292150 Septic Sludge 3" Scum 8" ATU Sludge 8" Scum 0 Pump Sludge .50 Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 11/13/2020 | 10:35 AM
02/03/2020 |  | Routine, Scheduled |  | Loudoun County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | None | None | Gravity | [24 empty] | [Comments]: Sale inspection on a conventional gravity septic system. The sewer line was camera snaked and was clear. The concrete septic tank was dug up it was 12" under the ground and was pump out. The inlet Tee was cast iron and the outlet Tee was pvc . The septic tank was inspected for any leaks or cracks none were seen. The pvc conveyance line was camera snaked to the d-box and was clear. The 10 port concrete d-box was 12" under the ground and was dug up to inspect. All 7 header lines and drain field lines were camera snaked and were clear. The drain field was probed. At time of inspection all components were in working condition | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/02/2020 | 04:43 AM
06/03/2020 |  | RoutineScheduled |  | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Ashleys Septic Service | 1930332 | Shane | Majewski | 1.000000 | 1500 |  |  | Pump | Gravity |  | Not Applicable |  | ["None"] | [] | NA | [16 empty] | Exempt |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 06/03/2020 | Jan 1 1900 3:00AM
12/31/2020 |  | Reportable Incident | S 800-15-0138 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | Owner called due to the light being on. Serviced system. Checked the pump, panel, & floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. Removed the spinfilter screen - drainfield is an LPD. The septic tank was flooded - could not check. There is visible wetness on the drainfield - have had alot of rain - once it dries need to keep an eye on it. The timer is set to 10 minutes every 2 hours. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12/31/2020 | Jan 1 1900 12:00PM
11/02/2020 |  | RoutineScheduled | {FIPSCode}-STS-77746 | Spotsylvania | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Recirculation Pump"] | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/09/2021 | 03:25 PM
04/14/2020 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  |  | Drip | Elevated Sand Mound | UV Light |  | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  |  | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/14/2020 | Jan 1 1900 10:00AM
02/21/2020 |  | Routine, Scheduled | E-05-111-0058 | Botetourt County | This AOSS should now return to normal function after having provided the above stated routine maintenance. | Approved | EHD - Alleghany-Roanoke | WAUGH, IAIN C | 1942001512 | IAIN | WAUGH | 4.000000 | 4000 | Septic Tank Only | Biomicrobics MicroFAST | Pump | Drip | Drip Tubing | None |  | ["Level Sensor Operation"] | ["BlowerCompressorAerator Operation","Level Sensor Operation"] | [18 empty] | [Pumpout Comments]: Septic tank on top hill 6" sludge, 3-5" slude in Fast unit and 1" in pump tank Good aeration in Fast unit. Cleaned airfilter All arams and pumps tested operational [Comments]: #1 Septic 4-6"-Sludge Pump Tank 6"-Sludge Alarm Good, Pump on FLoat switch bad, Replaced with new 13amp pump run float. #2 Septic tank 4"-Sludge Pump Tank 1-2"-Sludge. Cleaned electrical plug but severe corrosion maybe drawing higher amps which caused float to burn up. Amp draw returned to 11.8a, 13.9 amps on Arrival | This AOSS should now return to normal function after having provided the above stated routine maintenance. |  | 03/05/2020 | Jan 1 1900 4:31PM
08/09/2020 |  | Reportable Incident |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Eco Virginia | 1942001235 | William | Poindexter | 1.000000 |  | none | none | Gravity | Gravity |  | Not Applicable |  | ["Distribution Pump Operation" ,"Level Sensor Operation"] | ["Level Sensor Operation" ,"Distribution Pump Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced pump, control floats and concrete lid. System is LPD, pump rate >100 gpm | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 |  | 06/03/2021 | 05:53 AM
03/27/2020 |  | RoutineScheduled |  | Warren | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Review | EHD - Lord Fairfax | Greenway Engineering | 1942001008 | Jeremy | Ferguson | 1.000000 | 1500 | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium"] | [] | YES | [17 empty] | Peat Moss needs replaced. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. |  | 09/28/2020 | 10:30 AM
03/13/2020 | Alternative | Routine/Scheduled | 136-15-0165 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | Serviced system. Checked the pump, panel, & floats (ok). Cleaned the filter and the diffuser in the Clearstream and cleaned the filter in the aerator | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 03/13/2020 | 12:00 PM
07/23/2020 |  | Follow-Up | 175-04-0011 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green | [9 empty] | ["Level Sensor (Float) Operation"] | ["Level Sensor (Float) Operation"] | [18 empty] | Replaced float in ATU. | This AOSS should now return to normal function after having provided the above state routine maintenance |  | 07/23/2020 | 04:00 PM
07/07/2020 |  | RoutineScheduled | {FIPSCode}-STS-70836 | Spotsylvania | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | The alarm light & alarm horn on the control panel are not working & should be replaced. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/09/2021 | 03:25 PM
12/01/2020 |  |  | 14-192-113 | Tazewell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 12/01/2020 |  | 6.990000 |  |  | 2.500000 |  |  | Attached to this report |  | BOD: 6.99 TSS: 2.50 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12/01/2020 | Jan 1 1900 1:45PM
08/06/2020 |  | Routine/Scheduled |  | Frederick | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Lord Fairfax | POWELLS PLUMBING, INC. | 1942001036 | Kurt | Holthaus | 1.000000 | 1000 | Microfast |  | Pump | Distribution Box | Aggregate Trench |  | 600.000000 | ["Blower/Compressor/Aerator Operation","Control Operation"] | ["Blower/Compressor/Aerator Operation","Control Operation"] | N/A | [17 empty] | Annual Inspection - Replaced audible alarm in control panel for discharge pump and serviced blower. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 09/10/2020 | 10:25 AM
06/18/2020 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump | Drip | Elevated Sand Mound | UV Light |  | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  | 7.19 | 7.330000 | 3.900000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 06/18/2020 | Jan 1 1900 1:30PM
11/02/2020 |  | RoutineScheduled | 179-09-0163-SR | Stafford | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  | ["Effluent Screens" ,"Attached Growth Medium"] | ["Effluent Screens" ,"Attached Growth Medium"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 |  | 04/09/2021 | 03:25 PM
10/01/2020 |  | RoutineScheduled | {FIPSCode}-STS-66158 | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions | 2705163102 | Michele | Ware | 2.000000 | [8 empty] | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","Other","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 10/01/2020 | 12:00 AM
03/12/2020 |  | Routine, Scheduled | 171-11-0284 | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Lord Fairfax | SEAL, CHARLES K | 1934000144 | CHARLES | SEAL | 1.000000 |  |  | EcoPure | Gravity | Distribution Box | Aggregate Trench | None |  | ["Attached Growth Medium","Septic Tank Baffles"] | ["Attached Growth Medium","Septic Tank Baffles"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/16/2020 | 11:15 AM
05/18/2020 | Alternative | Reportable Incident | 136-06-0102 | Gloucester | This AOSS should now return to normal function after having provided the above state routine maintenance | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | Puraflo |  | Gravity | None | Aggregate Bed | None | 450.000000 | ["Septic Tank Baffles","Sludge/Scum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | [17 empty] | Septic tank pumped to facilitate replacement of building sewer and effluent screen Replaced building sewer and effluent screen. Conducted routine service on PuraFlo biofilters. | This AOSS should now return to normal function after having provided the above state routine maintenance |  | 05/25/2020 | 07:30 AM
01/14/2020 |  | Reportable Incident | 234-14-282 | Chesapeake | This AOSS should now return to normal function after having provided the above stated routine maintenance. | Approved | EHD - Chesapeake | R & K Septic, Inc. |  | Craig | Van Holten |  |  | Clearstream ATU | [6 empty] | ["Distribution Pump Operation","Level Sensor Operation"] | ["Distribution Pump Operation","Level Sensor Operation"] | [18 empty] | [Comments]: Replaced alarm bulb, cleaned pump screen and screen filter | This AOSS should now return to normal function after having provided the above stated routine maintenance. |  | 01/14/2020 | Jan 1 1900 7:30AM
02/07/2020 |  | Routine, Scheduled | SD-86-724 | Spotsylvania County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | None | None | Gravity | Distribution Box | Aggregate Trench |  |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] |  | YES | YES | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/06/2020 | 02:45 PM
01/06/2020 |  | Routine, Scheduled | 093-06-0134 | Isle of Wight County | This AOSS should now return to normal function after having provided the above stated routine maintenance. | Approved | EHD - Western Tidewater | HERMAN, ADAM C | 1934000195 | ADAM | HERMAN | 1.000000 | 1250 | Clearstream ATU | None | Pump | Distribution Box | Aggregate Trench | None |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | [18 empty] | [Comments]: Replaced blower and diffuser. System functioning properly. | This AOSS should now return to normal function after having provided the above stated routine maintenance. |  | 01/09/2020 | Jan 1 1900 8:15AM
05/05/2020 |  | RoutineScheduled | SD-12-149 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Soils, Inc. | 1940001392 | Markham | Smith | 2.000000 | 1500 |  |  | Pump | Gravity | Pad | Not Applicable | 62.500000 | [] | ["Attached Growth Medium","Control Operation","Effluent Screens","SludgeScum Accumulation","Level Sensor Operation"] | YES | [17 empty] | Pump Chamber had 2in scum 8in Sludge Septic tank had 0 in scum 5 sludge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 06/13/2020 | 01:25 PM
02/19/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | EZ Treat Sandfilter | EZ Treat Sandfilter | Pump | Drip | Drip Tubing | UV Light |  | ["Disinfection","Effluent Screens"] | ["Disinfection","Effluent Screens"] |  | Good | Clear | [5 empty] | 02/11/2020 |  | 21.000000 |  | 11.000000 | [5 empty] | [Comments]: Spin filter cleaned.Pump Amps 8.73 ETM 470h Cycles 4746Septic Sludge 4" Scum 0.50ATU Sludge 1" Scum 0Pump Sludge 0 Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/19/2020 | Jan 1 1900 1:56PM
07/20/2020 |  | RoutineScheduled | 181-01-0240 (LEGACY ALT. SYSTEM) | Rockbridge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Hunter E. Ayres, General Contractor | 1942001166 | Hunter | Ayres | 1.000000 | 1250 | Biomicrobics MicroFAST |  | Siphon | Gravity | Trenches | Not Applicable |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Filter checked and cleaned. No apparent leaks in system or drain field area. Control panel functioning properly. Lids properly secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 07/24/2020 | 07:15 AM
02/20/2020 |  | Routine, Scheduled |  | York County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Peninsula | PARSLEY, JAMES MICHAEL | 194001106 | JAMES | PARSLEY | 1.000000 | 1000 | Clearstream ATU | Septic Tank Only | Pump | Distribution Box | Gravel-Less Trench | None |  | ["None"] | ["Effluent Screens"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/21/2020 | Jan 1 1900 3:30PM
10/13/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/27/2021 | 01:26 PM
08/26/2020 |  | RoutineScheduled | 2006-143-0346 | Henrico | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 | Approved | EHD - Henrico | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | none | none | Pump | Gravity | Pad | Not Applicable |  | ["Attached Growth Medium" ,"Effluent Screens"] | ["Attached Growth Medium" ,"Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected | The peat is beginning to age. We recommend treating around the modules for ants. | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 |  | 04/09/2021 | 03:25 PM
04/30/2020 | Alternative |  | 151-11-0091 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | KC Forge Environmental Service, LLC | 1942001034 | Kent | Cuthbertson |  |  |  |  | Pump | Gravity | Trenches | UV | 26427.000000 | [] | [] | [18 empty] | All lab results are included in the attached file below. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 02:25 PM
03/17/2020 |  | Routine, Scheduled |  | Loudoun County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | None | Pump | Distribution Box | Aggregate Trench | [23 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/12/2020 | 02:21 PM
11/13/2020 |  | RoutineScheduled | 91-184-5002 | Scott | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Effluent Screens"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
07/27/2020 |  | RoutineScheduled | VAG408227 | Rockingham | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Central Shenandoah | Onsite Wastewater Services - May Supply | 1942001627 | Drew | Shull | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/28/2021 | 05:41 AM
05/08/2020 |  | Initial Visit | 05-160-0175 | Montgomery | This AOSS is not functioning as designed or in acc | Approved | EHD - New River | MONTGOMERY SANITATION SERVICES, INC | 1942001003 | TIM | CONNER |  |  |  | NONE | PUMP | MANIFOLD | DRIP | NONE |  | [] | [] | [17 empty] | Pumped Out | Blower is not working & the pump tank needs to be pumped and cleaned. | This AOSS is not functioning as designed or in acc |  | 05/08/2020 | 12:00 AM
04/24/2020 |  | RoutineScheduled | SP-04-409 | Caroline | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Dispersal System Operation" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Recirculation Pump"] | NA | [15 empty] | Will be sent separately | Inspected | Effluent is coming to the surface in the drainfield areas. We recommend contacting an Alternative Onsite Soil Evaluator (AOSE) to evaluate the drainfield, and make repair or replacement recommendations. | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 |  | 04/09/2021 | 03:25 PM
07/23/2020 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump | Drip | Elevated Sand Mound | UV Light |  | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  |  | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 07/23/2020 | Jan 1 1900 1:00PM
05/07/2020 |  | RoutineScheduled | 153-STS-20158 | Prince William | This AOSS is functioning as designed and in accord | Approved | EHD - Prince William | Wastemaster |  | Tim | Jenkins | 2.000000 |  |  |  | Pump |  | Discharge | Chlorine |  | [] | [] |  | Musty | Clear | 6.800000 |  |  | 1.700000 |  | 05/07/2020 |  | 5.000000 |  |  | 4.000000 |  |  | Will be sent separately |  |  | This AOSS is functioning as designed and in accord |  | 05/07/2020 | 09:30 AM
05/01/2020 |  | RoutineScheduled |  | Fairfax | This AOSS is functioning as designed and in accord | Approved | EHD - Fairfax | Great Falls Septic Service | 1942001301 | Joshua | Hott | 1.000000 | 1250 |  | Puraflo | Pump | Distribution Box | Aggregate Trench | None | 500.000000 | ["Effluent Screens","None"] | ["Effluent Screens","None"] |  | Low | [17 empty] | This AOSS is functioning as designed and in accord |  |  | 12:00 AM
03/11/2020 |  | Initial Visit | 177-19-0099-SP | Spotsylvania County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | None | None | Pump | Distribution Box | Aggregate Trench | [22 empty] | [Comments]: Start-Up Inspection | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/06/2020 | 02:45 PM
11/21/2020 |  | RoutineScheduled | 175-04-0856 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Wastemaster Inc |  | Timothy | Jenkins | 2.000000 |  | PuraFlo | Effluent Filter | Pump | Gravity | Discharge | Chlorination |  | [] | [] |  | Musty | Clear | 7.400000 |  |  | 1.800000 | [12 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:55 PM
09/10/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | The risers opn the septic tank are oval and make it difficult to get the lids on. The filter cannot be removed because of this as well. There is no inlet tee. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/27/2021 | 01:26 PM
10/23/2020 |  | Follow-Up | n/a | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Wastemaster Inc |  | Timothy | Jenkins | 3.000000 |  | ATU | Recirculating Sand Filter | Pump | Gravity | Discharge | Chlorination |  | [] | [] | [18 empty] | In for pump out of all tanks and filter change out in MultiFlo. Barry's septic pumped out all tanks. Replaced filters in multiflo. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 11/05/2020 | 10:55 AM
08/25/2020 |  | RoutineScheduled | E-05-111-0058 | Botetourt | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 4000 | Biomicrobics Fast |  | Pump | Pressure | Drip | Not Applicable |  | [] | [] | NA | [16 empty] | Inspected | Sludge levels-- 6" sludge in Lower Septic tank & Pump tank, floats and pump opperational. Play Ground parking septic Tanks 8-16" sludge, No pumping needed. Up top Hill Blower alarm good filter cleaned. pump opperational, sludge levels= Fast tank 4" fast unit 12" pump tank -trace sludge, Good aeration. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 08/28/2020 | Jan 1 1900 9:30AM
05/07/2020 |  | Routine/Scheduled | 03-120-0734AR | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesterfield | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1500 | Orenco Advantex | None | Pump | Drip | Drip Tubing | None |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | System is 16 years old: the Septic Tank does not have proper Riser access; the System's Pump and Floats have exceeded life expectancy; Discharge Floats are not properly secured; the Discharge Riser is leaking; the Advantex Media Filters (sheets) and Lid have exceeded life expectancy; the Control Panel has exceeded life expectancy | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 06/26/2020 | Jan 1 1900 1:08PM
10/14/2020 |  | Initial Visit | 023-STS-42583 | Botetourt | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1000 | Advantex |  | Gravity | Gravity | Trenches |  |  | ["None"] | ["None"] | [18 empty] | Initial visit and start-up. Manually ran recirculation pump to get to normal operating level. Tightened loose unions that were leaking. Tested floats, pump and alarm. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 10/21/2020 | Jan 1 1900 7:03PM
01/22/2020 |  | Routine, Scheduled |  | Loudoun County | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Paid | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | None | None | Gravity | [24 empty] | [Comments]: Sale inspection on a conventional septic system. There is a cleanout out side of the house. The septic tank was dug up it was 18" below the surface. The tank was pumped out and inspected for any leaks or cracks. The sewer and conveyance line were camera snaked no issues were seen. The 8 port concrete d-box was dug up it was 12" under the ground and was in good condition. All 7 lines were camera snaked. 1 line was crushed about a foot from d-box. It will need dug up and the section replaced. The drain field was probed. At this time the septic system in not in complete working condition. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 03/02/2020 | 04:43 AM
02/17/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Biomicrobics MicroFAST |  | Pump | Drip | Drip Tubing | UV Light |  | ["BlowerCompressorAerator Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation"] |  | Good | Good | [15 empty] | [Comments]: Recommend pumping MicroFast tank.Spin filter cleaned.Pump Amps 7.85 ETM 855h 5m Cycles 4661Water Meter Reading 235600Septic Sludge 13" Scum 7"ATU Sludge 16" Scum 1"Pump Sludge 1" Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/17/2020 | Jan 1 1900 4:50PM
02/20/2020 |  | Routine, Scheduled | 12-163-0089 | New Kent County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chickahominy | PARSLEY, JAMES MICHAEL | 194001106 | JAMES | PARSLEY | 1.000000 | 500 | Clearstream ATU | Septic Tank Only | Pump | Distribution Box | Aggregate Trench | None |  | ["None"] | ["Effluent Screens"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/21/2020 | Jan 1 1900 3:11PM
10/21/2020 |  | Routine/Scheduled | 12-120-0201A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. |  |  | Clearstream ATU |  | Pump |  |  |  |  | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 10/21/2020 | Jan 1 1900 12:00PM
02/06/2020 |  | Routine, Scheduled |  | Loudoun County | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Paid | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | None | Pump | Distribution Box | Aggregate Bed | [22 empty] | [Comments]: Septic tanks effluent level was below the Tees. The tank was pumped out and inside of the tank inspected. there is a crack on the left corner of tank and the concrete around it is soft. The pump tank has a spot in the mid seam were water is squirting in. The county and a AOSE will need to be contacted | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 03/02/2020 | 04:43 AM
11/20/2020 |  | RoutineScheduled | 08-118-0060 | Charles City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Onsite Maintenance Team | 1942001039 | Corey | Braxton | 3.000000 |  | Advantex AX20 |  | Pump | Pressure | Drip |  | 250.000000 | [] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation"] | YES | Musty | Clear | 7.100000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 11/21/2020 | 12:00 AM
10/13/2020 |  | Reportable Incident |  | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  |  |  |  | ["Blower/Compressor/Aerator Operation","Control Operation","Level Sensor (Float) Operation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Level Sensor (Float) Operation"] | N/A | [17 empty] | Replaced aerator, alarm float in CT, alarm light bulb, gauge & bushing. Cleaned pump screen and screen filter. | This AOSS should now return to normal function after having provided the above state routine maintenance |  | 10/13/2020 | Jan 1 1900 9:00AM
06/26/2020 |  | RoutineScheduled |  | Frederick | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Pending Review | EHD - Lord Fairfax | Aquarobic Services | 1934000142 | Michael | Blake |  |  | none | none | Pump | Gravity | Mound | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"Auxiliary Filter" ,"Control Operation"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced failed processor and failed blower (with a loaner). Junction box terminal strip was very corroded. Replaced terminal strip and ground lugs. Pump failed in testing, searching for replacement. Evidence of groundwater infiltration at manway seals and pipe penetrations. Need resealed. Single point aeration has developed. Diffusers need replaced. Float switches failed testing, need replaced. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 07/01/2022 | 10:30 AM
03/30/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Clearstream | EcoPod | Pump |  |  | UV Light |  | ["BlowerCompressorAerator Operation","Disinfection","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Disinfection"] |  | Good | Clear | 6.020000 | 0.640000 |  |  |  | 03/30/2020 |  |  |  | 2.000000 | [5 empty] | [Comments]: Delta EcoPod needs pumping.Pump 1 Amps 9.1/8.7Pump 2 Amps 9.5/5.2 ETM 111h/121h Septic Sludge 6" Scum 12"ATU Sludge 12" Scum 0.25Pump Sludge 4"/1" Scum 0.50/0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/30/2020 | Jan 1 1900 11:31AM
12/08/2020 |  | RoutineScheduled | 2032-96-153 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Wastemaster Inc |  | Timothy | Jenkins |  |  | Sequencing Bat Reactor |  |  |  | Discharge |  |  | [] | [] |  | Musty | Clear | 7.700000 |  |  | 1.400000 | [12 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12/08/2020 | 01:00 PM
05/28/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Recommend removing larger bushes from around the modules | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/27/2021 | 01:26 PM
08/20/2020 |  | Initial Visit | 199-05-0028 | York | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Peninsula | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1500 | Orenco Advantex |  | Pump | Distribution Box | Aggregate Bed | None | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | Musty | Clear | [15 empty] | Initial Visit for service agreement. Processing Tank in high level - pumped 1000 gallons - serviced RSV, Recirc pump and effluent screen. Cause of high level due to lack of service. Treatment Module - media drapes and spray grid serviced. Discharge Tank - normal operating level - discharge pump, float sensors and controls operating properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 08/21/2020 | Jan 1 1900 7:30AM
02/12/2020 |  | Routine, Scheduled |  | Loudoun County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | None | Pump | Distribution Box | Aggregate Trench | [23 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/02/2020 | 04:43 AM
03/06/2020 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Onsite Wastewater Service | 1942001223 | MATTHEW | FERRELL | 1.000000 | 1250 |  |  | Gravity | Pressure | Drip | Not Applicable |  | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 03/06/2020 | 12:00 AM
07/30/2020 |  | Routine/Scheduled |  | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump | Distribution Box |  | None |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  |  | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 07/30/2020 | Jan 1 1900 12:45PM
03/05/2020 |  | Reportable Incident |  | Fluvanna County | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Paid | EHD - Blue Ridge | ARNOLD, ARCHIE G | 1942001291 | ARCHIE | ARNOLD |  |  | Norweco Singulair ATU | Septic Tank Only | Pump | Drip | Elevated Sand Mound | None |  | ["BlowerCompressorAerator Operation"] | [19 empty] | [Comments]: O&M: No power going out to system. homeowner wasn’t home. Left instructions so that when we return the breakers can be on. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 03/13/2020 | 03:07 PM
01/10/2020 |  | Routine, Scheduled | 07-120-0041A | Chesterfield | This AOSS should now return to normal function after having provided the above stated routine maintenance. | Approved | EHD - Chesterfield | Chapin, Ben |  | Ben | Chapin |  |  | Septic Tank Only | Septic Tank Only | None | None | None | None | [21 empty] | Lab results not reported by Operator, EHS chose "No" in order to allow saving updated entry. VENIS File Names: 516 Enon Chuch Rd.jpeg | This AOSS should now return to normal function after having provided the above stated routine maintenance. |  | 02/12/2020 | Jan 1 1900 2:36PM
05/18/2020 |  | RoutineScheduled | 15-113-035 | Buchanan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | Septic Inc |  | Denny | Deel |  |  |  |  | Gravity | Gravity | Pad | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
01/23/2020 |  | RoutineScheduled | 10-113-039 | Buchanan County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | DEEL, DENNY M | 1942001097 | DENNY | DEEL |  |  | Norweco Singulair ATU | None | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens"] |  | Musty | Clear | [15 empty] | [Comments]: 5 Blue crystal 10 Bio Max Added | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 02/05/2020 | Jan 1 1900 5:20PM
06/17/2020 |  | Routine/Scheduled | 04-172-0277A | Powhatan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesterfield | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1500 | Orenco Advantex |  | Pump | Distribution Box | Aggregate Trench | None | 600.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | Musty | Clear | [15 empty] | Routine service conducted - Serviced recirc pump, effluent screen, and media drapes. Serviced discharge pump. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 06/18/2020 | Jan 1 1900 8:20AM
06/25/2020 |  | RoutineScheduled | 177-06-0471-SWP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | EcoPod | none | Pump | Gravity | Drip | Not Applicable |  | ["Distribution Pump Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Distribution Pump Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | We recommend replacing the 12" riser & lid on the Septic Tank. | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 |  | 04/09/2021 | 03:25 PM
11/20/2020 |  | RoutineScheduled | 96-197-A4 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | Wise Health Dept |  | Rodney | Neece | 1.000000 |  | Atu Jet |  | Gravity | Gravity | Discharge | Chlorination |  |  |  |  | None | Clear | 6.400000 | 6.000000 |  | 0.000000 | good | [11 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  |  | 12:00 AM
10/19/2020 |  | RoutineScheduled | SD-96-343 | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC |  | Jason | Brown | 2.000000 | 1000 | Septic tank | Pura-Flo | Pump | Pressure | Pad | Not Applicable |  | [] | [] | YES | Musty | Cloudy | [15 empty] | This inspection is for a real estate transfer. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 10/20/2020 | 04:55 PM
02/07/2020 |  | Routine, Scheduled |  | Warren County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Lord Fairfax | Ferguson, Jeremy | 1942001008 | Jeremy | Ferguson | 1.000000 | 1000 | Aquarobic Mini Plant | None | Pump | Drip | Drip Tubing | None |  |  | ["Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | [Comments]: System is in compliance with approved plans and health department regulations. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/27/2020 | 10:30 AM
04/03/2020 |  | Routine, Scheduled | 06-192-226 | Tazewell County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Cumberland Plateau | DEEL, DENNY M | 1942001097 | DENNY | DEEL |  |  | Norweco Singulair ATU | None | Gravity | None | Alternative Discharge | Chlorine | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens"] |  | Musty | Clear | [15 empty] | [Comments]: 2 blue crystals, 7 biomax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/08/2020 | Jan 1 1900 10:37AM
12/11/2020 | Alternative | RoutineScheduled | 171-06-0921 | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [7 empty] | Chlorination |  | [] | [] |  | None | Clear | 7.670000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12/17/2020 | 02:35 PM
07/02/2020 |  | RoutineScheduled |  | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 2705051738 | Joshua | Hott |  |  | Septic | Puraflo | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [19 empty] | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. |  |  | 12:00 AM
10/12/2020 |  | Routine/Scheduled | 02-142-0150 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chickahominy | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1500 | Orenco Advantex |  | Gravity | Distribution Box | Aggregate Trench | None | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | None | Clear | [15 empty] | Routine Service Processing Tank - normal operating level - RSV, Recirc. Pump & effluent screen serviced. Float sensors and controls operating properly. Treatment Module - media drapes & spray grid serviced. Distribution box - normal operating level - all laterals accepting effluent. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 10/16/2020 | Jan 1 1900 7:45AM
03/09/2020 |  | Routine, Scheduled | {FIPSCode}-STS-1543 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesapeake | R & K Septic, Inc. |  | John | Butt, Jr |  |  | Clearstream ATU |  | Pump | Drip | Elevated Sand Mound | UV Light |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] |  |  | 4.39 | 7.490000 | 4.000000 | [13 empty] | [Comments]: Needs a UV Bulb | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/09/2020 | Jan 1 1900 1:45PM
03/20/2020 |  | Initial Visit | 17-114-136 | Buckingham | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Piedmont | Taylor's Septic Service | 1942001028 | Penny | Taylor | 1.000000 | 1000 |  |  | Pump |  | Trenches | UV | 450.000000 | [] | ["Control Operation","Disinfection","Dispersal Sytem Operation","Level Sensor Operation"] | [18 empty] | water sampling will need to be done | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. |  | 04/03/2020 | 12:00 AM
05/26/2020 |  | Pump-Out Only |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | POWELLS PLUMBING, INC. | 1942001036 | Kurt | Holthaus | 1.000000 | 1000 | Puraflo |  | Pump | Drip | Drip Tubing |  |  | ["Sludge/Scum Accumulation"] | ["Sludge/Scum Accumulation"] | N/A | [17 empty] | Pumped septic tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 07/02/2020 | 02:12 PM
03/09/2020 |  | Routine, Scheduled | {FIPSCode}-STS-4015 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesapeake | R & K Septic, Inc. |  | John | Butt, Jr |  |  | Clearstream ATU |  | Pump | Drip | Elevated Sand Mound | UV Light |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] |  |  | 10.4 | 7.870000 | 2.000000 | [13 empty] | [Comments]: UV is not working. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/09/2020 | Jan 1 1900 1:30PM
01/24/2020 |  | Routine, Scheduled | 099-17-0068 SP | King George County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | None | Pump | Distribution Box | Aggregate Trench |  |  | ["Attached Growth Medium","Effluent Screens","Recirculation Pump"] | ["Attached Growth Medium","Effluent Screens","Recirculation Pump"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/04/2020 | 07:46 AM
07/10/2020 |  | RoutineScheduled |  | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Payment | EHD - Chesterfield | Stamie E. Lyttle Co. | 1942001470 | Eric | Tambourine | [9 empty] | [] | [] | [19 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. |  |  | 12:00 AM
05/13/2020 |  | RoutineScheduled |  | Warren | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/26/2021 | 09:04 AM
06/18/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/14/2021 | 04:27 PM
05/08/2020 |  | RoutineScheduled | 2070-01-153 | Prince William | This AOSS is functioning as designed and in accord | Approved | EHD - Prince William | Wastemaster | 1965-001817 | Tim | Jenkins | 2.000000 |  |  |  | Pump |  | Discharge | Chlorine |  | [] | [] |  | Musty | Clear | 7.400000 |  |  | 2.200000 |  | 05/08/2020 |  | 5.000000 |  |  | 1.900000 |  |  | Will be sent separately |  |  | This AOSS is functioning as designed and in accord |  | 05/08/2020 | 09:15 AM
08/14/2020 | Alternative | RoutineScheduled | 171-11-0018 | Shenandoah | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Lord Fairfax | Onsite Wastewater Services - May Supply | 1942001022 | Sara | Tusing | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/28/2021 | 05:41 AM
07/22/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/14/2021 | 04:27 PM
01/09/2020 |  | Routine, Scheduled |  | Essex County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Three Rivers | PINNIX, JOEL S | 1934000193 | JOEL | PINNIX |  |  | Septic Tank Only | Septic Tank Only | None | None | None | None | [22 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/13/2020 | 03:13 PM
12/18/2020 |  | Reportable Incident |  | Isle Of Wight | This AOSS should now return to normal function after having provided the above state routine maintenance | Pending Payment | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Puraflo |  | Pump |  |  | Not Applicable |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Sludge/Scum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Sludge/Scum Accumulation"] | YES | None | [17 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance |  | 12/18/2020 | Jan 1 1900 8:30AM
10/01/2020 |  | RoutineScheduled | 11-118-0070 | Charles City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | GeoEnvironmental Services, Inc. | 1942001010 | Peter | Mamunes | 1.000000 | 1000 |  |  | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["SludgeScum Accumulation","Level Sensor Operation","Effluent Screens","Control Operation","BlowerCompressorAerator Operation","Dispersal System Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 10/09/2020 | Jan 1 1900 3:30PM
09/28/2020 |  | RoutineScheduled | 2006-143-0199 | Henrico | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Henrico | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Ecoflo | Ecoflo | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Attached Growth Medium" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | ["Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Control Operation" ,"Distribution Pump Operation" ,"Attached Growth Medium"] | YES | [15 empty] | Will be sent separately | Inspected | Few roots on septic tank inlet wedge lid. Pod #1 has a cracked roof. Junction box is broken on pump vault. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
02/03/2020 |  | Routine, Scheduled | 033-10-014-SWP | Caroline County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Ware, Michele P | 1942001165 | Michele | Ware |  |  | Septic Tank Only | Septic Tank Only | None | None | None | None |  |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | [18 empty] | [Comments]: Sludge Level Septic Tank: 3" | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/05/2020 | 08:31 AM
03/11/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS should now return to normal function after having provided the above stated routine maintenance. | Paid | EHD - Fairfax | MCKIM, STEPHEN E | 1934000043 | STEPHEN | MCKIM |  |  | Septic Tank Only | Septic Tank Only | None | None | None | None | [21 empty] | [Pumpout Comments]: Microfast septic and atu sides pumped out | This AOSS should now return to normal function after having provided the above stated routine maintenance. |  | 03/12/2020 | Jan 1 1900 10:00AM
09/17/2020 |  | RoutineScheduled | 08-142-0120 | Hanover | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Delta Whitewater | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | YES | [17 empty] | Inspection port fixed, main line and component replacement done 9/29/20 | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 09/24/2020 | 12:00 AM
02/26/2020 |  | Follow-Up | 179-18-0070-SR | Stafford County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001350 | Mike | Cook | 1.000000 |  | None | None | Gravity | Distribution Box | [15 empty] | 25.000000 | [8 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/03/2020 | 11:00 AM
09/21/2020 |  | Reportable Incident | 175-17-0438 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green | [9 empty] | ["Level Sensor (Float) Operation"] | ["Level Sensor (Float) Operation"] | [18 empty] | Replaced low water float. | This AOSS should now return to normal function after having provided the above state routine maintenance |  | 09/21/2020 | 10:30 AM
04/22/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | SES MidAtlantic LLC | 1942001203 | James | Green | 1.000000 |  | Delta Environmental Products, DF Series | Delta Environmental Products, DF Series | Pump | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. Needs new Zoner. | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 |  | 04/15/2021 | 09:00 AM
08/19/2020 |  | Routine/Scheduled | 033-08-0152-SP | Caroline | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1500 | Biomicrobics MicroFAST | None | Pump | Drip | Drip Tubing | None | 450.000000 |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | Musty | Clear | [15 empty] | Routine service conducted. Processing / trash tank - normal operating level - compressor serviced. Discharge tank - normal operating level - discharge pump serviced, float sensors and controls operating properly. Drip - manual headworks serviced - drip screen serviced, drip laterals flushed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 08/26/2020 | 07:40 AM
05/08/2020 |  | Pump-Out Only |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | POWELLS PLUMBING, INC. | 1942001036 | Kurt | Holthaus |  |  | Microfast | [6 empty] | ["Sludge/Scum Accumulation"] | ["Sludge/Scum Accumulation"] | N/A | [17 empty] | Pumped Microfast | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 06/19/2020 | 02:41 PM
02/19/2020 |  | Routine, Scheduled | 228-04-1027 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Virginia Beach | R & K Septic, Inc. |  | John | Butt, Jr |  |  |  |  | Pump | Distribution Box |  | None |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] |  |  | 12.11 | 7.500000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/19/2020 | Jan 1 1900 8:30AM
08/11/2020 |  | Follow-Up |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim |  |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | All risers were sealed up and ground water is not making it into the risers | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/14/2021 | 04:27 PM
03/19/2020 |  | Routine, Scheduled | 179-07-0319-SWP | Stafford County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001350 | Mike | Cook | 1.000000 |  | Puraflo | None | Pump | Distribution Box | Aggregate Trench |  |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/01/2020 | 06:33 AM
04/22/2020 |  | Routine/Scheduled | 136-10-0156 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | EcoPod | None | Pump | Distribution Box | Aggregate Trench | None |  |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | In the Discharge Tank, the Floats were not properly secured, and the wiring had been installed int the side of the Riser; the Seals in the Distribution Box had dirt, roots, and water leaking/intruding into the Box D-Box seals replaced - 05/07/2020 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/27/2020 | 10:06 AM
06/09/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Best 1 | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | The blower alarm was not functioning. The fuse was replaced and the alarm is functioning as designed now. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/27/2021 | 01:26 PM
05/01/2020 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Eco Virginia | 1942001235 | William | Poindexter | 1.000000 |  | none | none | Pump | Gravity | Pad | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 |  | 06/03/2021 | 05:53 AM
05/19/2020 |  | RoutineScheduled | 12-142-0139 | Hanover | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Clearstream |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | YES | [16 empty] | Pumped Out | Replaced Clearstream blower 05/19/2020 | This AOSS should now return to normal function after having provided the above state routine maintenance. |  |  | 12:00 AM
10/23/2020 |  | Initial Visit |  | Montgomery | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Payment | EHD - New River | MSS INC |  | Tim | Conner | 1.000000 | 1000 GALLONS | MICROFAST |  | Gravity | Gravity | Trenches | Not Applicable |  | ["on"] | ["on"] | YES | Musty | Clear | [5 empty] | 11/13/2020 | Sample Chamber | [6 empty] | Attached to this report | Inspected | TANK NEEDS TO BE PUMPED & CLEANED BLOWER NEEDS TO BE REPLACED | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 11/13/2020 | 12:00 PM
05/04/2020 |  | RoutineScheduled | 101-06-0097 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark | [9 empty] | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 06:55 AM
08/28/2020 |  | Reportable Incident | 10-142-0276 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Old Dominion Onsite, Inc. | 1942001549 | Russell | Revis | [11 empty] | N/A | [17 empty] | responded to call about alarm. System had caught itself up by the time we got there and was functioning properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 08/28/2020 | Jan 1 1900 8:09AM
02/26/2020 |  | Routine, Scheduled | 06-160-0331 | Montgomery County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - New River | Conner, Timothy Wayne | 1942001003 | Timothy | Conner | 1.000000 | 1000 | Microfast | None | Gravity | Distribution Box | Aggregate Bed | None | [21 empty] | [Comments]: EVERYTHING APPEARS TO BE FUNCTIONING PROPERLY AT THIS TIME. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/10/2020 | 09:45 AM
10/14/2020 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintanence requirements | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | Best 1 | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | An inspection on a conventional gravity septic system. The state requires that all conventional septic tanks must be pumped out every 5 years and filed with the state and county . There is a cleanout near the house. The sewer line was camera snaked and was clear. The septic tank was 14" under the ground. The tank lid was dug up and pumped out. Tank was inspected for any leaks or cracks none were found. The conveyance line was camera snaked and was clear. The 9 port plastic d-box was ground level and broken. It will need to be replaced. All 8 header lines were camera snaked. The header lines from 2-8 were crushed anywhere from 4 feet to 6 feet out from the d-box. They will also need to be corrected. the drain field was probed and dry. At time of inspection septic system was not in working condition. | This AOSS is not functioning as designed or in accordance with the performance/maintanence requirements |  | 04/14/2021 | 04:27 PM
12/29/2020 |  | Follow-Up | SWP-02-230 | Stafford | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Pad | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Resealed all risers. Resealed pump tank wedge lid. Resealed pump tank outlet pipe. Resealed leaking knockout on pump tank. Resealed septic tank inlet pipe. Re-plumbed recirc pipe with new union. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
11/25/2020 |  | Routine/Scheduled | 2008-143-0014 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Henrico | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | Puraflo | None | Pump | None | Aggregate Bed | None | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | Musty | Clear | [15 empty] | Routine Service Primary Septic Tank - normal level - effluent screen serviced. Pump Tank - normal level - pump, float sensors & controls operating properly. PuraFlo Modules - FOUR - Peatmoss Good - raked / turned all modules. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 11/30/2020 | 08:30 AM
06/12/2020 | Alternative | RoutineScheduled | 166-04-608 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers |  |  | joel | pinnix | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
12/13/2020 |  | RoutineScheduled | 061-17-321 | Fauquier | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Rappahannock-Rapidan | Wastemaster Inc |  | Timothy | Jenkins | 2.000000 |  | ATU |  | Pump | Gravity | Drip |  |  | [] | [] | [19 empty] | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. |  | 01/14/2021 | 09:05 AM
03/12/2020 |  | RoutineScheduled | 107-00-0606 (LEGACY ALT. SYSTEM) | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Onsite Wastewater Services - May Supply | 1942001022 | Sara | Tusing | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Pressure | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 05/28/2021 | 05:41 AM
12/03/2020 |  | Routine, Scheduled | 124-STS-2379 | Fairfax | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Sandfilter, Non-recirculating |  |  |  |  | UV Light |  | ["Disinfection","Effluent Screens"] | ["Disinfection","Effluent Screens"] |  | Good | Clear | 7.100000 | 16.100000 |  |  |  | 12/03/2020 | Discharge | 2.000000 |  | 66.000000 | 2.000000 |  |  |  |  | Pump 1 Amps 11.04 ETM 26 hrs Cycles 534 Pump 2 Amps 11.21 ETM 25 hrs Cycles 523 Septic Sludge 1" Scum 0 Pump Sludge 0 Scum 0 | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12/03/2020 | Jan 1 1900 1:00PM
06/05/2020 |  | RoutineScheduled | 107-06-0478 | Augusta | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central Shenandoah | Hunter E. Ayres, General Contractor | 1942001166 | Hunter | Ayres | 1.000000 | 1500 | Biomicrobics Microfast |  | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","SludgeScum Accumulation"] | NA | [16 empty] | Pumped Out | Control panel functioning properly. No apparent leaks in system or drain field area. System pumped and cleaned. Installed new blower. Lids properly secured | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 06/20/2020 | 12:00 AM
03/17/2020 |  | Routine, Scheduled | SD-07-475 | Fauquier County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 2.000000 |  | Delta Environmental Products, DF Series | None | Pump | Drip | Drip Tubing |  |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","SludgeScum Accumulation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [18 empty] | [Comments]: Atu panel had alarmed yesterday. Today, air pump was not running and alarm bulb was burnt out. Installed new air pump and LED alarm bulb. Ants had started chewing on air sample tube (for alarm). Tube not leaking yet. Added black tape as layer of protection. Spin filter was very dirty and crushed. Replaced filter and verified both solenoids were working. Owner says no pump tank alarms in past year. Pump tank and septic tank need pumped out asap for excessive sludge accumulation. Owner has appointment with local pumper for Friday. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/18/2020 | 12:54 PM
07/03/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/27/2021 | 01:26 PM
02/06/2020 |  | Routine, Scheduled |  | Loudoun County | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Paid | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | None | None | Pump | Distribution Box | Aggregate Trench | [22 empty] | [Comments]: Pump tank needs pumped out | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 03/02/2020 | 04:43 AM
05/02/2020 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 | Pending Payment | EHD - Loudoun | WasteMaster, Inc. | 1942001062 | Tim | Jenkins | 1.000000 |  | none | none | Gravity | Gravity |  | Chlorination |  |  |  | NA | [5 empty] | 2.200000 |  |  |  |  | 0.000000 |  |  |  |  | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 |  | 06/21/2021 | 10:37 AM
09/09/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | SES MidAtlantic LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Drip | UV |  | ["Effluent Screens" ,"Auxiliary Filter" ,"Disinfection"] | ["Disinfection" ,"Auxiliary Filter" ,"Effluent Screens"] | YES | [7 empty] | 09/09/2020 |  | 25.000000 |  | 1600.000000 |  |  |  | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/15/2021 | 09:00 AM
04/10/2020 |  | RoutineScheduled |  | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Ashleys Septic Service | 1836776 | Shane | Majewski | 1.000000 | 1200 |  |  | Pump | Gravity | Trenches | Not Applicable | 600.000000 | ["Distribution Pump Operation"] | [] | NA | [6 empty] | sample | 04/10/2020 | Sample Chamber | 24.000000 |  |  | 17.900000 |  |  |  | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 04/10/2020 | 12:00 AM
08/31/2020 |  | Reportable Incident |  | Virginia Beach | This AOSS should now return to normal function after having provided the above state routine maintenance | Pending Payment | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [9 empty] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation"] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation"] | N/A | [17 empty] | Replaced pump | This AOSS should now return to normal function after having provided the above state routine maintenance |  | 08/31/2020 | Jan 1 1900 6:00PM
02/21/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Fairfax | BLEVINS, JOEL R, SR | 1934000415 | JOEL | BLEVINS |  |  | Microfast | Septic Tank Only | None | None | None | None |  | ["None"] | ["None"] | [8 empty] | 02/21/2020 |  | 175.000000 | [5 empty] | Attached to this report |  | [Lab Comments]: Notified homeowner to not put any ails or grease in the system and we will take another sample in 30 days. [Comments]: Compressor is strong, pad is dry and cleaned the air filter. No sludge build up in tank. Grade was lowered over some of the pad for landscaping. Seven of the round boxes are above grade in grass area. Took water sample | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/05/2020 | Jan 1 1900 10:11AM
09/17/2020 |  | Reportable Incident |  | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [9 empty] | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | Replaced pump and on/off float. Replaced the aerator hose bib. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 09/24/2020 | Jan 1 1900 4:45PM
11/25/2020 |  | Routine, Scheduled | 175-14-0220 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | EcoPod |  | Pump | Drip | Drip Tubing | UV Light |  | ["Blower/Compressor/Aerator Operation","Disinfection"] | ["Blower/Compressor/Aerator Operation","Disinfection"] |  | Acceptable | Clear | [15 empty] | Spin filter cleaned. Pump Amps 7.02 ETM 972 Cycles 8869 Water Meter Reading 202430 Septic Sludge 2" Scum 2" ATU Sludge 4" Scum 2" Pump Sludge 3" Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 11/25/2020 | 09:05 AM
04/15/2020 |  | Routine, Scheduled |  | Warren County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Lord Fairfax | Cubbage, Harrison Lee, II | 1942001021 | Harrison | Cubbage | 1.000000 | 1500 | Septic Tank Only | Orenco Advantex | Gravity | Distribution Box | Aggregate Trench | None |  | ["Control Operation","Level Sensor Operation"] | ["Control Operation","Level Sensor Operation"] |  | Musty | Clear | [15 empty] | [Comments]: Reconnected float to float tree Recirc Pump- Off 19.7min On .3min ETM-3338Hr Cycle Count-99999 SLudge/Scum Accumulations: Comp.1-6"/2" Comp.2- 6"/0" | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/24/2020 | 02:28 PM
12/14/2020 |  | Routine, Scheduled | 175-90-0354 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green |  |  |  |  | Pump | Manifold | Aggregate Trench | None |  | ["Effluent Screens"] | ["Effluent Screens"] | [18 empty] | Pump Amps 8.40 Septic Sludge 7" Scum 0 Pump Sludge 2" Scum 0 Demand control panel. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 12/14/2020 | 11:42 AM
03/03/2020 |  | Routine, Scheduled | 16-163-0068 | New Kent County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chickahominy | Madison Environmental LLC |  | Larry | Madison, Jr. |  |  | Clearstream ATU |  | Pump | Distribution Box |  |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/03/2020 | Jan 1 1900 3:15AM
03/17/2020 |  | Routine, Scheduled | SWT-05-533 | Stafford County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Biomicrobics MicroFAST | None | Pump | Drip | Drip Tubing |  |  | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | [18 empty] | [Comments]: We recommend replacing the EZ Set lid on the septic tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/06/2020 | 02:45 PM
08/21/2020 |  | RoutineScheduled |  | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Ashleys Septic Service | 1930332 | Shane | Majewski | 1.000000 | 1200 |  |  | Pump | Gravity | Trenches | Not Applicable |  | ["None"] | ["None"] | YES | [16 empty] | Pumped Out | Maintenance Inspection- Distribution is manifold | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 08/27/2020 | Jan 1 1900 12:01PM
01/29/2020 |  | Routine, Scheduled |  | Albemarle County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Blue Ridge | CLARK, MICHAEL J | 1934000023 | MICHAEL | CLARK |  |  | Septic Tank Only | Septic Tank Only | None | None | None | None |  |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/09/2020 | 04:58 AM
04/21/2020 |  | Routine, Scheduled | 196.87.297 | Westmoreland County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers |  |  |  |  | 2.000000 | 2500 |  |  | Pump | Manifold | Elevated Sand Mound |  |  | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [5 empty] | 65.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/21/2020 | 05:00 PM
04/01/2020 |  | Routine, Scheduled |  | Loudoun County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | None | None | Pump | Distribution Box | Aggregate Trench | [23 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/12/2020 | 02:21 PM
01/15/2020 |  | Initial Visit | SHUN-B8XMDX | Suffolk | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Western Tidewater | Farmer’s Septic Service, Inc. |  | Ross | Cole | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | [Comments]: Serviced system. Checked the pump, panel, & floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. The Salcor UV is not working - needs new circuit board. Visible wetness on the drainfield - most likely from rain. The timer is set to 3.75 minutes every 3 hours. Did not take initial sample. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 01/15/2020 | Jan 1 1900 12:00PM
11/10/2020 |  | RoutineScheduled | 98-184-5001 | Scott | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | EHD - Lenowisco | [16 empty] | None | Clear | 8.000000 | 6.000000 |  | 0.000000 | [12 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
02/04/2020 |  | Routine, Scheduled | SWP-04-470 | Spotsylvania County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | None | Pump | Distribution Box | Aggregate Trench |  |  | ["Attached Growth Medium"] | ["Attached Growth Medium"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/02/2020 | 11:52 AM
06/08/2020 |  |  | 02-142-0801 | Hanover | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Advantex | [6 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens"] | [17 empty] | Pumped Out | RSV was clogged not allowing water to flow to the discharge tank. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 09/17/2020 | 12:00 AM
11/02/2020 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump | Drip | Elevated Sand Mound | UV Light |  | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  | 3.6 | 7.680000 | 4.600000 | [13 empty] | Replaced UV bulb | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 11/02/2020 | Jan 1 1900 9:45AM
01/16/2020 | Alternative | Routine, Scheduled | 234-14-285 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesapeake | R & K Septic, Inc. |  | John | Butt, Jr |  |  | Clearstream ATU |  | Pump | Drip | Elevated Sand Mound | UV Light |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] |  |  | 2.16 | 7.020000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/16/2020 | Dec 30 1899 10:30AM
03/30/2020 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump | Distribution Box | Aggregate Bed | None |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  |  | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/30/2020 | Jan 1 1900 1:30PM
12/08/2020 |  | RoutineScheduled | 2037-96-153 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Wastemaster Inc |  | Timothy | Jenkins | 2.000000 |  | Recirculating Sand Filter |  | Pump | Gravity | Discharge | Chlorination |  | [] | [] |  | Musty | Clear | 6.900000 |  |  | 1.900000 | [12 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12/16/2020 | 02:00 PM
09/11/2020 |  | Follow-Up | 069050485 | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Combs Wastewater Management LLC | 1942001353 | Amy | Combs | 2.000000 | 1000 |  |  | Pump | Pressure | Drip | Not Applicable | 450.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12/31/2020 | 12:00 AM
05/08/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/27/2021 | 01:26 PM
12/06/2020 |  | RoutineScheduled | 139-04-0265 | Greene | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Alternative Systems Inspection Services, LLC | 1942001047 | Wesley | Basore | 1.000000 | 500 | Biomicrobics |  | Pump | Pressure | Drip | Not Applicable | 150.000000 | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation","Effluent Screens"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12/18/2020 | 06:10 PM
06/22/2020 |  | RoutineScheduled | 2008-143-0177 | Henrico | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Henrico | Stamie E. Lyttle Co. | 1942001470 | Eric | Tambourine | [9 empty] | [] | [] | [19 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 06/22/2020 | 12:00 AM
10/08/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | SES MidAtlantic LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/15/2021 | 09:00 AM
05/14/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/14/2021 | 04:27 PM
05/04/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Onsite Wastewater Services - May Supply | 1942001022 | Sara | Tusing | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Inspection by ds | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/28/2021 | 05:41 AM
03/13/2020 |  | Reportable Incident |  | Fairfax County | This AOSS should now return to normal function after having provided the above stated routine maintenance. | Paid | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green | [9 empty] | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | [18 empty] | [Comments]: Installed new compressor & concrete casing lid. | This AOSS should now return to normal function after having provided the above stated routine maintenance. |  | 03/13/2020 | Jan 1 1900 2:00PM
04/06/2020 |  | Routine, Scheduled | 136-04-0645 | Gloucester County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers | Farmer’s Septic Service, Inc. |  | Ross | Cole | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | [Comments]: Serviced system. Checked the pump, panel, & floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. Replaced the old Clearstream top. The alarm light on the Clearstream panel is bad. The septic tank needs pumping - 18" of sludge and pump the scum off the top of the Clearstream tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/06/2020 | 12:00 PM
09/15/2020 |  | RoutineScheduled | 187100086 | Warren | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Lord Fairfax | Onsite Wastewater Services - May Supply | 1942001627 | Drew | Shull | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Pressure | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | System pumped by First Choice Septic Service Inc 9/15/2020 | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/28/2021 | 05:41 AM
03/19/2020 |  | Follow-Up |  | Loudoun County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | None | None | Gravity | [24 empty] | [Comments]: A new drain field line, new d-box,and part of the conveyance line was installed. A concrete riser and filter were installed on the outlet side of the septic tank. Mr Tolley and Loudoun County Health dept inspected. At this time the septic system is in working condition. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/12/2020 | 02:21 PM
01/15/2020 |  | Routine, Scheduled | 107-06-0888 | Augusta | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Central Shenandoah | Cubbage, Harrison Lee, II | 1942001021 | Harrison | Cubbage | 1.000000 | 1000 | Septic Tank Only | Ecoflo | Pump | Drip | Drip Tubing | None |  | ["Attached Growth Medium","Control Operation","SludgeScum Accumulation"] | ["Control Operation"] |  | Musty | Clear | [5 empty] | 01/15/2020 | Pump Tank | 47.000000 | [5 empty] | Attached to this report |  | [Comments]: Ecoflo Peat is in need of replacing. Will also need to pump septic tank prior and recommend a riser installation at that point and filter is able to add Drip System- Off 2hrs On 10min All floats and drainfield is fine | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. |  | 01/31/2020 | 10:52 AM
05/19/2020 |  | Routine, Scheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Puraflo |  |  | Manifold |  | None |  | ["Effluent Screens"] | ["Effluent Screens"] | [18 empty] | Pump Amps 7.45 ETM 561.19 Pump Amps 7.55 ETM 50340 Pump Amps 12.85/13.25 Septic Sludge 11" Scum 0 Pump Sludge 3"/1" Scum 0/0 No pumping necessary at this time. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 05/19/2020 | Jan 1 1900 12:22PM
07/23/2020 |  | RoutineScheduled | SD-12-167 | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Wastemaster Inc |  | Timothy | Jenkins | 3.000000 |  | ATU | ATU | Pump | Gravity | Discharge | Chlorination |  | [] | [] |  | Musty | Clear | 7.300000 |  | 24.000000 | 2.200000 | [12 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 03:10 PM
10/15/2020 |  | Initial Visit |  | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Chesapeake | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | Serviced system. Checked the pump, panel, & floats (ok). Cleaned the filter in the Clearstream, cleaned the screen in the spinfilter, and cleaned the UV bulb. Changed the diffuser in the Clearstream and changed the filter in the aerator. Replaced the ballast in the UV panel. The timer is set to 7 minutes every 2 hours. Took initial BOD & Fecal samples. Spinfilter return hose still discharging in the pump tank - needs to be addressed. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 10/15/2020 | Jan 1 1900 12:00PM
02/25/2020 |  | Routine, Scheduled | 179-18-0319-SP | Stafford County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Orenco Advantex | None | Pump | Distribution Box | Aggregate Trench |  |  | ["Attached Growth Medium","Effluent Screens","Recirculation Pump"] | ["Attached Growth Medium","Effluent Screens","Recirculation Pump"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/06/2020 | 02:45 PM
06/19/2020 | Alternative | Routine/Scheduled | 157-18-0084 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | Serviced system. Checked the pump, panel, & floats (ok). Cleaned the filter in the Clearstream and cleaned the UV light bulb. Changed the diffuser in the Clearstream and changed the filter in the aerator. The timer is set to 2.5 minutes every 1.5 hours. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 06/19/2020 | 12:00 PM
03/16/2020 |  | RoutineScheduled | 182-06-0046 | Rockingham | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Central Shenandoah | Onsite Wastewater Services - May Supply | 1942001022 | Sara | Tusing | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/28/2021 | 05:41 AM
03/13/2020 |  | Routine, Scheduled |  | Loudoun County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | None | None | Gravity | [24 empty] | [Comments]: Sale inspection on a conventional pump septic system. The septic control panel is outside and is a timed dose . There is one pvc cleanout near the house. The sewer line was camera snaked and was clear. The septic tank has plastic risers on both inlet and outlet. The tank was sludge judged and does not need pumped out. There is a filter on the outlet side of the tank that was cleaned. The manufacture recommends cleaning the filter every 6 months. And the state requires that the septic tank be pumped out every 5 years and filed with the state and county. The pump tank, pump, floats and force main were inspected. The plastic monster box is at ground level it has 7 drain field lines. The header lines were camera snaked and the drain field was probed. At time of inspection all components are in working condition. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/12/2020 | 02:21 PM
05/13/2020 |  | Follow-Up | 179-10-0072-STWP | Stafford | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | 20 Replaced 1? check valve for pump, sealed top seam of PT on outlet end (wood side corner), resealed wedge lid, bleached cleaned system and had all tanks pumped out by others. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
07/06/2020 |  | RoutineScheduled | 033-17-0197-SP | Caroline | This AOSS is not functioning as designed or in accordance with the performance/Maintenance requirements | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Dispersal System Operation"] |  | NA | [15 empty] | Will be sent separately | Inspected | Effluent is surfacing at the lower area of the mound. We recommend contacting an Alternative Onsite Soil Evaluator (AOSE) for repair options. | This AOSS is not functioning as designed or in accordance with the performance/Maintenance requirements |  | 04/09/2021 | 03:25 PM
01/13/2020 |  | Routine, Scheduled | 07-173-066 | Prince Edward County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Piedmont | Taylor, Penny | 1942001028 | Penny | Taylor | 2.000000 | 2000 | Septic Tank Only | Eljen Geotextile Sandfilter | Pump | Manifold | Elevated Sand Mound | None | 450.000000 | ["Effluent Screens","SludgeScum Accumulation"] | ["Control Operation","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | [18 empty] | [Pumpout Comments]: Pumped and cleaned the septic/trash tank | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/17/2020 | Jan 1 1900 7:23AM
08/31/2020 |  | RoutineScheduled | 043170189 | Clarke | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Lord Fairfax | Greenway Engineering | 1942001008 | Jeremy | Ferguson | 1.000000 | 1500 | microfast | none | Pump | Pressure | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","SludgeScum Accumulation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 08/31/2020 | 04:50 PM
03/26/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | EZ Treat Sandfilter |  | Pump |  |  | None |  | ["Effluent Screens"] | ["Effluent Screens"] |  | Good | [16 empty] | [Comments]: Pump 1 Amps 12.10Pump 2 Amps 16.11/16.40Septic Sludge 4" Scum 1"ATU Sludge 9" Scum 0.50Pump Sludge 3" Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/26/2020 | Jan 1 1900 12:10AM
08/08/2020 |  | RoutineScheduled |  | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Fairfax | Wastemaster Inc |  | Timothy | Jenkins | 2.000000 |  | PuraFlo |  | Pump | Gravity | Discharge | Chlorination |  | [] | [] |  | Musty | Clear | 7.600000 |  |  | 2.200000 | [11 empty] | Misfiled report. Report was filed under owner's address, but the SDS is in Prince William County. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 09/02/2020 | Jan 1 1900 2:45PM
08/31/2020 |  |  |  | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001301 | Joshua | Hott | [9 empty] | ["Effluent Screens"] | ["Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
11/18/2020 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump | Distribution Box | Gravel-Less Trench | UV Light |  | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 11/18/2020 | Jan 1 1900 1:00PM
05/08/2020 | Alternative | Routine/Scheduled | 41583 | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | POWELLS PLUMBING, INC. | 1942001036 | Kurt | Holthaus | 1.000000 | 1000 |  |  | Pump | Manifold | Aggregate Trench |  | 450.000000 | ["Effluent Screens"] | ["Effluent Screens"] | N/A | [17 empty] | Annual Inspection - Serviced effluent screen(s). | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 05/12/2020 | 03:04 PM
03/06/2020 |  | RoutineScheduled | 133 16 0039 | Franklin | This AOSS is functioning as designed and in accord | Approved | EHD - West Piedmont |  |  |  |  | 1.000000 | 1500 |  | Orenco Advantex | Pump | Distribution Box | Aggregate Trench | None |  | ["Effluent Screens"] | ["Effluent Screens"] | [18 empty] | [Pumpout Comments]: Not needed at this time [Comments]: Septic tank 1" scum 6-8" sludge, Recirc zone 7" sludge, discharge zone 10" sludge, All float switches opperational, pumps operational good spray pattern, no big alarms in history aside from a few high water use events, | This AOSS is functioning as designed and in accord |  | 03/07/2020 | 02:07 PM
04/28/2020 |  | RoutineScheduled | 177-18-0278-SWP | Spotsylvania | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"Control Operation" ,"Dispersal System Operation" ,"Auxiliary Filter" ,"Attached Growth Medium" ,"BlowerCompressorAerator Operation"] | ["SludgeScum Accumulation" ,"Level Sensor Operation" ,"Septic Tank Baffles" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"BlowerCompressorAerator Operation" ,"Control Operation" ,"Attached Growth Medium" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | Sludge in FAST side is toilet paper, needs a pump out. BOD collected, waiting on results. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
05/04/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/27/2021 | 01:26 PM
09/03/2020 |  | Reportable Incident | 175-13-0135 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green | [9 empty] | ["Disinfection"] | ["Disinfection"] | [18 empty] | Installed new head works on UV Light unit. | This AOSS should now return to normal function after having provided the above state routine maintenance |  | 09/03/2020 | 04:00 PM
06/15/2020 |  | RoutineScheduled | 132-07-0032 | Fluvanna | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Blue Ridge | All In Septic Services | 1942001442 | Dennis | Mitchell | 1.000000 | 1500 | Norweco |  | Gravity | Gravity | Discharge | Chlorination |  | ["Disinfection"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Disinfection","SludgeScum Accumulation"] | NA | None | Cloudy | [5 empty] | 06/22/2020 | Sample Chamber |  |  |  |  | 0.100000 |  | Attached to this report | Inspected |  | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 06/24/2020 | 05:00 PM
06/10/2020 |  | Reportable Incident |  | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [9 empty] | ["Blower/Compressor/Aerator Operation","Control Operation"] | ["Blower/Compressor/Aerator Operation","Control Operation"] | N/A | [17 empty] | Replaced aerator | This AOSS should now return to normal function after having provided the above state routine maintenance |  | 06/10/2020 | Jan 1 1900 12:45PM
05/26/2020 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump | Distribution Box |  | None |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  | 14.07 | 7.520000 | 6.300000 | [13 empty] | Replaced alarm bulb | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 05/26/2020 | Jan 1 1900 3:45PM
05/12/2020 |  | RoutineScheduled | -STS-90066 | Spotsylvania | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 2.000000 |  | EZ Treat Sandfilter | none | Pump | Gravity | Drip | Not Applicable |  | ["Attached Growth Medium" ,"Auxiliary Filter" ,"Control Operation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | ["SludgeScum Accumulation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Attached Growth Medium" ,"Auxiliary Filter" ,"Control Operation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles"] | YES | [15 empty] | Will be sent separately | Inspected | A few roots at inlet pipe. Alarm is burned out. No power making it to alarm bulb and horn does not work. Check valve not holding on drip pump. Homeowner is working with AOSE for new system. | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
01/20/2020 |  | Reportable Incident |  | Essex County | This AOSS should now return to normal function after having provided the above stated routine maintenance. | Paid | EHD - Three Rivers | PINNIX, JOEL S | 1934000193 | JOEL | PINNIX |  |  | Septic Tank Only | Septic Tank Only | None | None | None | None | [21 empty] | [Comments]: High water alarm due to clogged pump intake. Cleaned pump intake - provided routine service. May have drainfield (drip) issues - noticed wet areas in drainfield. Need to reevaluate once system is operating normally. | This AOSS should now return to normal function after having provided the above stated routine maintenance. |  | 01/23/2020 | 10:15 AM
03/28/2020 | Alternative | RoutineScheduled | 104-02-0401 | Amherst | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | WAUGH, IAIN C | 1942001512 | IAIN | WAUGH | 1.000000 | 2500 | BioMicrobics Micro Fast 0.5 |  | Pump | Pressure | Drip | Not Applicable |  | ["Control Operation","Dispersal System Operation"] | ["Control Operation","Dispersal System Operation"] | [18 empty] | [Pumpout Comments]: Taylor's Septic Service pumped out the fast treatment tank on both side (2 of the 3 6" Black Tubes over fast unit to remove sludge. Approx 1" sludge remains [Comments]: 1. Moved Zoner Valve box to recenter over unit 2. Taylors Septic Pumped out 1200 Galllons from the Fast Treatment unit and cleaned and backwasd 3. Replaced Fast Blower Control Panel with updated | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 03/28/2020 | 09:17 PM
11/19/2020 |  | Routine/Scheduled | 13-174-0178 | Prince George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Crater | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 2.000000 |  | Multiflo ATU |  | Pump |  |  |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 11/19/2020 | Jan 1 1900 10:00AM
10/05/2020 |  | Follow-Up | 175-05-0891 | Prince William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green | [9 empty] | ["None"] | ["None"] | NO | [7 empty] | 10/05/2020 | Sample Chamber | 57.000000 | [7 empty] | Puraflo BOD 57 | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 10/05/2020 | 04:00 PM
03/20/2020 |  | Routine, Scheduled | S-04-111-0070 | Botetourt County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Alleghany-Roanoke | Advanced Environmental & Septic, LLC | 1934000259 | Rodney | Rice | 1.000000 |  | Orenco Advantex |  | Pump | Distribution Box | Aggregate Trench | None |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/20/2020 | Jan 1 1900 12:45AM
12/16/2020 |  | RoutineScheduled | 157-15-106 | Rappahannock | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Randy's Complete Water & Wastewater Services | 1942001335 | Randy | Gray | 1.000000 |  | puroflo |  | Pump | Gravity | Trenches |  | 75.000000 | ["None"] | ["None"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12/17/2020 | 06:15 PM
11/10/2020 |  |  | 069150359 | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 2705110225 | Larry | Royston | [9 empty] | ["None"] | ["None"] | YES | [16 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12/05/2020 | 12:00 AM
08/07/2020 |  | Reportable Incident |  | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [9 empty] | ["Control Operation","Level Sensor (Float) Operation"] | ["Control Operation","Level Sensor (Float) Operation"] | N/A | [17 empty] | Replaced alarm float in Clearstream tank. | This AOSS should now return to normal function after having provided the above state routine maintenance |  | 08/07/2020 | Jan 1 1900 8:00AM
04/22/2020 |  | Routine, Scheduled | 04-120-0333A | Chesterfield County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesterfield | Madison Environmental LLC |  | Larry | Madison, Jr. |  |  | Orenco Advantex |  | Pump |  |  |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | [18 empty] | [Comments]: Repaired recirculating pump piping. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/22/2020 | Jan 1 1900 12:00PM
07/09/2020 |  | Routine/Scheduled | 18-120-0444A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. |  |  | Aqua Klear |  | Pump |  |  |  |  | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 07/09/2020 | Jan 1 1900 3:30AM
03/12/2020 |  | Routine, Scheduled |  | Prince William County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Orenco Advantex |  |  |  |  | UV Light |  | ["BlowerCompressorAerator Operation","Effluent Screens"] | ["BlowerCompressorAerator Operation","Effluent Screens"] |  | Good | Clear | [15 empty] | [Comments]: Pump 1 Amps 11.01 ETM 235h 14m Cycles 28030Pump 2 Amps 5.98 ETM 11h 0m Cycles 1123Septic Sludge 3" Scum 0.50ATU Sludge 1" Scum 0Pump Sludge 0 Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/12/2020 | 02:04 PM
03/18/2020 |  | Reportable Incident |  | Prince William County | This AOSS should now return to normal function after having provided the above stated routine maintenance. | Paid | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green | [9 empty] | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | [18 empty] | [Comments]: Installed D 80 compressor. | This AOSS should now return to normal function after having provided the above stated routine maintenance. |  | 03/18/2020 | 01:30 PM
06/15/2020 |  |  | 2006-143-0156 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Advantex |  | Pump |  |  |  |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 09/17/2020 | 12:00 AM
03/30/2020 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump | Drip | Elevated Sand Mound | UV Light |  | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  |  | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/30/2020 | Jan 1 1900 11:00AM
10/19/2020 |  | Reportable Incident | SD-06-51 | Fauquier | This AOSS should now return to normal function after having provided the above state routine maintenance | Approved | EHD - Rappahannock-Rapidan | SES Mid Atlantic | 1942001203 | Michael | Green | [9 empty] | ["Blower/Compressor/Aerator Operation"] | ["Blower/Compressor/Aerator Operation"] | [18 empty] | Installed new MicroFast blower. | This AOSS should now return to normal function after having provided the above state routine maintenance |  | 10/19/2020 | 04:00 PM
12/08/2020 |  | RoutineScheduled | 17-192-081 | Tazewell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | CLEARSTREAM |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Effluent Screens"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
10/26/2020 | Alternative | RoutineScheduled | 124-STS-2379 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Rejected | EHD - Lord Fairfax | [6 empty] | Fast | [6 empty] | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 10/26/2020 | 12:00 AM
06/23/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/27/2021 | 01:26 PM
10/14/2020 |  | Reportable Incident |  | Loudoun | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Loudoun | POWELLS PLUMBING, INC. | 1942001036 | Kurt | Holthaus | [9 empty] | ["Distribution Pump Operation"] | ["Distribution Pump Operation"] | N/A | [17 empty] | Pumped down pump chamber and replaced 3" brass gate valve. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 11/25/2020 | 12:33 PM
06/10/2020 |  | RoutineScheduled | C11-180-0049 | Roanoke | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Alleghany-Roanoke | King's Alternative Septic | 1942001094 | David | King | 2.000000 | 1500 | Orenco Advantex AX 20 RT |  | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [17 empty] | Cleaned effluent screens, checked sludge level - showing low and does not need to be pumped at this time. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 07/20/2020 | 12:00 AM
06/19/2020 |  | Reportable Incident | 109-05-0318 | Bedford | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Whitewater |  | Pump | Pressure | Drip | Not Applicable |  | [] | [] | NA | [16 empty] | Inspected |  | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 06/28/2020 | 12:30 PM
11/06/2020 |  | RoutineScheduled | {FIPSCode}-STS-22884 | Scott |  |  | EHD - Lenowisco |  |  | John | Hyder |  |  | Multi flow ATU |  | Gravity |  |  | Chlorination | 450.000000 |  |  |  | None | Clear | 7.500000 | 5.000000 |  |  | chlorine residual 0 | [10 empty] | No laboratory testing performed. Routine inspection only. |  |  |  | 12:00 AM
09/15/2020 |  | RoutineScheduled | 069120030 | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Combs Wastewater Management LLC | 1942001353 | Amy | Combs | 2.000000 | 1000 |  |  | Pump | Gravity | Trenches | Not Applicable | 600.000000 | [] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12/31/2020 | 12:00 AM
06/16/2020 |  |  | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Fairfax | FIVE STAR SEPTIC INC | 1944001248 | AARON | GOINS | [9 empty] | [] | [] | [17 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 06/16/2020 | 12:00 AM
05/20/2020 |  |  | 107-10-0114 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Inboden Environmental Services, Inc | 1942001083 | Terry | Inboden | [8 empty] | 5013.000000 | ["None"] | ["None"] |  |  |  | 7.710000 | 7.320000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 06/25/2020 | 12:00 AM
08/14/2020 |  | RoutineScheduled | 181-06-0301 | Rockbridge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Hunter E. Ayres, General Contractor | 1942001166 | Hunter | Ayres | 1.000000 | 1000 | Biomicrobics MicroFAST-1500 gal. |  | Gravity | Gravity | Trenches | Not Applicable |  | ["Auxiliary Filter","Effluent Screens"] | ["Auxiliary Filter","Effluent Screens"] | YES | [17 empty] | Filters checked and cleaned. Control panels, blower, alarms and pump functioning properly. No apparent leaks in system or drain field area. System did not need to be pumped. Lids properly secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 09/15/2020 | 09:15 PM
01/09/2020 |  | RoutineScheduled | 069050309 | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Combs Wastewater Management LLC | 1942001353 | Amy | Combs | 2.000000 |  |  |  | Pump | Gravity | Drip | Not Applicable | 600.000000 | [] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 01/13/2021 | 12:00 AM
10/29/2020 | Alternative | RoutineScheduled | 171-08-0088 | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | None | Clear | 7.250000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 11/06/2020 | 03:55 PM
05/19/2020 |  | Pump-Out Only | {FIPSCode}-STS-28098 | Clarke | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | POWELLS PLUMBING, INC. | 1942001036 | Kurt | Holthaus | [9 empty] | ["Sludge/Scum Accumulation"] | ["Sludge/Scum Accumulation"] | N/A | [17 empty] | Pumped septic. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 05/19/2020 | 02:11 PM
05/02/2020 |  | RoutineScheduled | SWP-04-344 | Stafford | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Attached Growth Medium" ,"Control Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Level Sensor Operation"] | ["SludgeScum Accumulation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Septic Tank Baffles" ,"Distribution Pump Operation" ,"Attached Growth Medium" ,"Control Operation"] | YES | [15 empty] | Will be sent separately | Inspected | Pumped out needed. Bad roots in septic tank wedge lid and pump tank wedge lid. Dug up distribution box, needs replaced. Vacuumed and augered peat in pods 3&5. Used camera to try to locate sample box; none found. Has effluent filter alarm, float not working; homeowner does not need it. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
06/04/2020 |  |  | 175-15-0457 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Pressure | Drip | UV |  | ["SludgeScum Accumulation","BlowerCompressorAerator Operation","Level Sensor Operation"] | ["BlowerCompressorAerator Operation","Level Sensor Operation"] | NA | [17 empty] | Septic-10"sludge 4"scum/ Microfast-14"sludge (Requires pump out) Pump tank-0"sludge (No pump out needed) Blower air filter cleaned/ Counts: Pump 551 ETM-181h 50m/ Peak-14 ETM-94h 32m/ High-0 ETM-0/ Zone1-259 ff-19/ Water meter-0135582.78/ Replaced 2 narrow angle floats (on & off)/ no breakout or spongy areas on the drip field. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  |  | 12:00 AM
09/08/2020 |  | Follow-Up | 175-11-0094 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green | [9 empty] | ["Level Sensor (Float) Operation"] | ["Level Sensor (Float) Operation"] | [18 empty] | Installed Clearstream float (blue). | This AOSS should now return to normal function after having provided the above state routine maintenance |  | 09/08/2020 | 04:00 PM
08/19/2020 |  | RoutineScheduled | 87-125-130 | Dickenson | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Effluent Screens"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
04/21/2020 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Pump | Distribution Box |  | None |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Recirculation Pump","Sludge/Scum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Recirculation Pump","Sludge/Scum Accumulation"] | N/A |  | 2.52 | 7.690000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/21/2020 | Jan 1 1900 1:45PM
02/28/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS should now return to normal function after having provided the above stated routine maintenance. | Paid | EHD - Fairfax | SEAMON, CHARLIE L | 1942001108 | CHARLIE | SEAMON |  |  | Septic Tank Only | Puraflo | Pump | Distribution Box | Aggregate Trench | None |  | ["SludgeScum Accumulation"] | [19 empty] | [Comments]: Performance Inspection: Puraflo Pad System. Septic tank-4"sludge 0"scum/ Pump tank-4"sludge. Recommend pump out of the pump tank due to sludge close to the pump intake. P1 cnts-251,377 ETM-150.04/ P2 cnts-171,103 ETM-147.03/ Effluent filter does not require cleaning at this time. Puraflo media appears to be good at this time. | This AOSS should now return to normal function after having provided the above stated routine maintenance. |  | 03/18/2020 | Jan 1 1900 5:59AM
12/28/2020 |  | Routine, Scheduled | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Biomicrobics MicroFAST |  |  |  |  | UV Light |  | ["Blower/Compressor/Aerator Operation","Dispersal System Operation","Distribution Pump Operation"] | ["Blower/Compressor/Aerator Operation"] |  | Acceptable | Clear | [15 empty] | Drainfield area needs mowing. Check valves & UV Bulb needs replacing. Pump Amps 9.76 ETM 234 hrs Cycles 1840 Water Meter Reading 119600 Septic Sludge 5" Scum 2" ATU Sludge 6" Scum 0 Pump Sludge 1" Scum 0 On 8 mins 15 secs Off 1 hr 55 mins | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 12/28/2020 | Jan 1 1900 12:41PM
07/01/2020 |  | RoutineScheduled | SWP-01-113 | Spotsylvania | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Distribution Pump Operation" ,"Dispersal System Operation"] | ["Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Alarm call by owner. Cleaned clogged spin filters & pump. Performed annual inspection. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/09/2021 | 03:25 PM
05/11/2020 |  | RoutineScheduled | 15-192-135 | Tazewell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. |  | Denny | Deel |  |  | NORWECO |  | Pump | Pressure | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens","Distribution Pump Operation","Level Sensor Operation"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
02/05/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Biomicrobics MicroFAST |  | Pump | Drip | Drip Tubing | UV Light |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] |  | Good | Clear | [5 empty] | 02/05/2020 |  | 23.000000 |  | 33.000000 | [5 empty] | [Comments]: Spin filter cleaned.Pump Amps 9.73 ETM 39h 17m Cycles 333Water Meter Reading 23000Septic Sludge 4" Scum 10"ATU Sludge 4" Scum Pump Sludge 0 Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/05/2020 | Jan 1 1900 11:38AM
04/03/2020 |  | RoutineScheduled | 43359 | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | ["None"] | ["None"] |  | None | Clear | 7.500000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 06/30/2020 | 12:00 AM
04/07/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Loudoun | SES MidAtlantic LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/15/2021 | 09:00 AM
06/16/2020 |  | RoutineScheduled | SD-09-61 | Fauquier | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"SludgeScum Accumulation"] | ["Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced broken vent grate for Advantex pod. Septic/recirc tank needs pumped out, owner to make arrangements. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
11/03/2020 |  | Routine/Scheduled |  | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump | Drip | Elevated Sand Mound | UV Light |  | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  | 7 | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 11/02/2020 | Jan 1 1900 11:00AM
01/13/2020 |  | Routine, Scheduled |  | Warren County | This AOSS should now return to normal function after having provided the above stated routine maintenance. | Paid | EHD - Lord Fairfax | POWELLS PLUMBING, INC. | 1942001036 | Kurt | Holthaus | 1.000000 | 1250 | Microfast |  | Pump | Drip | Drip Tubing |  | 600.000000 | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | [18 empty] | [Comments]: Annual Inspection - Serviced blower and customer replaced spin filter. | This AOSS should now return to normal function after having provided the above stated routine maintenance. |  | 01/13/2020 | 12:40 PM
02/17/2020 |  | Routine, Scheduled | 14-100-0353 | Accomack County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Eastern Shore | DUER, PETE C | 1942001051 | PETE | DUER | 2.000000 | 2000 | Septic Tank Only | Aqua Safe ATU | Pump | None | None | None |  | ["None"] | ["None"] | [18 empty] | [Comments]: Aoss Inspection. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/25/2020 | 10:30 AM
06/08/2020 |  | RoutineScheduled | SWT-01-242 | Stafford | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 |  | 04/09/2021 | 03:25 PM
01/27/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Fairfax | Hott, Joshua D. | 1942001301 | Joshua | Hott |  |  | Septic Tank Only | Septic Tank Only | None | None | None | None | [22 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/05/2020 | Jan 1 1900 10:54AM
01/20/2020 |  | Routine, Scheduled | 033-06-0481-SR | Caroline County | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Puraflo | None | Pump | Distribution Box | Aggregate Bed |  |  | ["Attached Growth Medium","Effluent Screens"] | ["Attached Growth Medium","Effluent Screens"] | [18 empty] | [Comments]: Upon arrival, there was standing water in the sample chamber. The pad did not show signs of saturation, so this may be due to seasonal weather conditions. We plan to revisit & re-evaluate during the summer in order to determine if peat replacement or a new installation will be the proper recommendation. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 02/04/2020 | 07:46 AM
08/19/2020 |  | RoutineScheduled |  | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Microfast | Pump Tank | Pump | Pressure | Drip |  |  | ["Dispersal System Operation","BlowerCompressorAerator Operation","SludgeScum Accumulation"] | ["Dispersal System Operation","BlowerCompressorAerator Operation"] | NA | [17 empty] | Septic-8"sludge 3"scum/ Microfast-14"sludge/ Pump tank-2"sludge (Septic/ Microfast tank requires pump out due to sludge levels) Blower air filter cleaned/ back flush valve stuck open, cleaned and valve started working correctly/ Counts: Pump-4272 ETM-368h 53m/ Peak-307 ETM-695h 22m/ Z1-2185 ff-42/ Z2-2202 ff-42/ High-30 ETM-0m/ Water meter-1,738,192/ Peak counts high due to issue with back flush valve. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  |  | 12:00 AM
10/21/2020 |  | RoutineScheduled | 179-15-0032-SP | Stafford | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter" ,"Attached Growth Medium" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | ["Control Operation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Auxiliary Filter" ,"Attached Growth Medium" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | YES | [15 empty] | Will be sent separately | Inspected | BOD collected, waiting on results. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
01/20/2020 |  | Routine, Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Chesapeake | R & K Septic, Inc. |  | Craig | Van Holten |  |  | Orenco Advantex |  | Pump | Distribution Box |  | None |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] |  |  |  | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/20/2020 | Jan 1 1900 9:30AM
08/14/2020 |  | RoutineScheduled | 181-07-0289 | Rockbridge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Hunter E. Ayres, General Contractor | 1942001166 | Hunter | Ayres | 1.000000 | 1000 | Biomicrobics MicroFAST-1500 gal |  | Pump | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","Effluent Screens","Control Operation"] | ["Control Operation","Auxiliary Filter","Effluent Screens"] | YES | [17 empty] | Filters checked and cleaned. New alarm buzzer installed in control panel. System did not need to be pumped. No apparent leaks in system or drain field area. Control panels returned to normal function after installation of buzzer. Pump and blower functioning properly. Lids properly secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 09/15/2020 | 08:55 PM
12/21/2020 |  | RoutineScheduled |  | Warren | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NO | [7 empty] | 12/23/2020 |  | 22.000000 | [5 empty] | Will be sent separately | Inspected | Lab Sample Normal | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/26/2021 | 09:04 AM
06/15/2020 |  | RoutineScheduled | 137-STS-25544 | Orange | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Wastemaster |  | Timothy | Jenkins | 3.000000 |  | Advantex |  | Pump | Gravity | Discharge | UV |  | [] | [] |  | Musty | Clear | 6.500000 | [12 empty] | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 06/15/2020 | 04:00 PM
01/16/2020 |  | Routine, Scheduled | 234-18-388 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesapeake | R & K Septic, Inc. |  | John | Butt, Jr |  |  | Clearstream ATU |  | Pump | Drip | Elevated Sand Mound | UV Light |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] |  |  | 3.46 | 7.990000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/16/2020 | Jan 1 1900 11:15AM
03/04/2020 |  | Routine, Scheduled |  | Mathews County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Three Rivers | Farmer’s Septic Service, Inc. |  | Ross | Cole | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | [Comments]: Serviced system. Checked the pump, panel, & floats (ok). Cleaned the filter in the Clearstream and cleaned the filter in the septic tank. Changed the diffuser in the Clearstream and changed the filter in the aerator. There are soggy patches on the drainfield - probably from rain. The timer is set to 2.5 minutes every 2 hours. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/04/2020 | 12:00 PM
09/02/2020 |  | RoutineScheduled | 153-STS-20170 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Prince William | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation" ,"Level Sensor Operation" ,"Control Operation"] | ["Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | NA | [7 empty] | 09/02/2020 |  | 8.000000 | [5 empty] | Will be sent separately | Inspected | Routine inspection and first BOD sampling. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
02/17/2020 |  | Routine, Scheduled |  | Albemarle County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Blue Ridge | ARNOLD, ARCHIE G | 1942001291 | ARCHIE | ARNOLD | 1.000000 | 1000 | Aqua Safe ATU | Septic Tank Only | Pump | Drip | Drip Tubing | UV Light | 150.000000 | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] |  | Earthy | Clear | [15 empty] | [Comments]: Changed Air Filter, Cleaned Disk & Effluent filter, flushed drip zone. 18" sludge in ATU, need to Pump-out next year. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/02/2020 | 01:40 PM
09/15/2020 |  | RoutineScheduled |  | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 4.000000 |  | Septic Tank #1 & Septic Tank #2 | EZ-Treat Recirc. / Pump Tank | Pump | Pressure | Trenches | Not Applicable |  | ["None"] | ["None"] | NO | [17 empty] | Septic Tank #1-10"sludge 8"scum/ Septic Tank #2-4"sludge 0"scum/ Recirc Tank-10"sludge 0"scum/ Pump Tank-0"sludge/ LPD Panel Counts: Peak-66/High-5/ Pump1-224 ETM-11h 52m/Pump2-208 ETM-11h 3m/ EZ Treat Counts: 60691 ETM-2664.66/ Pump to newest drainfield counts: cc1-7293 ETM-2553.06/ cc27180 ETM- 2551.16/ No spongy or breakout spots on the drainfields. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
09/30/2020 |  | RoutineScheduled | SWT-03-618 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected | The sample chamber lid is missing and should be replaced. | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 |  | 04/09/2021 | 03:25 PM
08/26/2020 |  | Reportable Incident | -STS-43175 | Roanoke | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Alleghany-Roanoke | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Delta Environmental DF Series |  | Pump | Pressure | Drip | Not Applicable |  | [] | [] | NA | [16 empty] | Inspected | Emergency Visit- Found Blower motor, pump and control panel not operational,lightning?- replaced blower motor and pump, Order new control panel, return 8-19-20 and 8-26-20, found zoner valve was sticking (worn due to age)causing back pressure and blocking flow likley causing the pump to burn up. Tried to improve the zoner valve and may need to get it replaced in the future. replaced plumbing in zoner box added unions and new spin filter and pressure gauge. Old control panel still being used and appears to operate ok at this time. System now operational. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 08/30/2020 | Jan 1 1900 12:30PM
08/17/2020 | Alternative | Initial Visit | 196.04.324 | Westmoreland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | Puraflo | None | Gravity | None | Aggregate Bed | None | 450.000000 | ["Attached Growth Medium"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | Musty | Clear | [15 empty] | Initial visit for service agreement Primary septic tank in normal operating level - effluent screen serviced. Pump Tank in normal operating level - pump, float sensors and controls operating properly PuraFlo peat biofilters - (4) - Biofilter in extreme poor condition - requires replacement - turned as best as possible | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 08/18/2020 | 08:00 AM
02/26/2020 |  | Reportable Incident | 234-15-420 | Chesapeake | This AOSS should now return to normal function after having provided the above stated routine maintenance. | Approved | EHD - Chesapeake | R & K Septic, Inc. |  | Craig | Van Holten |  |  | Clearstream ATU |  | Pump | Drip | Elevated Sand Mound | UV Light |  | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | [18 empty] | [Comments]: Replaced aerator, cleaned pump screen and screen filter. | This AOSS should now return to normal function after having provided the above stated routine maintenance. |  | 02/26/2020 | Jan 1 1900 8:00AM
12/21/2020 | Alternative | RoutineScheduled | 157-09-0163 | Mathews | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Three Rivers | Church View Septic Service Inc. | 1942001302 | Charles | Langford | 1.000000 | 1000 | ECOPOD |  | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [18 empty] | DRAINFIELD AREA COMPLETELY SATURATED TO WAY TOO MUCH RAIN IN THE AREA. HOPEFULLY AREA WILL DRY AND SYSTEM WILL RETURN TO NORMAL FUNCTIONING. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. |  | 01/08/2021 | 12:00 AM
01/13/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Fairfax | KLEINDL, JAMES LEE | 1942001380 | JAMES LEE | KLEINDL | 1.000000 | 1500 | Biomicrobics MicroFAST | Septic Tank Only | Pump | Distribution Box | Aggregate Trench | None | [22 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/03/2020 | Jan 1 1900 6:43PM
02/17/2020 |  | Follow-Up | 2007-143-0054 | Henrico County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Henrico |  |  |  |  | 1.000000 |  |  | Ecoflo | Pump | Distribution Box | [23 empty] | [Comments]: Septic tank pumped out by others prior to peat replacement. Degraded peat was removed by hand with pitch forks in pod #2 and new peat was installed. Peat was purchased from Wrights Ready Mix. The degraded peat was disposed at Spotsylvania Refuse. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/19/2020 | 05:59 AM
04/06/2020 |  | Routine/Scheduled | 07-120-0773A | Colonial Heights | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesterfield | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | [11 empty] | N/A | [17 empty] | At the time of maintenance, the service expert found that all components were functioning properly and the system was operational. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/06/2020 | Jan 1 1900 10:08AM
07/24/2020 |  | RoutineScheduled | 171-09-0199 | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Onsite Wastewater Service | 1942001223 | MATTHEW | FERRELL | 1.000000 | 1000 | puraflo |  | Pump | Gravity | Trenches | Not Applicable |  | ["None"] | ["None"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
11/12/2020 |  | RoutineScheduled |  | Augusta | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Dispersal System Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"Control Operation" ,"Dispersal System Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Repaired valve boxes and valves also replaced timer in panel Repaired Air Vac | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance |  | 04/26/2021 | 09:04 AM
12/19/2020 |  | RoutineScheduled | 109-19-0184 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 2.000000 | 3000 | EcoPod |  | Pump | Gravity | Trenches |  |  | ["None"] | ["None"] | [18 empty] | Quarterly Inspection. Alarm occurring in discharge pump tank. High level alarm float repositioned to a better anchor point. The septic tank and grease traps were recently pumped to investigate plumbing piping issue. 2" of liquid in grease traps and 18" of liquid in septic tank. Blower operational and effluent quality excellent. Solids levels - EQ Tank - 5", DeNite Tank - 2", Discharge Pump Tank - 0" | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12/22/2020 | 07:03 PM
01/10/2020 |  | Routine, Scheduled |  | Prince William County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Biomicrobics MicroFAST | [6 empty] | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] |  | Good | Good | [15 empty] | [Comments]: Septic Sludge 8" Scum 10"ATU Sludge 12" Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/10/2020 | 03:08 PM
03/20/2020 |  | Routine, Scheduled | R16-180-0037 | Roanoke | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Alleghany-Roanoke | Advanced Environmental & Septic, LLC | 1934000259 | Rodney | Rice | 1.000000 |  | EZ Treat Sandfilter |  | Pump | Distribution Box |  | None |  |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump"] |  | Musty | clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/20/2020 | Jan 1 1900 11:00AM
01/23/2020 |  | RoutineScheduled | 08-113-162 | Buchanan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Cumberland Plateau | DEEL, DENNY M | 1942001097 | DENNY | DEEL |  |  | Septic Tank Only | Septic Tank Only | Gravity | Gravity | Discharge | None | [11 empty] | 02/22/2020 |  | 2.240000 |  |  | 1.200000 |  |  | Attached to this report |  | [Lab Comments]: 2020 YEARLY MONITORING RESULTS [Comments]: UPLOADING MONITORING ONLY VENIS File Names: BrianWard2020.pdf | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/16/2020 | Jan 1 1900 5:05PM
12/24/2020 |  | RoutineScheduled | 179-10-0226-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Recirculation Pump" ,"SludgeScum Accumulation" ,"Attached Growth Medium"] | ["Attached Growth Medium" ,"Effluent Screens" ,"Recirculation Pump"] | YES | [15 empty] | Will be sent separately | Inspected | We recommend pumping the Advantex unit due to sludge accumulation. | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 |  | 04/09/2021 | 03:25 PM
04/20/2020 |  | Routine, Scheduled | 01-177-1221 | Pulaski County | This AOSS should now return to normal function after having provided the above stated routine maintenance. | Approved | EHD - New River | KING, WILLIAM M, II | 1942001112 | WILLIAM | KING | 1.000000 | 1000 |  | Septic Tank Only | Pump | Drip | Drip Tubing | None | 300.000000 | ["Auxiliary Filter","SludgeScum Accumulation"] | ["Auxiliary Filter","SludgeScum Accumulation"] | [18 empty] | [Comments]: Cleaned Spin Filter, pumped tank, system is working correctly. | This AOSS should now return to normal function after having provided the above stated routine maintenance. |  | 04/27/2020 | 08:38 PM
10/14/2020 |  | Reportable Incident | {FIPSCode}-STS-3125 | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance | Approved | EHD - Chesapeake | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1500 | Orenco Advantex |  | Pump | Distribution Box | Aggregate Trench | None | 450.000000 | ["Control Operation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | [17 empty] | Pumped tanks empty due to failed control panel. 10/13/2020 Alarm - system back-up ... due to failed Motherboard. 10/14/2020 - Return for Repair / Service Processing tank - low level due to recent alarm event - serviced RSV, Recirc Pump and Effluent Screen. Treatment Module - serviced media drapes & spray grid Discharge tank - high level due to recent alarm event - serviced pump, float sensors verified to be operating. Replaced failed control motherboard - reset timers from permit . Processing tank - high level condition Pump Tank - high level condition. Control panel shows evidence of possible lightning strike / power surge and requires replacement of motherboard and/or control panel. Pumped system to allow for storage to obtain required components. | This AOSS should now return to normal function after having provided the above state routine maintenance |  | 10/16/2020 | Jan 1 1900 11:00AM
04/17/2020 |  | Routine, Scheduled | SD-12-110 | Fauquier County | This AOSS should now return to normal function after having provided the above stated routine maintenance. | Approved | EHD - Rappahannock-Rapidan | JOHNSTON, JOSHUA C | 1934000089 | JOSHUA | JOHNSTON | 1.000000 | 1250 | Septic Tank Only | EcoPod | Gravity | Distribution Box | Gravel-Less Trench | None | 300.000000 |  | ["BlowerCompressorAerator Operation"] |  | none | [16 empty] | [Comments]: Blower cleaned, amperage taken on blower, dispersal area inspected. | This AOSS should now return to normal function after having provided the above stated routine maintenance. |  | 04/21/2020 | 05:37 PM
10/20/2020 | Alternative | Initial Visit | 150-19-0062 | King William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [9 empty] | 11.000000 | [7 empty] | Serviced system. Checked the pump, panel, & floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. The aerator needs to be raised - fixed the pressure switch on the aerator. Replaced the alarm light bulb. There is visible wetness on the drainfield - grading. The timer is set to .5 minutes every .5 hour. Took initial BOD sample. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 10/20/2020 | 12:00 PM
03/05/2020 |  | Reportable Incident | 175-03-0134 | Southampton County | This AOSS should now return to normal function after having provided the above stated routine maintenance. | Approved | EHD - Western Tidewater | R & K Septic, Inc. |  | John | Butt, Jr | [9 empty] | ["Control Operation"] | ["Control Operation"] | [18 empty] | [Comments]: Replaced control panel | This AOSS should now return to normal function after having provided the above stated routine maintenance. |  | 03/05/2020 | Jan 1 1900 2:00PM
06/17/2020 |  | RoutineScheduled | 179-STS-90131 | Stafford | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Puraflo | none | Pump | Gravity | Drip | Not Applicable |  | ["Distribution Pump Operation" ,"Effluent Screens" ,"Dispersal System Operation" ,"Attached Growth Medium" ,"Auxiliary Filter"] | ["Effluent Screens" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Attached Growth Medium"] | YES | [15 empty] | Will be sent separately | Inspected | Headworks box was not accesible due to standing water. | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 |  | 04/09/2021 | 03:25 PM
12/22/2020 |  | Routine, Scheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Puraflo |  |  |  |  | None |  | ["Effluent Screens"] | ["Effluent Screens"] | [18 empty] | Pump 1 Amps 15.11 ETM 5976 hrs Cycles 34420 Pump 2 Amps 15.05 ETM 7459 hrs Cycles 34326 Septic Sludge 3" Scum 2" Pump Sludge 1" Scum 0 On 60 secs Off 2 hrs | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 12/22/2020 | Jan 1 1900 12:30PM
10/09/2020 |  | RoutineScheduled | 179-12-0175-SWP | Stafford | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Level Sensor Operation"] | ["Control Operation" ,"Level Sensor Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Tanks full, no alarm. Replaced failed motherboard, programmed, and tested. Removed some roots from d-box. BOD sample past due. Could not collect today as local lab does not accept samples on Fridays. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
06/18/2020 |  |  | 03-183-001 | Russell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 06/18/2020 |  | 19.200000 |  |  | 2.270000 | [5 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 06/18/2020 | 12:00 AM
03/19/2020 |  | Routine, Scheduled | 179-08-0157-SWP | Stafford County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001350 | Mike | Cook | 1.000000 |  | Puraflo | None | Pump | Distribution Box | Aggregate Trench |  |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/01/2020 | 06:33 AM
06/15/2020 |  | RoutineScheduled | -STS-43184 | Botetourt | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | Hunter E. Ayres, General Contractor | 1942001166 | Hunter | Ayres | 1.000000 | 1500 | Biomicrobics MicroFAST |  | Pump | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","Effluent Screens"] | ["Auxiliary Filter","Effluent Screens"] | YES | [17 empty] | Checked and cleaned all filters. Control panels functioning properly. No apparent leaks in system or drain field area. Slight overgrowth on media. Lids properly secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 07/13/2020 | 12:00 AM
07/23/2020 |  | RoutineScheduled | 069041055 | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 2705110223 | Larry | Royston | [9 empty] | ["None"] | ["None"] | YES | [16 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 09/02/2020 | 12:00 AM
11/12/2020 |  | Routine, Scheduled | 153-STS-20241 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Biomicrobics MicroFAST |  |  |  |  | None |  | ["Blower/Compressor/Aerator Operation"] | ["Blower/Compressor/Aerator Operation"] |  | Acceptable | Clear | [15 empty] | Septic Sludge 10" Scum 2" ATU Sludge 12" Scum 0 Pump Sludge 1" Scum 0 Pump Amps 10.70 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 11/12/2020 | 10:04 AM
01/16/2020 |  | Routine, Scheduled |  | Loudoun County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | None | Pump | Distribution Box | Aggregate Trench | [23 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/02/2020 | 04:43 AM
02/19/2020 |  | Routine, Scheduled | 04-197-A4 | Wise County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Lenowisco | DEEL, DENNY M | 1942001097 | DENNY | DEEL |  |  | Jet ATU | None | Gravity | None | Alternative Discharge | Chlorine | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection"] |  | Musty | Clear | [15 empty] | [Comments]: Installs Own Tablets | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/10/2020 | Jan 1 1900 5:39PM
01/31/2020 |  | Routine, Scheduled | SP-04-341 | Caroline County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | None | Pump | Distribution Box | Aggregate Trench |  |  | ["Attached Growth Medium","None","Recirculation Pump"] | ["Attached Growth Medium","None","Recirculation Pump"] | [18 empty] | [Comments]: We recommend adding a 4" Tee onto the sewer line where it enters the tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/02/2020 | 11:52 AM
02/19/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS should now return to normal function after having provided the above stated routine maintenance. | Paid | EHD - Fairfax | SEAMON, CHARLIE L | 1942001108 | CHARLIE | SEAMON |  |  | Septic Tank Only | Microfast | Pump | Manifold | Aggregate Trench | None |  | ["BlowerCompressorAerator Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation"] | [10 empty] | 42.000000 | [5 empty] | Attached to this report |  | [Comments]: Performance Inspection and BOD Sample: Microfast to LPD Trenches. Septic-8"sludge 2"scum/Microfast-14"sludge/Pump Tank-2"sludge. Pump out of septic/Microfast tank is required. Replaced 2 faulty wide angle floats (off and alarm) P1 cnts-760 ETM-47h 35m/ P2 cnts-726 ETM-45h 59m. Blower air filter cleaned. Need sample box replaced. | This AOSS should now return to normal function after having provided the above stated routine maintenance. |  | 03/06/2020 | Jan 1 1900 4:11PM
10/06/2020 |  | RoutineScheduled | 04-197-176 | Wise | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | ADVANTEX |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Disinfection","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation","Septic Tank Baffles"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Disinfection","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation","Septic Tank Baffles"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
04/11/2020 |  | RoutineScheduled | SD-12-167 | Culpeper | This AOSS is functioning as designed and in accord | Approved | EHD - Rappahannock-Rapidan | Wastemaster |  | Douglas | Crooks | 2.000000 | [6 empty] | Chlorine |  | [] | [] |  | Low | Clear | 7.400000 |  |  | 1.800000 |  | 04/11/2020 |  | 4.000000 |  |  | 3.000000 |  |  | Attached to this report |  | Functioning as Designed | This AOSS is functioning as designed and in accord |  |  | 12:00 AM
02/18/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Biomicrobics MicroFAST |  | Pump | Drip | Drip Tubing | UV Light |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection"] |  | Good | Clear | [15 empty] | [Comments]: Spin filter cleaned.Pump Amps 8.18 ETM 591h Cycles 2491Water Meter Reading 221800Septic Sludge 3" Scum 2"ATU Sludge 5" Scum 0.25Pump Sludge 1" Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/18/2020 | Jan 1 1900 3:00PM
05/28/2020 |  | Routine, Scheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Puraflo |  |  |  |  | None |  | ["Effluent Screens"] | ["Effluent Screens"] | [18 empty] | Pump 1 Amps 5.56 ETM 82834 Cycles 75730 Pump 2 Amps 10.41 ETM 82294 Cycles 75602 Septic Sludge 11 Scum 0.50 Pump Sludge 0 Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 05/28/2020 | Jan 1 1900 9:10AM
04/17/2020 |  | Routine, Scheduled | 07-160-0088 | Montgomery County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1934000259 | Rodney | Rice | 1.000000 |  |  |  | Gravity | Distribution Box | Aggregate Trench | None |  |  | ["BlowerCompressorAerator Operation","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/17/2020 | 11:15 AM
10/06/2020 |  | RoutineScheduled | 109-06-0177 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 |  | Large Treatment System |  | Pump | Pressure | Drip | Not Applicable |  | [] | [] | NA | [16 empty] | Inspected | Large Treatment unit Not listed in VDH list - Sludge levels-- 12" sludge in Septic tank zone. Both Blowers are operational and alternating. Aeration- -10"-12" sludge - Clarifier 30" sludge- Pump Tank 24" sludge Pump1 ct 31563 etm 129754 Pump#2 ct28140 ETM 201021, (#1 2157.41Hr 31989 Ct) - (#2 2643.85Hr 28795 Ct) Continue to backwash often to prevent building up of sludge. Pump #1 Ran approx 1500 cycles since last inspection in 139Hours. Pump#2 Ran approx 1480 cycles in 133Hours | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 10/30/2020 | 12:30 PM
09/08/2020 |  | Follow-Up |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 | Pending Payment | EHD - Loudoun | WasteMaster, Inc. | 1942001062 | Tim | Jenkins |  |  | Multiflo FTB | none | Gravity | Gravity |  | Chlorination |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | In for aerator not running. Found wiring connections burned up. Also piping broken. Tested aerator works fine. Repaired wiring and piping. System is scheduled for pump out this week. | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 |  | 06/21/2021 | 10:37 AM
04/01/2020 |  | Routine, Scheduled |  | Loudoun County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | None | None | Pump | Manifold | [24 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/12/2020 | 02:21 PM
10/05/2020 |  | RoutineScheduled | 177-09-0244-SP | Spotsylvania | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Distribution Pump Operation"] | ["BlowerCompressorAerator Operation" ,"Distribution Pump Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/09/2021 | 03:25 PM
02/20/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Fairfax | MCKIM, STEPHEN E | 1934000043 | STEPHEN | MCKIM |  |  | Septic Tank Only | Septic Tank Only | None | None | None | None |  |  | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/29/2020 | Jan 1 1900 4:29PM
04/20/2020 |  | Routine, Scheduled | 16-160-0170 | Montgomery County | This AOSS should now return to normal function after having provided the above stated routine maintenance. | Approved | EHD - New River | KING, DAVID A | 1942001094 | DAVID | KING | 1.000000 | 1200 |  | Septic Tank Only | Gravity | Distribution Box | Gravel-Less Trench | None | 150.000000 | ["Effluent Screens"] | ["Effluent Screens"] | [18 empty] | [Comments]: Cleaned Effluent Screen, system is working correctly. | This AOSS should now return to normal function after having provided the above stated routine maintenance. |  | 04/27/2020 | 08:29 PM
12/01/2020 |  | Routine/Scheduled |  | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Whitewater ATU |  | Pump |  |  |  |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  | 9.23 | 6.830000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 12/01/2020 | Jan 1 1900 7:30AM
09/05/2020 |  | RoutineScheduled | 2011-08-153 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Wastemaster Inc |  | Timothy | Jenkins | 2.000000 |  | PuraFlo | Post Aer | Pump | Gravity | Discharge | UV |  | [] | [] |  | Musty | Clear | 7.500000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 09/11/2020 | 11:55 AM
07/22/2020 |  | RoutineScheduled | 14-142-0271 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Old Dominion Onsite, Inc. | 1942001134 | John | Ewing | 1.000000 | 1000 | Orenco Advantex |  | Pump | Distribution Box | Aggregate Trench | UV Light | 200.000000 | ["Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation"] | ["Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation"] | NA | [17 empty] | Distribution box lid is cracked, leaks around the header pipe and should be replaced UV light was replaced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 08/12/2020 | Jan 1 1900 2:02PM
03/14/2020 |  | RoutineScheduled | VAG401881 | Rockingham | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Central Shenandoah | Onsite Wastewater Services - May Supply | 1942001022 | Sara | Tusing |  |  | none | none | Pump | Gravity |  | Chlorination |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/28/2021 | 05:41 AM
03/23/2020 |  | Routine, Scheduled |  | Loudoun County | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Paid | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 2.000000 |  | EcoPod | None | Pump | Distribution Box | Aggregate Trench | [22 empty] | [Comments]: ATU and pump tank need pumped out | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 04/12/2020 | 02:21 PM
11/19/2020 |  | Follow-Up | Sd-02-803 | Fauquier | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 2.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation" ,"Distribution Pump Operation"] | ["Dispersal System Operation" ,"Distribution Pump Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced K-rain zoner valve. Tested rates. Flushed tubing and cleaned zone return valve. Zoner rotated properly and dosed one zone at a time. Owner to consider adding plumbers heat tape to zoner box during winter. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
08/17/2020 | Alternative | Reportable Incident | 151-05-318 | Lancaster | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | obsidian onsite services |  | joel | pinnix | [9 empty] | [] | ["Other"] | [18 empty] | HIgh water alarm - all components normal. Maybe due to excessive rain events. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  |  | 12:00 AM
01/25/2020 |  | Routine, Scheduled | SD-09-214 | Fauquier County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | Brown, Jason W | 1942001049 | Jason | Brown | 1.000000 | 1200 | Septic Tank Only | EZ Treat Sandfilter | Gravity | None | Aggregate Trench | None |  |  |  |  | musty | [16 empty] | VENIS File Names: Childers O&M Jan 25 2020.odt | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/18/2020 | 04:36 PM
01/07/2020 |  | Routine, Scheduled | SP-05-99 | Caroline County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Ware, Michele P | 1942001165 | Michele | Ware |  |  | Septic Tank Only | Septic Tank Only | None | None | None | None |  |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/07/2020 | 07:34 AM
01/12/2020 |  | Routine, Scheduled |  | Albemarle County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Blue Ridge | BASORE, WESLEY LEE | 1942001047 | Wesley | Basore | 1.000000 | 500 | Ecoflo | None | Pump | Distribution Box | Gravel-Less Trench | None | 150.000000 | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/18/2020 | 02:02 PM
10/21/2020 |  | RoutineScheduled | 94-184-5001 | Scott |  |  | EHD - Lenowisco | S.E.P.T.I.C., INC. |  | Denny | Deel | [7 empty] | Chlorination |  |  |  |  | None | Clear | 8.500000 | 6.000000 |  | 0.000000 | [11 empty] | Jeanette Duncan performed the inspection Tank information not found Contractor information incomplete |  |  |  | 12:00 AM
11/17/2020 |  | Routine/Scheduled | 05-160-0281 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 | 1000 | Delta Environmental Products, DF Series |  | Pump | Drip | Drip Tubing | None | 46.000000 | ["None"] | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 11/17/2020 | 10:30 AM
12/14/2020 |  | Follow-Up | {FIPSCode}-STS-19461 | Wise | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | Wise County Health Department |  | Rodney | Neece | 1.000000 |  | ATU |  | Gravity | Gravity | Discharge | Chlorination |  |  |  |  | Septic | Cloudy | 5.500000 | 0.000000 |  | 1.000000 | Dechloricator tablets not touching the effluent unit not running | [11 empty] | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12/14/2020 | 12:00 AM
08/12/2020 |  | RoutineScheduled | 187110209 | Warren | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Lord Fairfax | Onsite Wastewater Services - May Supply | 1942001022 | Sara | Tusing | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity |  | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/28/2021 | 05:41 AM
12/01/2020 |  | RoutineScheduled | 06-113-249 | Buchanan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Effluent Screens"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
07/30/2020 |  | RoutineScheduled | 177-12-0311-SR | Spotsylvania | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Recirculation Pump" ,"Attached Growth Medium"] | ["Effluent Screens" ,"Recirculation Pump" ,"Attached Growth Medium"] | YES | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/09/2021 | 03:25 PM
10/16/2020 |  | RoutineScheduled | 04-197-A11 | Wise | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Effluent Screens"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Effluent Screens"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
06/04/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/27/2021 | 01:26 PM
01/29/2020 |  | Routine, Scheduled | 179-15-0247-SP | Stafford County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001350 | Mike | Cook | 1.000000 |  | None | None | Gravity | Distribution Box | Aggregate Trench |  |  | ["BlowerCompressorAerator Operation","Control Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/03/2020 | 05:52 AM
03/18/2020 |  | RoutineScheduled | 04-100-0980 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Bundick Well & Pump | 1942001051 | Peter | Duer | 1.000000 | 750 | Septic Tank | Purflo | Pump | Pressure | Pad | Not Applicable | 300.000000 | ["None"] | ["None"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 07/01/2020 | 12:35 PM
07/29/2020 |  | RoutineScheduled | 06-195-518-DIS | Washington | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Mount Rogers | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
01/16/2020 |  | Routine, Scheduled | 107-01-0142 (LEGACY ALT. SYSTEM) | Augusta | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central Shenandoah | SEAL, CHARLES K | 1934000144 | CHARLES | SEAL | 1.000000 |  | Septic Tank Only | Microfast | Pump | Manifold | Drip Tubing | None |  | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation"] | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation"] | [19 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 02/21/2020 | 04:31 PM
03/27/2020 |  | Routine, Scheduled |  | Prince William County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Delta Environmental Products, DF Series |  |  |  |  | None |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] |  | Good | Good | [15 empty] | [Comments]: Spin filter cleaned.Pump Amps 8.18 ETM 71h Cycles 25336Water Meter Reading 1418850Septic Sludge 9" Scum 0.50ATU Sludge 2" Scum 3"Pump Sludge 5" Scum 0Control panel needs new light bulbs. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/27/2020 | 01:15 PM
09/24/2020 |  | Follow-Up |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Lord Fairfax | Aquarobic Services | 1934000142 | Michael | Blake |  |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"BlowerCompressorAerator Operation"] | ["Control Operation" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | New blower installed. Also replaced the light assembly for blower standby. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 07/01/2022 | 10:30 AM
07/27/2020 |  |  | 027-STS-15542 | Buchanan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 07/27/2020 |  | 13.300000 |  |  | 1.000000 |  |  | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 07/27/2020 | 12:00 AM
09/24/2020 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump | Distribution Box | Aggregate Bed | None |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  |  | 6.260000 | 5.300000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 09/24/2020 | Jan 1 1900 8:00AM
04/22/2020 |  | Routine, Scheduled | 177-17-0403-SWP | Spotsylvania County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | None | None | Gravity | Distribution Box | Gravel-Less Trench |  |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] |  | YES | YES | [15 empty] | [Comments]: Routine inspection. Collected first BOD sample. Atu alarm not working, heavy corrosion inside control box. Owner is going to contact installer. Cleaned air filter. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/27/2020 | 04:14 AM
07/29/2020 |  | RoutineScheduled | 08-174-0093 | Prince George | This AOSS should now return to normal function after having provided the above state routine maintenance. | Rejected | EHD - Crater | Stamie E. Lyttle Co. | 1942001470 | Eric | Tambourine | [9 empty] | [] | [] | [19 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 07/29/2020 | 12:00 AM
07/08/2020 |  | Routine, Scheduled | 175-06-0218 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Clearstream |  |  |  |  | None |  | ["Blower/Compressor/Aerator Operation"] | ["Blower/Compressor/Aerator Operation"] |  | Good | Clear | [15 empty] | Pump Amps 11.27 ETM 177.79 Cycles 4545 Septic Sludge 10" Scum 2" ATU Sludge 0 Scum 0 Pump Sludge 2" Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 07/08/2020 | 12:45 PM
05/19/2020 |  | RoutineScheduled | CS-94-37 | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | SEAL’S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | tank only |  | Pump | Pressure | Trenches |  |  | ["None"] | ["None"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 05/19/2020 | 12:00 AM
09/21/2020 | Alternative | Routine/Scheduled | 157-14-0133 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | Serviced system. Checked the pump, panel, & floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. Replaced the buzzer. The timer is set to 2 minutes every 2 hours. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 09/21/2020 | 12:00 PM
05/26/2020 |  | Routine, Scheduled | 175-11-0194 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Clearstream |  |  |  |  | UV Light |  | ["Effluent Screens"] | ["Effluent Screens"] |  | Good | Clear | [15 empty] | Pump Amps 8.03 ETM 9368 Cycles 2080 Septic Sludge 8" Scum 2" ATU Sludge 0 Scum 0 Pump Sludge 1" Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 05/26/2020 | 08:53 AM
01/14/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS should now return to normal function after having provided the above stated routine maintenance. | Paid | EHD - Fairfax | SEAMON, CHARLIE L | 1942001108 | CHARLIE | SEAMON |  |  | Septic Tank Only | Microfast | Pump | Manifold | Drip Tubing | UV Light |  | ["BlowerCompressorAerator Operation","Level Sensor Operation"] | ["BlowerCompressorAerator Operation","Level Sensor Operation"] | [10 empty] | 32.000000 |  | 1.800000 |  |  |  | Attached to this report |  | [Comments]: Performance Inspection and Samples: Microfast & UV Light to American Drip. Septic-4"sludge 0"scum/ATU 0"sludge/Pump Tank-0"sludge. Zone1 counts-387 ff-11/Zone2 counts-387 ff-13/pump cnts-797 ETM-187h 27m/ Peak cnts-488 ETM-255h 47m/High-13 ETM-0 Replaced faulty peak float. | This AOSS should now return to normal function after having provided the above stated routine maintenance. |  | 02/19/2020 | Jan 1 1900 6:25AM
07/29/2020 |  | RoutineScheduled | 17-113-126 | Buchanan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Control Operation","BlowerCompressorAerator Operation","Disinfection","Effluent Screens"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
12/30/2020 |  | RoutineScheduled | 175-12-0388 | Prince William | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Blower is loud, but is working. Replacement may be needed in the near future. | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 |  | 04/09/2021 | 03:25 PM
05/29/2020 |  | RoutineScheduled | swt-00-676 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Wastemaster |  | Timothy | Jenkins | 2.000000 |  | ATU | Drip DF | Pump | Pressure | Drip | Chlorination |  | [] | [] | [18 empty] | American Tank Cleaning Recently pumped out trash tank, ATU and pump tank | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 05/29/2020 | 07:03 PM
07/02/2020 |  | RoutineScheduled | SD-13-210 | Culpeper | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | EcoPod | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Dispersal System Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Dispersal System Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/09/2021 | 03:25 PM
11/23/2020 |  | Routine/Scheduled | 234-17-229 | Chesapeake | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Chesapeake | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | Serviced system. Checked the pump, panel, & floats (ok). Cleaned the filter in the Clearstream and cleaned the disc filter. Changed the diffuser in the Clearstream and changed the filter in the aerator. The UV is burnt up. The septic tank needs additional risers on it so it can be properly inspected in the future. Visible wetness on the drainfield - most likely from rain - need to keep an eye on it. The timer is set to 8 minutes every 2 hours. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. |  | 11/23/2020 | Jan 1 1900 12:00PM
12/13/2020 |  |  | 133 06 0431 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | Western Virginia Water Authority | 1942001145 | Michael | Doss |  |  |  |  | Gravity | Pressure | Drip | UV |  | ["None"] | ["None"] | NA | Musty | Clear | 6.920000 |  |  |  |  | 12/09/2020 | Sample Chamber | 10.000000 |  | 31.000000 | 13.000000 | 7.200000 |  | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 01/13/2021 | 09:05 AM
05/23/2020 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 | Pending Payment | EHD - Loudoun | WasteMaster, Inc. | 1942001062 | Tim | Jenkins | 1.000000 |  | Delta Environmental Products, DF Series | Delta Environmental Products, DF Series | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 |  | 06/21/2021 | 10:37 AM
11/23/2020 |  | RoutineScheduled | 107-16-0390 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Pump | Pressure | Drip | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 06/02/2021 | 12:00 AM
01/28/2020 |  | Routine, Scheduled |  | Loudoun County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | None | None | Pump | Distribution Box | Aggregate Trench | [23 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/06/2020 | 07:11 AM
09/10/2020 |  | RoutineScheduled |  | Rockingham | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity |  | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation"] | ["BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Repaired Blower panel at time of service | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance |  | 04/26/2021 | 09:04 AM
06/19/2020 |  | RoutineScheduled | 177-06-0357-SWT | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Recirculation Pump" ,"Dispersal System Operation" ,"Attached Growth Medium"] | ["Effluent Screens" ,"Recirculation Pump" ,"Dispersal System Operation" ,"Attached Growth Medium"] | YES | [15 empty] | Will be sent separately | Inspected | We removed roots from the surge & distribution boxes. The sewer line may have settled. We would recommend contacting a plumber for a camera inspection of this line. | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 |  | 04/09/2021 | 03:25 PM
02/27/2020 |  | Follow-Up |  | Fairfax County | This AOSS should now return to normal function after having provided the above stated routine maintenance. | Paid | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green | [9 empty] | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | [18 empty] | [Comments]: Installed new compressor. | This AOSS should now return to normal function after having provided the above stated routine maintenance. |  | 02/27/2020 | Jan 1 1900 4:00PM
03/10/2020 |  | Routine, Scheduled | 177-16-0364-SWP | Spotsylvania County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Norweco Singulair ATU | None | Pump | Distribution Box | Aggregate Trench |  |  | ["BlowerCompressorAerator Operation","Effluent Screens","None"] | ["BlowerCompressorAerator Operation","Effluent Screens","None"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/06/2020 | 02:45 PM
06/30/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/27/2021 | 01:26 PM
05/26/2020 |  | RoutineScheduled | 04-125-055 | Dickenson | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | Septic Inc |  | Denny | Deel |  |  | Norweco |  | Gravity |  | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
06/10/2020 |  | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 2705110225 | Larry | Royston | [9 empty] | [] | [] | NA | None |  | 0.000000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 03:10 PM
12/07/2020 |  | RoutineScheduled | SD-05-240 | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | None | Clear | 7.650000 |  |  |  |  | 12/07/2020 |  | 12.000000 |  |  | 13.400000 | [5 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12/21/2020 | 03:00 PM
01/15/2020 |  | Routine, Scheduled |  | Dinwiddie County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Crater | Madison Environmental LLC | 1934 000061 | Larry | Madison, Jr. |  |  | Biomicrobics MicroFAST |  | Pump |  |  |  |  | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/15/2020 | Jan 1 1900 3:30AM
11/02/2020 |  | Reportable Incident | 061-STS-24498 | Fauquier | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Level Sensor Operation"] | ["Level Sensor Operation"] | NA | [15 empty] | Will be sent separately | Inspected | High level alarm. Alternating relay pulled in, but neither pump contactor pulled in due to failed "on" float switch. Replaced all 4 float switches and tested pump and panel operation. Discovered panel had been modified from original wiring (perhaps at time of installation). The 2nd float served as the "on" float for pump #1, and the "lag on" float served as the "on" float for pump #2. All 3 floats were only about 2" apart from each other. Pumps do alternate in this configuration, but there is no lead/lag operation where the lag pump kicks on when the lead pump fails and causes high level alarm. Not sure how to restore wiring. Original plans called for 15" between on/off floats. Suspect the floats may have been moved closer together for a much smaller dose back when the drainfield malfunctioned. Adjusted floats so that dose is now about 6". If LPD drainfield handles the bigger dose, the floats will be spread another 6" at next site visit. Replaced concrete lid on pump tank and disposed of the old one. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
05/15/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/14/2021 | 04:27 PM
06/10/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | EcoPod | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/27/2021 | 01:26 PM
05/21/2020 |  | Routine/Scheduled | 01-120-0617A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesterfield | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | [11 empty] | N/A | [17 empty] | At the time of maintenance, the service expert found that all tanks were found at normal level. He tested all floats and pumps and confirmed that all were functioning properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 05/21/2020 | Jan 1 1900 2:53PM
12/17/2020 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  |  | Drip | Elevated Sand Mound | UV Light |  | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  |  | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 12/17/2020 | Jan 1 1900 2:00PM
02/03/2020 |  | Routine, Scheduled | 234-17-434 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesapeake | R & K Septic, Inc. |  | John | Butt, Jr |  |  | Clearstream ATU |  | Pump | Drip | Elevated Sand Mound | UV Light |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] |  |  | 4.3 | 6.650000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/03/2020 | Jan 1 1900 3:00PM
04/21/2020 |  | RoutineScheduled | 175-14-0331 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | [9 empty] | ["SludgeScum Accumulation"] | [] | [18 empty] | Septic/ATU-12" sludge scum could not be measured ATL-10" sludge. Pump tank 8" sludge Septic/ATU & pump tank require pump out and was done by others 4/24/2020 Cleaned air filter for blower. Replaced septic lid, replaced high level alarm light. Found all switches in control panel were off. Turned switches on and tested system. W/M-012302.55 | This AOSS should now return to normal function after having provided the above state routine maintenance. |  |  | 12:00 AM
07/31/2020 | Alternative | RoutineScheduled | 150-07-089 | King William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Onsite Maintenance Team | 1942001039 | Corey | Braxton | 2.000000 |  | Advantex AX20 |  | Gravity | Gravity | Trenches |  | 250.000000 | ["Attached Growth Medium"] | ["Attached Growth Medium","Control Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump"] |  | Musty | Clear | 6.900000 | 3.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
02/28/2020 |  | Follow-Up | SD-05-390 | Fauquier County | This AOSS should now return to normal function after having provided the above stated routine maintenance. | Approved | EHD - Rappahannock-Rapidan | SES Mid Atlantic | 1942001203 | Michael | Green | [9 empty] | ["Control Operation"] | ["Control Operation"] | [18 empty] | [Comments]: Installed PLC in control panel & (5) control floats. | This AOSS should now return to normal function after having provided the above stated routine maintenance. |  | 02/28/2020 | 10:30 AM
08/18/2020 |  | Routine, Scheduled | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Orenco Advantex |  |  |  |  | UV Light |  | ["Dispersal System Operation"] | [19 empty] | Water Meter is not operational. Broken discharge line. Septic Sludge 0 Scum 0 Pump Sludge 0 Scum 0 | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 08/18/2020 | Jan 1 1900 9:40AM
04/15/2020 |  | Routine, Scheduled | 2006-143-0223 | Henrico County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Henrico |  |  |  |  | 1.000000 | 1250 |  | None | Pump | None | Gravel-Less Bed | None |  |  | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [18 empty] | [Pumpout Comments]: 8" scum layer 12" sludge layer 4’ overall depth [Comments]: Peat Moss mixed and turned | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/17/2020 | 05:40 PM
05/28/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Pad | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | SEPTIC AND ATU NEEDS PUMPED OUT | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 |  | 04/14/2021 | 04:27 PM
06/24/2020 |  | Routine/Scheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Loudoun | POWELLS PLUMBING, INC. | 1942001036 | Kurt | Holthaus | 1.000000 | 1200 |  |  | Pump | Manifold | Aggregate Trench |  | 600.000000 | ["Effluent Screens"] | ["Effluent Screens"] | N/A | [17 empty] | Annual Inspection - Serviced effluent screen(s). | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 06/29/2020 | 01:17 PM
11/24/2020 |  | Follow-Up | 099-11-0033-SP | King George | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Pad | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Replaced failed fuji blower with a 1/2 hp fpz blower. Added a union for future maintenance and replacement. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
11/28/2020 |  |  | SD-02-499 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC |  | Jason | Brown | 2.000000 | 1500 gal | septic/trash | pump tank | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | YES | Musty | Cloudy | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 11/29/2020 | 08:05 AM
08/07/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Ecoflo | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Recommend pumping and basic maintenance on peat. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/27/2021 | 01:26 PM
02/26/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Fairfax | Hott, Joshua D. | 1942001301 | Joshua | Hott | 1.000000 | 1875 | Septic Tank Only | Puraflo | Pump | Distribution Box | Aggregate Trench | None |  | ["Effluent Screens"] | ["Effluent Screens"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/18/2020 | Jan 1 1900 3:03PM
11/16/2020 |  | RoutineScheduled | 181-06-0267 | Rockbridge | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Central Shenandoah | Valley Soil & Environmental Consulting, LLC | 1942001218 | John | Lam | 1.000000 | 1000 | Septic tank only |  | Pump | Pressure | Trenches | Not Applicable | 75.000000 | ["Dispersal System Operation","Effluent Screens"] | ["Effluent Screens"] | YES | [17 empty] | LPD system #1: HD ID #181-04-0275; cleaned septic tank effluent filter at Lot 10; added handle to effluent filter; measured 13" of solids; LPD pump and control panel not functioning and will require replacement. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. |  | 12/04/2020 | 12:00 AM
05/05/2020 |  | Routine, Scheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Biomicrobics MicroFAST |  |  |  |  | UV Light |  | ["Blower/Compressor/Aerator Operation","Disinfection"] | ["Blower/Compressor/Aerator Operation","Disinfection"] |  | Good | Clear | [15 empty] | Spin filter cleaned. Pump Amps 11.19 ETM 270 hrs Cycles 1945 Water Meter Reading 151200 Septic Sludge 10" Scum 0.50 ATU Sludge 6" Scum 0 Pump Sludge 1" Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 05/05/2020 | Jan 1 1900 11:22AM
02/24/2020 |  | Routine, Scheduled | 234-14-213 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesapeake | R & K Septic, Inc. |  | John | Butt, Jr |  |  | Clearstream ATU |  | Pump | Drip | Elevated Sand Mound | UV Light |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] |  |  | 8.41 | 8.220000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/24/2020 | Jan 1 1900 11:20AM
05/26/2020 |  | RoutineScheduled | 099-11-0040-SWP | King George | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Recirculation Pump" ,"Attached Growth Medium"] | ["Attached Growth Medium" ,"Effluent Screens" ,"Recirculation Pump"] | YES | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/09/2021 | 03:25 PM
03/09/2020 |  | Routine, Scheduled | 800-11-0310 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Western Tidewater | R & K Septic, Inc. |  | Craig | Van Holten |  |  | Clearstream ATU |  | Gravity | Distribution Box |  | None |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/09/2020 | Jan 1 1900 1:00PM
12/24/2020 | Alternative | RoutineScheduled | 159-14-0086 | Middlesex | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Church View Septic Service Inc. | 1942001302 | Charles | Langford | 1.000000 | 1250 | Ecopod |  | Pump | Pressure | Pad | Not Applicable |  | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | ["Auxiliary Filter"] | [18 empty] | No power to blower needs to be addressed. Spin filter changed. Pump station could use pumping. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 01/14/2021 | 12:00 AM
05/19/2020 |  | Reportable Incident | C102-06-0065 | Alleghany | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Alleghany-Roanoke | Hunter E. Ayres, General Contractor | 1942001166 | Hunter | Ayres | 3.000000 | 2500 | Whitewater ATU |  | Pump | Pressure | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation","Distribution Pump Operation","Auxiliary Filter"] | ["BlowerCompressorAerator Operation","Distribution Pump Operation","Auxiliary Filter"] | YES | [17 empty] | Effluent filter checked and cleaned. Effluent pump replaced. Blower/motor replaced. Lids properly secured | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 06/20/2020 | Jan 1 1900 10:35AM
10/17/2020 |  | RoutineScheduled | SD-10-008 | Orange | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Wastemaster Inc |  | Timothy | Jenkins | 2.000000 |  | ATU | Polishing Sandfilter | Pump | Gravity | Discharge | UV |  | [] | [] |  | Musty | Clear | 7.300000 | 8.100000 |  |  |  | 10/17/2020 |  | 3.000000 |  | 0.800000 | 3.400000 | [5 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 11/16/2020 | 08:00 PM
01/03/2020 |  | Routine, Scheduled | 13-0140 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Virginia Beach | R & K Septic, Inc. |  | Robbie | Van Holten |  |  |  |  | Pump | Distribution Box | Aggregate Bed | None |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] |  |  |  | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/03/2020 | Jan 1 1900 10:30AM
05/14/2020 |  | Reportable Incident | 04-120-0199A | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance | Approved | EHD - Chesterfield | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1500 | Orenco Advantex |  | Pump | Distribution Box | Aggregate Trench | None | 450.000000 | ["Effluent Screens","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | Musty | Clear | [15 empty] | Processing tank reduced in volume to facilitate repairs. Resealed riser access on processing tank, replaced wiring and electrical splice box in recirculation tank, replaced riser on pump tank and installed new electrical splice box. | This AOSS should now return to normal function after having provided the above state routine maintenance |  | 05/26/2020 | Jan 1 1900 8:00AM
10/18/2020 |  | Routine/Scheduled | 07-160-0308 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Orenco Advantex |  | Gravity | Distribution Box |  | None |  | ["None"] | ["Control Operation","Level Sensor (Float) Operation","Recirculation Pump","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 10/14/2020 | 03:45 PM
06/02/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/27/2021 | 01:26 PM
03/30/2020 |  | Routine, Scheduled | 05-192-349 | Tazewell County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Cumberland Plateau | DEEL, DENNY M | 1942001097 | DENNY | DEEL |  |  | Norweco Singulair ATU | None | Gravity | None | Alternative Discharge | Chlorine | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens"] |  | Musty | Clear | [15 empty] | [Comments]: 10 biomax, 5 blue crystals | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/13/2020 | Jan 1 1900 8:51AM
05/21/2020 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  |  |  | Aggregate Trench |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Recirculation Pump","Sludge/Scum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Recirculation Pump","Sludge/Scum Accumulation"] | N/A |  |  | 7.000000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 05/21/2020 | Jan 1 1900 1:00PM
02/17/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Paid | EHD - Fairfax | MCKIM, STEPHEN E | 1934000043 | STEPHEN | MCKIM |  |  | Septic Tank Only | Septic Tank Only | None | None | None | None |  | ["SludgeScum Accumulation"] | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | [18 empty] | [Comments]: septic and atu need pumped out | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 02/29/2020 | Jan 1 1900 4:59PM
07/01/2020 |  | RoutineScheduled | 069-18-0358 | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Combs Wastewater Management LLC | 1942001353 | Amy | Combs | 2.000000 | 1500 |  | Microfast | Pump | Pressure | Drip | Not Applicable | 450.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | YES | None | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 07/03/2020 | 12:00 AM
07/27/2020 |  | RoutineScheduled | 132-04-0198 | Fluvanna | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Blue Ridge | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Norweco Singulair ATU | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"SludgeScum Accumulation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Pump tank needs pumped out as sludge is well above the pump intake. Owner to make arrangements. Pressure gauge was stuck, replaced it. Aerator did not turn back on after cleaning and would not reset. UF cable evidently has a bad spot as positioning it just right caused the blower to restart. Owner should have cable repaired or replaced. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
10/02/2020 |  | Routine/Scheduled | 05-160-0373 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Orenco Advantex |  | Pump | Drip | Drip Tubing | None | 121.000000 | ["None"] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 10/02/2020 | 12:00 PM
10/08/2020 |  | Pump-Out Only | 02-172-0752AR | Powhatan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesterfield | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1250 | Orenco Advantex |  | Pump | Distribution Box | Gravel-Less Trench | None | 450.000000 |  | ["Sludge/Scum Accumulation"] | N/A | [17 empty] | Pumpout conducted by CWS, supervised by Miller Staff Supervised pumpout by CWS as recommended from previous service visit - refilled processing tank | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 10/13/2020 | Jan 1 1900 8:00AM
01/28/2020 |  | Routine, Scheduled | SP-05-213 | King George County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001350 | Mike | Cook | 1.000000 |  | Puraflo | None | Pump | Distribution Box | Aggregate Bed |  |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/03/2020 | 08:59 AM
04/02/2020 |  | Routine/Scheduled |  | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump | Distribution Box |  | None |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  |  | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/02/2020 | Jan 1 1900 10:45AM
09/23/2020 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump | Drip | Elevated Sand Mound | UV Light |  | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | Replaced UV cord & UV bulb | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 09/23/2020 | Jan 1 1900 3:30PM
04/11/2020 |  | Follow-Up | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance | Approved | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green | [9 empty] | ["None"] | ["None"] | [18 empty] | Repaired force main break on grinder pump. | This AOSS should now return to normal function after having provided the above state routine maintenance |  | 04/11/2020 | Jan 1 1900 10:30AM
05/11/2020 |  | RoutineScheduled | 171-15-0232 | Pittsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Pittsylvania-Danville | Acres of Virginia, Inc. | 1942001044 | Melvin | Collins | 1.000000 | 1050 | Advantex | none | Pump | Pressure | Trenches | Not Applicable | 450.000000 | ["None"] | ["None"] | YES | [17 empty] | Checked filter and tank, Light for low water level on. Pump sounded okay and was working. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 01:10 PM
06/19/2020 |  |  | SWP-05-409 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | DCM Septic LLC | 1942001350 | Michael | Cook | 2.000000 | 1250 | 1-6 |  | Pump | Gravity | Trenches |  | 600.000000 | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | YES | None | Clear |  |  | 24.000000 | [11 empty] | Inspected | home owner will pump out system in 3 months they will contact me when it has been done. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 06/19/2020 | 07:10 PM
01/09/2020 |  | Routine, Scheduled |  | Loudoun County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | None | Pump | Distribution Box | Aggregate Trench | [23 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/15/2020 | 06:36 AM
09/14/2020 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump | Distribution Box |  | UV Light |  | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  |  | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 09/14/2020 | Jan 1 1900 10:00AM
05/02/2020 |  | RoutineScheduled | {FIPSCode}-STS-1192 | Buchanan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. |  | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Effluent Screens"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
12/02/2020 |  | Initial Visit | 800-STS-13880 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [9 empty] | 4.000000 |  | 1.000000 | [5 empty] | Serviced system. Checked the pump, panel, & floats (ok). Cleaned the filter in the Clearstream and cleaned the UV light bulb. Changed the diffuser in the Clearstream, changed the filter in the aerator, and changed the mesh screen in the spinfilter. The timer is set to 4 minutes every 2 hours. Took initial BOD & Fecal samples. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12/02/2020 | Jan 1 1900 12:00PM
12/28/2020 |  | Follow-Up | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Ashleys Septic Service | 1930332 | Shane | Majewski | 1.000000 | 1200 |  |  | Pump | Gravity | Drip | Not Applicable | 600.000000 | ["Dispersal System Operation","Distribution Pump Operation"] | ["Dispersal System Operation","Distribution Pump Operation"] | NO | [16 empty] | Pumped Out | Original report filed 1/18/21- used wrong address (5978) Replace 2 pumps/ 2 check valves, 3 floats, 2 shut off valves/ dig up all lines- Vacuam lines/ install caps- | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 03/31/2021 | Jan 1 1900 12:00AM
10/05/2020 | Alternative | Routine/Scheduled | 166-17-094 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | Advanced Septic |  | Pump | Distribution Box | Aggregate Trench |  | 450.000000 |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Recirculation Pump","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | Musty | Clear | [15 empty] | Routine Service - Anua PuraSys SBR - Primary Septic Tank - normal operating level - acts as sludge return tank from SBR Processing Tank - normal operating level - sludge return pump and controls operating properly - submersible aeration pump operating properly - Discharge pump, float sensors and controls operating properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 10/12/2020 | 08:30 AM
03/06/2020 |  | Routine, Scheduled |  | Buchanan County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Cumberland Plateau | DEEL, DENNY M | 1942001097 | DENNY | DEEL |  |  | Norweco Singulair ATU | None | Gravity | None | Alternative Discharge | Chlorine | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens"] |  | Musty | Clear | [15 empty] | [Comments]: 5 blue crystals,10 bio max,3 rubber | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/16/2020 | Jan 1 1900 11:56AM
06/14/2020 |  | Reportable Incident |  | Virginia Beach | This AOSS should now return to normal function after having provided the above state routine maintenance | Pending Payment | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [9 empty] | ["Blower/Compressor/Aerator Operation","Control Operation"] | ["Blower/Compressor/Aerator Operation","Control Operation"] | N/A | [17 empty] | Replaced aerator | This AOSS should now return to normal function after having provided the above state routine maintenance |  | 06/14/2020 | Jan 1 1900 8:30AM
04/20/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | SES MidAtlantic LLC | 1942001203 | James | Green | 1.000000 |  | Clearstream | Clearstream | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/15/2021 | 09:00 AM
10/23/2020 |  | RoutineScheduled | 13-184-107 | Scott |  |  | EHD - Lenowisco | [11 empty] | UV |  |  |  |  | None | Clear | 8.000000 | 6.000000 | [13 empty] | Jeanette Duncan performed this inspection Tank information was not found No records of maintenance or monitoring |  |  |  | 12:00 AM
07/06/2020 |  | Routine, Scheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Biomicrobics MicroFAST |  |  |  |  | None |  | ["Blower/Compressor/Aerator Operation"] | ["Blower/Compressor/Aerator Operation"] |  | Good | Clear | [5 empty] | 07/06/2020 | Pump tank | 58.000000 | [7 empty] | Pump Amps 11.45 ETM 3 hrs Cycles 20 Water Meter Reading 5500 Septic Sludge 6" Scum 0 ATU Sludge 3" Scum 0 Pump Sludge 0 Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 07/06/2020 | Jan 1 1900 1:55PM
01/06/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Fairfax | BLEVINS, JOEL R, SR | 1934000415 | JOEL | BLEVINS |  |  | Puraflo | Septic Tank Only | None | None | None | None |  | ["None"] | ["None"] | [18 empty] | [Comments]: Peat looks good. Draining well and there is no settlement. Ditches are dry and cleaned the filter. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/07/2020 | Jan 1 1900 10:46AM
08/20/2020 |  | RoutineScheduled |  | Shenandoah | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Control Operation"] | ["Auxiliary Filter" ,"Control Operation"] | NA | [7 empty] | 08/20/2020 |  | 8.000000 | [5 empty] | Will be sent separately | Inspected | Lab Sample Normal Recommend resecuring panel to post | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/26/2021 | 09:04 AM
06/09/2020 |  | RoutineScheduled | 019-STS-24436 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1000 | Advantex AX20RT |  | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | NA | [16 empty] | Inspected | New Install of Advantex AX20RT Setup timer setting for 8 people normal use, 8.4min off 0.8 min on in normal use mode. Alarm functiuonal, New plastic Septic tank noted to have a slight bit of settling already. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 06/10/2020 | 09:30 AM
10/12/2020 | Alternative | Routine/Scheduled | 151-15-0124 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 3.000000 | 3000 | EcoPod |  | Pump | Distribution Box | Aggregate Bed |  |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 10/12/2020 | 02:30 PM
11/04/2020 |  | RoutineScheduled | 107-18-0354 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Onsite Wastewater Services - May Supply | 1942001627 | Drew | Shull | 1.000000 |  | Orenco Advantex | none | Pump | Gravity |  | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 05/28/2021 | 05:41 AM
06/06/2020 |  | RoutineScheduled | 01-192-353 | Tazewell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. |  | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Effluent Screens"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
09/01/2020 | Alternative | Routine/Scheduled | 136-11-0294 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | Serviced system. Checked the pump, panel, & floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. Installed 2 - 6" risers and 1 - 12" x 12" riser on the septic tank. The timer is set to 3 minutes every 2 hours. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 09/01/2020 | 12:00 PM
03/24/2020 |  | Routine, Scheduled |  | Loudoun County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim |  |  | Biomicrobics MicroFAST | None | Pump | Drip | Drip Tubing | [23 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/12/2020 | 02:21 PM
10/07/2020 |  | Routine/Scheduled | 124-STS-2379 | Westmoreland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Rejected | EHD - Rappahannock | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | PremierTech, EFX |  | Pump | None | Aggregate Bed | None | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | Musty | Clear | [15 empty] | Routine Service Primary Septic Tank - normal operating level - replaced access riser - effluent screen serviced. Pump Basin - pump, float sensors and controls operating properly. BioFilter - Peatmoss in good condition - raked / turned | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 10/13/2020 | 07:15 AM
05/20/2020 |  | RoutineScheduled | 182-18-0093 | Rockingham | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Central Shenandoah | Onsite Wastewater Services - May Supply | 1942001022 | Sara | Tusing | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Pressure | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/28/2021 | 05:41 AM
03/25/2020 |  | Routine, Scheduled | 15-120-0498A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesterfield | CARRINGTON, JOHN W, SR | 1934000128 | JOHN | CARRINGTON |  |  | Norweco Singulair ATU | None | Pump | Distribution Box | None | None |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [18 empty] | [Comments]: The alternative system is operating as designed. Lab results not reported by Operator, EHS chose "No" in order to allow saving updated entry. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/24/2020 | Jan 1 1900 4:16PM
10/16/2020 | Alternative | RoutineScheduled | 39799 | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | Musty |  | 6.810000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 10/30/2020 | 03:25 PM
07/17/2020 |  | Initial Visit | 124-STS-2379 | Dinwiddie | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Rejected | EHD - Crater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | Could not service. Need to fix air line from aerator to Clearstream (busted loose under aerator). Need to re-install UV to be able to get the pump out as well as repair the UV - probably bulb. There are septic flies in the panel. Drainfield is dry. Can not get pump out due to the way it is set up. Pressure switch on the aerator is not hooked up. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. |  | 07/17/2020 | Jan 1 1900 12:00PM
09/04/2020 |  | RoutineScheduled | SWP-05-282 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Effluent Screens" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Effluent Screens" ,"Recirculation Pump"] | YES | [15 empty] | Will be sent separately | Inspected | We recommend replacing the Advantex Pod Vent Cap. We also recommend removing the small trees on the uphill side of the drainfield to prevent root intrusions into the drainfield lines. | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 |  | 04/09/2021 | 03:25 PM
10/06/2020 |  | Routine, Scheduled | 175-02-0499 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Orenco Advantex |  |  |  |  | None |  | ["Effluent Screens"] | ["Effluent Screens"] |  | Acceptable | Clear | [15 empty] | Pump Amps 11.35 ETM 721070 Cycles 999999 Pump Amps 11.40 ETM 10487 Cycles 64238 Septic Sludge 9" Scum 0 Pump Sludge 2" Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 10/06/2020 | 05:00 PM
05/12/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/14/2021 | 04:27 PM
05/13/2020 |  | Routine/Scheduled | 18-120-0330AR | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. |  |  | Clearstream |  | Pump |  |  |  |  | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 05/13/2020 | Jan 1 1900 12:00PM
07/22/2020 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU | [6 empty] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  |  | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 07/24/2020 | Jan 1 1900 9:30AM
12/02/2020 |  | Follow-Up | 175-11-0248 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green | [9 empty] | ["None"] | ["None"] | [18 empty] | Installed new PC in control panel. | This AOSS should now return to normal function after having provided the above state routine maintenance |  | 12/02/2020 | 04:00 PM
04/06/2020 |  | Routine/Scheduled | 13-120-0417 VU | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Rejected | EHD - Chesterfield | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | [11 empty] | N/A | [17 empty] | At the time of maintenance, the service expert was not able to locate and inspect the are of the drain field and the distribution box. Our office will obtain a copy of the septic permit to assist in locating it during the next visit. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/06/2020 | Jan 1 1900 11:28AM
05/28/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 2.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/14/2021 | 04:27 PM
05/29/2020 |  | Reportable Incident | 109-16-0148 | Bedford | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central |  |  | joel | pinnix | [9 empty] | ["Control Operation"] | ["Control Operation"] | [8 empty] | 01/01/1900 | [9 empty] | DF pump timer relay fault. Replaced timer relay. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 01/01/1900 | 12:00 AM
04/02/2020 |  | RoutineScheduled |  | Fairfax | This AOSS is functioning as designed and in accord | Approved | EHD - Fairfax | J&G septic |  | James | Kleindl | 1.000000 | 2000 |  |  | gravity | gravity | trenches | N/A |  | [] | [] | NA | None | Clear | [5 empty] | 04/02/2020 | Sample Chamber | 59.000000 | [8 empty] | This AOSS is functioning as designed and in accord |  | 04/20/2020 | 12:00 AM
05/26/2020 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump | Drip | Elevated Sand Mound | UV Light |  | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  | 10.69 | 8.000000 | 7.200000 | [13 empty] | Replaced UV bulb | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 05/26/2020 | Jan 1 1900 12:45PM
05/26/2020 | Alternative | Reportable Incident | 073-STS-106116 | Gloucester | This AOSS should now return to normal function after having provided the above state routine maintenance | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | None | None | Gravity | Distribution Box | Aggregate Trench | None | 450.000000 | ["Dispersal System Operation"] | ["Dispersal System Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | [17 empty] | Septic tank pumped to facilitate distribution box replacement. Replaced failed distribution box with new - spliced existing conveyance line - spliced to existing header lines | This AOSS should now return to normal function after having provided the above state routine maintenance |  | 06/05/2020 | 07:30 AM
04/02/2020 |  | Routine, Scheduled | 2014-143-0140 | Henrico County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Henrico |  |  |  |  | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | [Comments]: Serviced system. Checked the pump, panel, & floats (ok). Cleaned the filter in the Clearstream and cleaned the filter in the aerator. Changed the diffuser in the Clearstream and replaced the relay in the panel. The grade on the pipe in the Clearstream is not okay. The septic tank needs additional risers on it so it can be properly inspected in the future. The timer is set to 4 minutes every 2 hours. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/02/2020 | 12:00 PM
05/15/2020 | Alternative | RoutineScheduled | 40601 | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Greenway Engineering | 1942001008 | Jeremy | Ferguson | 1.000000 | 1000 | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 09/28/2020 | 10:00 AM
05/07/2020 |  | RoutineScheduled | SD-08-426 | Fauquier | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation" ,"Level Sensor Operation" ,"Control Operation"] | ["Level Sensor Operation" ,"Distribution Pump Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | House vacant at time of inspection. In the past 30 days, system averaged 6.7 discharge cycles per day at 1.0 minutes run time. No infiltration observed. House does appear to have water treatment system in crawl space. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
02/05/2020 |  | Reportable Incident | SD-08-418 | Fauquier County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001350 | Mike | Cook |  |  | Orenco Advantex | None | Pump | Distribution Box | [23 empty] | [Comments]: Replaced middle float. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/06/2020 | 10:23 AM
10/30/2020 |  | Reportable Incident | 15-142-0139 | Hanover | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Chickahominy | Old Dominion Onsite, Inc. | 1942001549 | Russell | Revis | [9 empty] | ["Recirculation Pump"] | ["Recirculation Pump"] | N/A | [17 empty] | System is alarming due to high recirc levels. Checked for leaks above the water level. Found two places in Discharge tank riser that are leaking near base of riser. Checked levels in treatment unit and septic tank. Treatment unit was full to the point that recirc water was spilling into discharge, or vice versa. Septic tank water level was high upon arrival, and an additional 2" rise of water level into riser was observed during my visit. Client explained that they had not used water during this time. Septic tank also needs a pumpout as a routine maintenance item, when this is done we should inspect further for leaks. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. |  | 10/30/2020 | Jan 1 1900 10:00AM
10/26/2020 |  | RoutineScheduled | {FIPSCode}-STS-60282 | Caroline | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  | ["Distribution Pump Operation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Attached Growth Medium" ,"Control Operation" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | ["Attached Growth Medium" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Control Operation" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | YES | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
06/09/2020 |  | RoutineScheduled | 44181 | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Greenway Engineering | 1942001008 | Jeremy | Ferguson | 1.000000 | 1000 | Puraflo | None | Pump | Pressure | Trenches | Not Applicable |  | ["Attached Growth Medium","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 07/21/2020 | 08:30 AM
02/12/2020 |  | Routine, Scheduled | 234-13-388 | Chesapeake | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Chesapeake | R & K Septic, Inc. |  | John | Butt, Jr |  |  | Clearstream ATU |  | Pump | Drip | Elevated Sand Mound | UV Light |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] |  |  | 46.2 | 7.590000 | 4.000000 | [13 empty] | [Comments]: Needs new UV Bulb and UV Quartz | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 02/12/2020 | Jan 1 1900 2:30PM
08/20/2020 |  | RoutineScheduled | 181-08-0192 | Rockbridge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Hunter E. Ayres, General Contractor | 1942001166 | Hunter | Ayres | 1.000000 | 1000 | Biomicrobics MicroFAST |  | Pump | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter","Effluent Screens"] | ["Auxiliary Filter","Effluent Screens"] | YES | [17 empty] | Filters checked and cleaned. No apparent leaks in system or drain field area. System did not need to be pumped. Control panels functioning properly. Lids properly secured | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 09/08/2020 | 07:10 PM
05/19/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/27/2021 | 01:26 PM
02/12/2020 |  | Routine, Scheduled | {FIPSCode}-STS-21544 | Hanover County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chickahominy | Old Dominion Onsite, Inc. |  | Jason | Hackler | 1.000000 | 1000 | Orenco Advantex |  | Pump | Distribution Box | Gravel-Less Trench | None |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | [18 empty] | [Comments]: Filter clogged water level high in septic tank. removed filter and cleaned. cleaned manifold and sprayers. cleaned pump screen. Some growth in the recirc chamber. system appears to be operating normally. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/12/2020 | Jan 1 1900 1:46PM
06/11/2020 |  | Routine/Scheduled | 199-04-0022 | York | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Peninsula | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | Ecoflo | None | Pump | Distribution Box | Aggregate Trench | None |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | The Filter in the Septic Tank is outdated (we recommend its replacement during your next schedule pumping service), and the Riser was found broken; the Ecoflo Biofilter has severely deteriorated and is no longer properly filtering water | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 06/16/2020 | Jan 1 1900 12:39PM
06/26/2020 |  |  | {FIPSCode}-STS-11298 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | WasteMaster |  | Timothy | Jenkins | 2.000000 |  | ATU | Polishing Sand Filter | Pump | Gravity | Discharge | Chlorination |  | [] | [] |  | Musty | Clear | 7.000000 |  |  | 2.100000 | [12 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 06/26/2020 | 09:25 AM
04/01/2020 |  | RoutineScheduled | 182-18-0305 | Rockingham | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Central Shenandoah | Onsite Wastewater Services - May Supply | 1942001022 | Sara | Tusing |  |  | Orenco Advantex | none | Pump | Gravity |  | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/28/2021 | 05:41 AM
11/30/2020 |  | Routine/Scheduled | 2008-143-0096 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Old Dominion Onsite, Inc. | 1942001549 | Russell | Revis | [9 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump"] | N/A | [17 empty] | Cleaned manifolds, recirc filter and RSV. Checked float and pump operation. Replaced two vent caps that have been damaged by a dog. System seems to be working properly. 4.7 avg overrides/30days | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 11/30/2020 | 12:50 PM
05/08/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/27/2021 | 01:26 PM
01/30/2020 |  | Routine, Scheduled | 16-100-0313 | Accomack County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Eastern Shore | DUNN, PHILLIP H | 1942001189 | PHILLIP | DUNN | 1.000000 | 1000 | Eljen Geotextile Sandfilter | None | Pump | Manifold | Aggregate Trench | None |  | ["Effluent Screens"] | ["Effluent Screens"] | [18 empty] | [Pumpout Comments]: Sludge judge test revealed 2 inches of oily film in the septic tank. No pumping is required at this time. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/31/2020 | 08:36 AM
07/02/2020 |  | Initial Visit | 04-174-0173 | Prince George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Crater | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1500 | Norweco Singulair ATU |  | Pump | Distribution Box | Aggregate Trench | None | 450.000000 |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | Musty | Clear | [15 empty] | System pumped for inspection / service Last documented / known service conducted 2014 by Coastal Plains Environmental Group. Processing tank (Septic, Aeration, Clarifier) pumped empty for inspection - aspirator serviced - effluent screen serviced - system refilled with fresh water. Discharge tank pumped empty for inspection and service - pump, float sensors and control panel appear to be operating properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 07/07/2020 | Jan 1 1900 8:30AM
08/17/2020 |  | Routine/Scheduled | 09-120-0253A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesterfield | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 500 | Hoot | None | Pump | Drip | Drip Tubing | None | 600.000000 |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | Musty | Clear | [15 empty] | Pumped trash tank empty for inspection. Real Estate Transfer Inspection / Service Pumped 500g from trash tank Aeration operating properly - serviced air compressor Discharge operating properly - discharge pump serviced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 08/18/2020 | Jan 1 1900 7:30AM
06/17/2020 |  | Reportable Incident | 16-172-0413A | Powhatan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesterfield | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | Orenco Advantex |  | Pump | Drip | Drip Tubing | UV Light | 600.000000 |  | ["Disinfection"] | N/A | Musty | Clear | [15 empty] | Processing Tank pumped for evaluation for real estate transfer - Alarm event from Sunday 06/14/2020 was for the U.V. Disinfection bulb had failed - 06/17/2020 - U.V. Bulb replaced and system placed back into 100% operational status. 06/25/2020 - Real Estate Inspection conducted for property transfer. Processing tank pumped for inspection by Premier Septic. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 06/26/2020 | Jan 1 1900 8:00AM
05/04/2020 |  | RoutineScheduled | SD-01-698 | Fauquier | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Level Sensor Operation"] | ["Control Operation" ,"Level Sensor Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced damaged riser on sample box and installed new lid (old one gone). Two pods had 2-3 inches of standing water, big pockets in other two. Septic tank needs pumped but can wait a few months until peat is replaced. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
09/22/2020 |  |  |  | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Environmental Systems Service | 19420001050 | Troy | Jenkins | 2.000000 |  | Septic Tank | Septic Tank |  |  | Drip |  | 1542.000000 | [] | [] |  |  |  | 7.490000 |  |  |  |  | 09/22/2020 | Sample Tap | 12.000000 |  |  | 33.000000 | 75.900000 |  | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 10/15/2020 | Jan 1 1900 3:00PM
03/11/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS should now return to normal function after having provided the above stated routine maintenance. | Paid | EHD - Fairfax | SEAMON, CHARLIE L | 1942001108 | CHARLIE | SEAMON |  |  | Septic Tank Only | Microfast | Pump | Manifold | Drip Tubing | None |  | ["BlowerCompressorAerator Operation","Dispersal System Operation"] | ["BlowerCompressorAerator Operation"] | [18 empty] | [Comments]: Performance Inspection:Microfast to American Drip. Septic-10"sludge 3"scum/Microfast-14"sludge/Pump tank-3"sludge.Need pump out of the Septic/Fast tank. Blower air filter cleaned.Broken drip tubing under walk path needs repair. Counts:Z1-819/Z2-814/Z3-808/Z4-819/Pump-3263 ETM-396h 35m/Peak-31 3h 43m/ Water meter-0246542.61 | This AOSS should now return to normal function after having provided the above stated routine maintenance. |  | 04/07/2020 | Jan 1 1900 5:48AM
07/13/2020 |  | Follow-Up | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance | Approved | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green | [9 empty] | ["Dispersal System Operation"] | ["Dispersal System Operation"] | [18 empty] | Put lower zone back in service. | This AOSS should now return to normal function after having provided the above state routine maintenance |  | 07/13/2020 | Jan 1 1900 8:30AM
10/13/2020 |  | RoutineScheduled | 2009-143-0158 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Microfast | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 10/23/2020 | 12:00 AM
11/17/2020 |  | Routine, Scheduled | 153-STS-20297 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | EZ Treat Sandfilter |  |  |  |  | None |  | ["Effluent Screens"] | ["Effluent Screens"] |  | Acceptable | Clear | [5 empty] | 11/17/2020 | Pump tank | 5.000000 | [7 empty] | Pump Amps 10.49 Water Meter Reading 37900 Septic Sludge 8" Scum 1" ATU Sludge 0 Scum 0 Pump Sludge 0 Scum 0 On 7 mins 47 secs Off 2hrs 52 mins Drainfield has soft spots. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 11/17/2020 | 10:45 AM
01/30/2020 |  | Routine, Scheduled | 069150393 | Frederick County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Lord Fairfax | Ferguson, Jeremy | 1942001008 | Jeremy | Ferguson | 1.000000 | 1500 | Microfast | None | Pump | Drip | Drip Tubing | None |  |  | ["BlowerCompressorAerator Operation","Control Operation","SludgeScum Accumulation"] | [18 empty] | [Comments]: System is in compliance with approved plans and health department regulations. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/30/2020 | 12:51 PM
05/29/2020 |  | RoutineScheduled | 15-113-047 | Buchanan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | Septic Inc |  | Denny | Deel |  |  | Norweco |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
09/25/2020 |  | RoutineScheduled | SWP-04-884 | Spotsylvania | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Rappahannock | Wastemaster Inc |  | Timothy | Jenkins | 2.000000 |  |  |  | Pump | Pressure | Drip |  |  | [] | [] | [18 empty] | In for alarm. Found pump tank high level. checked pump and controls. pump weak. added some time to pump cycle. owner reported out of alarm. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 10/08/2020 | 01:15 PM
07/31/2020 |  | RoutineScheduled | {FIPSCode}-STS-12560 | Clarke | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Greenway Engineering | 1942001008 | Jeremy | Ferguson | 1.000000 | 1250 | LPD | none | Pump | Pressure | Trenches | Not Applicable |  | ["SludgeScum Accumulation","Level Sensor Operation"] | ["SludgeScum Accumulation","Level Sensor Operation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 07/31/2020 | 03:45 PM
01/22/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Puraflo |  |  |  |  | None |  | ["Effluent Screens"] | ["Effluent Screens"] | [18 empty] | [Comments]: Pump 1 Amps 13.44 ETM 255.18h Cycles 62226Pump 2 Amps 14.23 ETM 161.07h Cycles 62156Septic Sludge 2" Scum 1"Pump Sludge 1" Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/22/2020 | Jan 1 1900 11:15AM
01/03/2020 |  | Routine, Scheduled |  | Warren County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Lord Fairfax | Cubbage, Harrison Lee, II | 1942001021 | Harrison | Cubbage | 1.000000 | 1500 | Septic Tank Only | Biomicrobics MicroFAST | Gravity | Distribution Box | Aggregate Trench | None |  | ["Attached Growth Medium","BlowerCompressorAerator Operation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation"] |  | Musty | Clear | [15 empty] | [Comments]: Blower starting to make mechanical noises please keep eye on and make sure keeps running. Will schedule pumping of tanks at time of service in 2021 Sludge/Scum Accumulations: Comp.1-16"/2" Comp.2- 16"/0" | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/18/2020 | 11:55 AM
05/04/2020 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump | Distribution Box |  | UV Light |  | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | Replaced UV bulb & UV ballast. Repaired air line. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 05/04/2020 | Jan 1 1900 6:15PM
10/07/2020 |  | RoutineScheduled | 107-10-0114 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Inboden Environmental Services, Inc | 1942001083 | Terry | Inboden | [8 empty] | 4535.000000 | [] | [] |  |  |  | 7.280000 | 8.450000 | 22.000000 | [13 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 11/06/2020 | 02:30 PM
12/29/2020 |  | Routine/Scheduled | 15-120-0260A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 1.000000 |  | Aqua Klear |  | Pump |  |  |  |  | ["Control Operation","Distribution Pump Operation","Septic Tank Baffles"] | ["Control Operation","Distribution Pump Operation","Septic Tank Baffles"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 12/29/2020 | Jan 1 1900 8:00AM
09/18/2020 |  | RoutineScheduled | 099-06-0342-SWP | King George | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | EcoPod | none | Pump | Gravity | Drip | Not Applicable |  | ["Attached Growth Medium" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | ["Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Level Sensor Operation" ,"Attached Growth Medium" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced air filter. Recommend pumping within 6 months. A few trees on mound, homeowner will remove trees, patch hole on headworks box and schedule pump out of septic tank. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
05/13/2020 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 | Pending Payment | EHD - Loudoun | WasteMaster, Inc. | 1942001062 | Tim | Jenkins | 1.000000 |  | Delta Environmental Products, DF Series | Delta Environmental Products, DF Series | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 |  | 06/21/2021 | 10:37 AM
10/26/2020 |  | RoutineScheduled | 08-192-132 | Tazewell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Effluent Screens"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
05/15/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | SES MidAtlantic LLC | 1942001236 | S. Michael | Lynn | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Dispersal System Operation" ,"Effluent Screens"] | ["Effluent Screens" ,"Dispersal System Operation"] | YES | [15 empty] | Will be sent separately | Inspected | One distribution box was found to be cracked and was replaced with permit from LCHD | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/15/2021 | 09:00 AM
09/30/2020 |  | Follow-Up | SP-04-100 | King George | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Ecoflo | none | Pump | Gravity | Pad | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Replaced broken effluent filter. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
07/21/2020 |  | RoutineScheduled |  | Buckingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Piedmont | Enviro-Klean Co. | 1942001087 | michael | clark |  |  |  |  | Pump | Pressure | Drip | Not Applicable |  | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
02/12/2020 |  | Routine, Scheduled |  | Louisa County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Blue Ridge | Old Dominion Onsite, Inc. |  | Robert | Nicholas | [9 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump"] | [18 empty] | [Comments]: Cleaned Effluent filter, flushed manifold. checked pump and float operation. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/12/2020 | 11:10 AM
05/22/2020 |  | RoutineScheduled | 179-13-0214-SP | Stafford | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Recirculation Pump" ,"Attached Growth Medium"] | ["Effluent Screens" ,"Recirculation Pump" ,"Attached Growth Medium"] | YES | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/09/2021 | 03:25 PM
07/14/2020 |  | RoutineScheduled | 109-10-0153 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1000 | Puraflo |  | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | NA | [16 empty] | Inspected | Corrected plumbing issue, uncrossing the pump up and drain line. This should fix the issue with peat moss not draining. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 07/15/2020 | 09:30 AM
01/10/2020 |  | Routine, Scheduled |  | King William County | This AOSS should now return to normal function after having provided the above stated routine maintenance. | Paid | EHD - Three Rivers | FRERE, FRANCIS B, JR | 1942001144 | FRANCIS | FRERE | 1.000000 | 1000 | Septic Tank Only | Clearstream ATU | Pump | Distribution Box | Aggregate Trench | None | 450.000000 | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | [Comments]: Clearstream alarm had been sounding, air pump locked up. Replaced pump, performed system maintenance. Clearstream Settleable Solids 90%, aerator not working approximately 3 weeks. Stirred up scum layer, will re-check SS in 2-3 weeks, and pump treatment unit if SS not below 50%. ST- 2" FOG, 4" sludge, PT- alarm, floats, pump operating properly. | This AOSS should now return to normal function after having provided the above stated routine maintenance. |  | 01/21/2020 | 08:15 PM
03/19/2020 |  | Initial Visit | 177-STS-87214 | Spotsylvania County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | None | None | Pump | [24 empty] | [Comments]: START-UP INSPECTION | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/06/2020 | 02:45 PM
05/05/2020 |  | RoutineScheduled | 181-06-0227 | Rockbridge | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central Shenandoah | Hunter E. Ayres, General Contractor | 1942001166 | Hunter | Ayres | 1.000000 | 1500 | Biomicrobics Microfast |  | Gravity | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","SludgeScum Accumulation","Auxiliary Filter"] | ["Auxiliary Filter","Attached Growth Medium","SludgeScum Accumulation"] | NA | [16 empty] | Pumped Out | Media block sprayed off. Sump pump no longer into system. No apparent leaks in system or drain field area. Control panel functioning properly. Blower filter cleaned. System pumped and cleaned. Lids properly secured. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 06/20/2020 | 09:30 AM
03/27/2020 |  | Reportable Incident | 234-15-111 | Chesapeake | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Chesapeake | Farmer's Septic Service, Inc. |  | Ross | Cole | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | [Comments]: Owner called due to the alarm going off. Serviced system. Checked the pump, panel, & floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. Installed a re-build kit on the aerator. The UV (Salcor) is not working - burnt up - only the tube is there. The septic tank needs additional risers on it so it can be properly inspected in the future. The timer is set to 1.25 minutes every 2 hours. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 03/27/2020 | Jan 1 1900 12:00PM
06/10/2020 |  | RoutineScheduled | 107-10-0114 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Inboden Environmental Services, Inc | 1942001083 | Terry | Inboden | [8 empty] | 1009.000000 | ["None"] | ["None"] |  |  |  | 7.710000 | 8.180000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 07/29/2020 | 12:00 AM
03/02/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Fairfax | MAJEWSKI, SHANE | 1934000134 | SHANE | MAJEWSKI | 1.000000 | 1200 | Septic Tank Only | Septic Tank Only | Pump | Distribution Box | Aggregate Trench | None | 450.000000 | ["Level Sensor Operation"] | ["Level Sensor Operation"] | [18 empty] | [Comments]: Replace 2 check valves Clean pump Chamber Maintenance Inspection Clean Filter | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/03/2020 | Jan 1 1900 1:18PM
01/20/2020 |  | Routine, Scheduled | 18-120-0186A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesterfield | Dominion Septic, Inc | 1942001350 | Mike | Cook | 2.000000 |  | Norweco Singulair ATU | None | Pump | Distribution Box | Aggregate Trench |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Lab results not reported by Operator, EHS chose "No" in order to allow saving updated entry. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/28/2020 | Jan 1 1900 1:39PM
09/25/2020 |  | RoutineScheduled | {FIPSCode}-STS-2095 | Warren | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Lord Fairfax | Onsite Wastewater Services - May Supply | 1942001022 | Sara | Tusing | 1.000000 |  | Orenco Advantex | none | Pump | Gravity |  | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Inspected DKS | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/28/2021 | 05:41 AM
11/23/2020 |  | RoutineScheduled |  | Warren | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity |  | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation"] | ["BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Added solution and snaked line between microfast tank and pump tank to clear a clog | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance |  | 04/26/2021 | 09:04 AM
03/12/2020 |  | Routine, Scheduled |  | Loudoun County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | None | None | Pump | Distribution Box | Aggregate Trench | [23 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/16/2020 | 11:28 AM
03/03/2020 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 | Pending Payment | EHD - Loudoun | WasteMaster, Inc. | 1942001062 | Tim | Jenkins |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | System Operating Properly at time of inspection | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 |  | 06/21/2021 | 10:37 AM
09/21/2020 |  | Reportable Incident | 154-12-0156 | Louisa | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Blue Ridge | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | ["Level Sensor Operation" ,"Control Operation" ,"Distribution Pump Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Septic tank just beginning to overflow, no alarm from control panel. Circuit board had visible damage and blown fuse. Second time board has failed. Replaced control panel and completed annual inspection. Treatment looks good in atu, but blower is making an intermittant raspy bearing sound. Grass is a little tall in drainfield, recommend cutting. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
04/29/2020 |  | Follow-Up | 099-18-0122 C-SWP | King George | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart |  |  | Orenco Advantex | none | Pump | Gravity | Drip | UV |  |  |  | NA | [9 empty] | 41.000000 |  | 88.000000 |  |  |  | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
12/12/2020 |  |  | {FIPSCode}-STS-11802 | Culpeper | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC |  | Jason | Brown | 2.000000 | 1250 | septic | sand filter | Gravity | Pressure | Discharge | Chlorination |  | [] | [] | YES | Musty | Cloudy | [14 empty] | Pumped Out |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 01/06/2021 | 03:40 PM
06/10/2020 |  | RoutineScheduled | 113-18-074 | Madison | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | ESS | 194200001050 | Troy | Jenkins | 2.000000 | 1500 | Septic Tank Only | Septic Tank Only |  | Pressure | Drip |  | 1599.000000 | ["None"] | [] |  |  |  | 7.160000 |  |  |  |  | 06/10/2020 | Sample Tap | 9.000000 |  |  | 1.800000 | 34.310000 |  | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 07/17/2020 | 03:22 AM
07/30/2020 |  | RoutineScheduled | 12-113-145 | Buchanan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  |  | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Effluent Screens"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
08/17/2020 |  | RoutineScheduled | 182-04-0173 | Rockingham | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Central Shenandoah | Onsite Wastewater Services - May Supply | 1942001022 | Sara | Tusing | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Pressure | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/28/2021 | 05:41 AM
05/12/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | pump tank needs pumped out | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 |  | 04/14/2021 | 04:27 PM
04/20/2020 |  | Follow-Up | SD-14-166 | Fauquier | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [9 empty] | 63.000000 | [5 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
02/20/2020 |  | Routine, Scheduled | SWP 97-210 | Spotsylvania County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | None | None | Pump | Drip | Drip Tubing |  |  | ["Auxiliary Filter","Dispersal System Operation","Distribution Pump Operation"] | ["Auxiliary Filter","Dispersal System Operation","Distribution Pump Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/06/2020 | 02:45 PM
03/25/2020 |  | Routine, Scheduled | 17-120-0335A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesterfield | CARRINGTON, JOHN W, SR | 1934000128 | JOHN | CARRINGTON |  |  | Norweco Singulair ATU | None | Pump | Distribution Box | None | None |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [18 empty] | [Comments]: The alternative system is operating as designed. Lab results not reported by Operator, EHS chose "No" in order to allow saving updated entry. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/24/2020 | Jan 1 1900 4:19PM
09/17/2020 |  | Routine, Scheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Puraflo |  |  |  |  | None |  | ["Effluent Screens"] | ["Effluent Screens"] | [18 empty] | Pump 1 Amps 14.60 ETM 107 hrs 49 mins Cycles 5607 Pump 2 Amps 14.20 ETM 106 hrs 47 mins Cycles 5481 Septic Sludge 12" Scum 0.50 Pump Sludge 3" Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 09/17/2020 | Jan 1 1900 2:35PM
06/29/2020 |  | RoutineScheduled | 179-14-0229-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | EcoPod | none | Pump | Gravity | Drip | Not Applicable |  | ["Distribution Pump Operation" ,"Dispersal System Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Disinfection" ,"Dispersal System Operation" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 |  | 04/09/2021 | 03:25 PM
01/27/2020 |  | Routine, Scheduled | SD-10-247 | Fauquier County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | JENKINS, TROY C, JR | 1942001050 | TROY | JENKINS |  |  | Septic Tank Only | Septic Tank Only | None | None | None | None | 13535.000000 | ["Control Operation"] | ["Control Operation"] |  |  |  | 7.110000 |  |  |  |  | 01/27/2020 | Effluent | 2.000000 |  |  | 11.600000 | 15.880000 |  | Attached to this report |  | [Pumpout Comments]: Was not pumped in Jan VENIS File Names: Suffield.pdf | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/14/2020 | 12:27 PM
02/20/2020 |  | Routine, Scheduled | 033-17-0119-SP | Caroline County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | None | Pump | Distribution Box | Aggregate Bed |  |  | ["Attached Growth Medium","Effluent Screens","Recirculation Pump"] | ["Attached Growth Medium","Effluent Screens","Recirculation Pump"] | [18 empty] | [Comments]: The Advantex pod vent cover is broken and should be replaced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/02/2020 | 11:52 AM
11/06/2020 |  | RoutineScheduled | 03-192-073 | Tazewell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | WHITEWATER |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
08/10/2020 |  | RoutineScheduled | 10-100-0464 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Bundick Well & Pump | 1942001051 | Peter | Duer | 1.000000 | 1500 | Septic Tank | Bio-Coir | Pump | Pressure | Pad | UV | 450.000000 | ["None"] | ["None"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 08/13/2020 | 12:40 PM
06/26/2020 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintanence requirements | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Sale inspection on a Conventional Gravity septic system This house has been vacant for several months. There are no clean outs. The sewer line was camera snaked and clear. The septic tank was pumped out and inspected for any leaks or cracks none were found. The plastic 9 port d-box was dug up it was 40" in the ground. The header lines were camera snaked and 5 out 0f 6 lines were clogged with roots. They will need dug up and the roots removed or new section of header lines installed. At time of inspection septic system was not in working condition. | This AOSS is not functioning as designed or in accordance with the performance/maintanence requirements |  | 04/14/2021 | 04:27 PM
08/21/2020 |  |  | 39029 | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 2705110225 | Larry | Royston | [9 empty] | ["None"] | ["None"] | YES | [16 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 09/02/2020 | 12:00 AM
09/16/2020 |  | Pump-Out Only |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | POWELLS PLUMBING, INC. | 1942001036 | Kurt | Holthaus |  |  | Orenco Advantex | [6 empty] | ["Sludge/Scum Accumulation"] | ["Sludge/Scum Accumulation"] | N/A | [17 empty] | Pumped septic. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 10/08/2020 | 01:25 PM
02/18/2020 |  | Routine, Scheduled |  | Loudoun County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Loudoun | Triple R Construction Co., Inc. | 1934000238 | Charles | Seamon | 1.000000 |  | Biomicrobics MicroFAST | None | Pump | Distribution Box | Aggregate Trench |  |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | [18 empty] | [Comments]: Recommend adding grass seed to the drainfield bare spots. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/25/2020 | 11:44 AM
06/18/2020 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump | Distribution Box |  |  |  | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  |  | 7.000000 | 5.000000 | [13 empty] | UV isn't working | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 06/18/2020 | Jan 1 1900 8:30AM
11/30/2020 |  | Routine/Scheduled | 800-STS-14487 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Western Tidewater | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 9000 | Advanced Septic | None | Pump | Distribution Box | Aggregate Trench | None | 4500.000000 |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Recirculation Pump","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | Musty | Clear | [5 empty] | 11/30/2020 | Clarifier Outfall | [8 empty] | Monthly service visit - lab sampling Primary Septic tank - normal operating level - both pumps pulled and serviced - float sensors and controls operating properly. Aeration Tank - normal operating level - compressor #1 & #3 serviced. Clarifier - overgrown - normal operating level. Pump tank - normal operating level - both pumps pulled and serviced - pump #1 clogged with gumballs Lab samples obtained for BOD5 and TSS and transported to Universal Laboratories. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 12/01/2020 | Jan 1 1900 8:30AM
03/24/2020 |  | Routine, Scheduled |  | Loudoun County | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Paid | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim |  |  | None | None | Pump | Distribution Box | Aggregate Trench | [5 empty] | NO | NO | [15 empty] | [Comments]: Pump tank needs pumped out | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 04/12/2020 | 02:21 PM
10/12/2020 |  | Routine/Scheduled |  | Frederick | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Lord Fairfax | POWELLS PLUMBING, INC. | 1942001036 | Kurt | Holthaus | 1.000000 | 1250 | Microfast |  | Pump | Drip | Drip Tubing |  | 600.000000 | ["Blower/Compressor/Aerator Operation","Control Operation"] | ["Blower/Compressor/Aerator Operation","Control Operation"] | N/A | [17 empty] | Real Estate Sale Inspection - Installed new Microfast control box and repaired conduit at blower. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 11/17/2020 | 10:44 AM
07/01/2020 |  | Routine/Scheduled | 087-STS-6315 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Henrico | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1500 | Orenco Advantex |  | Pump | Distribution Box | Aggregate Trench | None | 450.000000 | ["Recirculation Pump"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | Musty | Clear | [15 empty] | Alarm Event - Routine Service Conducted while correcting alarm condition ... Processing tank found to be in high level due to fracture in recirc forcemain - repaired while on property. Full service conducted - RSV, Effluent Screen & recirc pump serviced. AdvanTex media serviced - spray grid serviced. Discharge tank pump serviced. Distribution box in normal level and balanced properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 07/07/2020 | 08:00 AM
02/04/2020 |  | Routine, Scheduled |  | James City County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Peninsula | Madison Environmental LLC | 1934 000061 | Larry | Madison, Jr. |  |  | Puraflo |  | Pump |  |  |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | [Comments]: Need to replace cord grippers during next site visit. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/04/2020 | Jan 1 1900 12:30PM
05/01/2020 |  | RoutineScheduled | 069051088 | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Combs Wastewater Management LLC | 1942001353 | Amy | Combs | 2.000000 | 1000 |  | Microfast | Pump | Pressure | Drip | Not Applicable | 450.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 05/01/2020 | 12:00 AM
07/20/2020 |  | Follow-Up | SWP-97-356 | Spotsylvania | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Replaced #1 blue valve. Replaced diaphragm for BF valve #1. Replaced all 3 brass globe valves in sand filters. Repaired H-pipe in sand filter 1,2 & 3 and replaced screens. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
07/20/2020 |  | Routine, Scheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green | [9 empty] | ["Effluent Screens"] | ["Effluent Screens"] | [18 empty] | Spin filter cleaned. Pump Amps 8.46/8.68 Water Meter Reading 675550 Septic Sludge 10" Scum 1" Pump Sludge 2" Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 07/20/2020 | Jan 1 1900 12:45PM
03/02/2020 |  | Routine, Scheduled | {FIPSCode}-STS-17219 | Wise County | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Lenowisco | DEEL, DENNY M | 1942001097 | DENNY | DEEL |  |  | Clearstream ATU | None | Gravity | None | Alternative Discharge | Chlorine | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Level Sensor Operation"] |  | Musty | Clear | [15 empty] | [Comments]: No Power on atu nobody lives there | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 03/03/2020 | Jan 1 1900 10:43AM
04/01/2020 |  | Routine, Scheduled | 2005-143-0250 | Henrico County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Henrico | [8 empty] | Pump |  |  |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/01/2020 | 11:00 AM
06/19/2020 |  | Initial Visit | VAG408017 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | [6 empty] | tank only | Multi Flo | Gravity | Gravity | Discharge | Chlorination |  | ["Attached Growth Medium","BlowerCompressorAerator Operation","Auxiliary Filter"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Auxiliary Filter"] | [18 empty] | replaced socks, aerator | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 06/19/2020 | 12:00 AM
10/20/2020 |  | Follow-Up | 69080360 | Frederick | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Lord Fairfax | Greenway Engineering | 1942001008 | Jeremy | Ferguson | 1.000000 | 1500 | Advantex |  | Pump | Pressure | Trenches | Not Applicable |  | [] | ["Attached Growth Medium","Effluent Screens","Recirculation Pump"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 11/03/2020 | 12:00 AM
10/30/2020 |  | RoutineScheduled | 13-183-116 | Russell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Effluent Screens"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
07/07/2020 |  | Follow-Up | {FIPSCode}-STS-67316 | Spotsylvania | This AOSS is not functioning as designed or in accordance with the performance/Maintenance requirements | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  | ["Distribution Pump Operation" ,"Control Operation" ,"Dispersal System Operation" ,"Attached Growth Medium" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Control Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | Follow-up visit to annual inspection. Upon arrival, the drip pump breaker was tripped. Reset breaker and pump returned to normal operation. Air pump is not working and should be replaced. Bush that was crowding headworks box and spin filter housing has been removed. We moved the headworks box for future service and cleaned the spin filter today. | This AOSS is not functioning as designed or in accordance with the performance/Maintenance requirements |  | 04/09/2021 | 03:25 PM
03/03/2020 |  | Reportable Incident | 181-12-0006 | Rockbridge County | This AOSS should now return to normal function after having provided the above stated routine maintenance. | Approved | EHD - Central Shenandoah |  |  |  |  | 1.000000 | 1500 |  | Orenco Advantex | Pump | Drip | Drip Tubing | None |  | ["Dispersal System Operation"] | ["Dispersal System Operation"] | [18 empty] | [Comments]: The System did not need to be pumped. The RSV split valve and effluent filter clogged causing low level alarms in the recirculating tank. The valve, filter, and recirculating pump were all pulled and cleaned. Water was then put in the tank to normal operating levels. Lids were properly secured. | This AOSS should now return to normal function after having provided the above stated routine maintenance. |  | 03/10/2020 | 30-12-1899 06:08 PM
11/10/2020 |  | RoutineScheduled |  | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001301 | Joshua | Hott | [9 empty] | [] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
11/05/2020 |  | RoutineScheduled | C-122-08-0034 | Craig | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | King's Alternative Septic | 1942001112 | William | King, II | 1.000000 | 1000 | Biomicrobics Microfast 0.5 |  | Pump | Gravity | Trenches | Not Applicable | 250.000000 | ["None"] | ["None"] | NA | [17 empty] | System is working correctly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 11/17/2020 | 12:00 AM
12/22/2020 |  | Routine/Scheduled | 175-05-0325 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Aquarobic Mini Plant |  |  |  |  | Not Applicable |  | ["Blower/Compressor/Aerator Operation"] | ["Blower/Compressor/Aerator Operation"] | N/A | None | Clear | [15 empty] | Pump Amps 7.2 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 12/22/2020 | 10:00 AM
06/04/2020 |  | Pump-Out Only |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | POWELLS PLUMBING, INC. | 1942001036 | Kurt | Holthaus |  |  | Puraflo | [6 empty] | ["Sludge/Scum Accumulation"] | ["Sludge/Scum Accumulation"] | N/A | [17 empty] | Pumped pump chamber. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 06/19/2020 | 02:21 PM
03/25/2020 |  | Routine, Scheduled |  | Loudoun County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | None | None | Pump | Distribution Box | Aggregate Trench | [23 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/12/2020 | 02:21 PM
12/02/2020 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump | Distribution Box |  | None |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  |  | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 12/02/2020 | Jan 1 1900 4:00PM
05/15/2020 |  | RoutineScheduled | 171-06-0632 | Pittsylvania | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Pittsylvania-Danville | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Puraflo |  | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | NA | [16 empty] | Inspected | Sludge level-1-2" scum layer on top-12" sludge on bottom in Septic tank - upon initial arrival i found the pump breaker tripped, I observed the pump run time had increased 5,924 hours since last year. I found the pump was locked up and not working. Pump ct 15228 Hour meter 6049.84Hr , Last year pump hr reading was 125.73 hrs based on this reading the pump ran for 246 days straight and in 6,101 events. After obtaining a new 2 HP pump from Vamac we returned, replaced the pump, replaced the check valve which had also failed and likely due to the constant cycling of the pump sending water up top with a bad check valve the peat pods were flooded and standing with water. After time they should return to normal but will be looked into again next year during the inspection incase the slightest chance the systme was installed wrong. It is possible an issue with the pods plumbing exhists. I base this soley on a past issue at another clients home and on an inspection Danny Hylton had done prior and to our May 1 5 inspection. I found the installer had accidently connected the pump to the drain line and drain line to the pump, Hence the peat pods filled with water in reverse. I will look into this again when we return for your next inspection. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 05/30/2020 | 09:30 AM
02/21/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Fairfax | MCKIM, STEPHEN E | 1934000043 | STEPHEN | MCKIM |  |  | Septic Tank Only | Septic Tank Only | None | None | None | None | [21 empty] | [Pumpout Comments]: Septic tank pumped out | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/22/2020 | Jan 1 1900 2:23PM
12/31/2020 | Alternative | Routine/Scheduled | 171-13-0271 | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | POWELLS PLUMBING, INC. | 1942001036 | Kurt | Holthaus | 1.000000 | 2000 | Microfast |  | Pump | Pressure | Drip |  | 450.000000 | ["Auxiliary Filter","Blower/Compressor/Aerator Operation","Sludge/Scum Accumulation"] | ["Auxiliary Filter","Blower/Compressor/Aerator Operation","Sludge/Scum Accumulation"] | YES | [16 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 01/15/2021 | 12:24 PM
06/23/2020 |  |  | 09-192-012 | Tazewell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 06/23/2020 |  | 10.300000 |  |  | 2.500000 |  |  | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 06/23/2020 | 12:00 AM
06/03/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | SES MidAtlantic LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Gravity | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/15/2021 | 09:00 AM
09/24/2020 |  | Routine/Scheduled | S 800-11-0023 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Western Tidewater | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | PremierTech, EFX |  | Pump | None | Aggregate Bed | None | 450.000000 | ["Attached Growth Medium"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | Musty | Clear | [15 empty] | Real Estate Inspection. Primary Septic Tank - normal operating level - effluent screen serviced. Pump Basin - normal operating level - pump, float sensors and controls operating properly. Peatmoss Biofilter - peatmoss broken down - requires replacement - turned and raked as best as possible. Distribution box - plastic - fractured - 4 absorption laterals present. Marked as "Good" as there is no surfacing of effluent present and not backing up into residence. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 10/06/2020 | Jan 1 1900 7:30AM
12/03/2020 |  | Routine/Scheduled | 04-120-0180AR | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesterfield | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 2.000000 | 2000 | Orenco Advantex |  | Pump | Distribution Box | Aggregate Trench | None | 600.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | None | Clear | [15 empty] | Routine Service Primary septic tank - normal level Secondary septic tank - normal level Processing Tank - normal operating level - RSV, Recirc Pump, Effluent screen serviced. Treatment Module - Media drapes & spray grid serviced. Pump Tank - normal level - pump, float sensors & controls operating properly. Distribution box - concrete - intact - all laterals accepting effluent. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 12/04/2020 | Jan 1 1900 7:45AM
03/03/2020 |  | Routine, Scheduled | 179-08-0136-SR | Stafford County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001350 | Mike | Cook |  |  | Orenco Advantex | None | Pump | Distribution Box | Aggregate Trench |  |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/06/2020 | 05:29 AM
03/19/2020 |  | Routine, Scheduled |  | Loudoun County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | None | Pump | Distribution Box | Aggregate Trench | [23 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/12/2020 | 02:21 PM
03/30/2020 |  | Routine, Scheduled |  | Loudoun County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | None | None | Pump | Manifold | [24 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/12/2020 | 02:21 PM
01/02/2020 |  | Routine, Scheduled | 179-12-0334-SWP | Stafford County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | EcoPod | None | Pump | Drip | Drip Tubing |  |  | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Distribution Pump Operation","Effluent Screens"] | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Distribution Pump Operation","Effluent Screens"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/04/2020 | 07:46 AM
04/08/2020 |  | Follow-Up |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | SES MidAtlantic LLC | 1942001203 | James | Green |  |  | EcoPod | none | Pump | Gravity | Drip | Not Applicable |  | ["Level Sensor Operation"] | ["Level Sensor Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced timer float. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/15/2021 | 09:00 AM
06/18/2020 |  | RoutineScheduled | SD-05-457 | Fauquier | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Media appears to be partially plugged, but effluent is clear and effluent level in treatment zone is ok (recirc trough visible). No action required at this time. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
01/10/2020 |  | Routine, Scheduled |  | Prince William County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Delta Environmental Products, DF Series |  |  |  |  | None |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] |  | Good | Clear | [15 empty] | [Comments]: Spin filter cleaned.Pump Amps 9.4 ETM 96h Cycles 34409Water Meter Reading 1278010Septic Sludge 8" Scum 1"ATU Sludge 6" Scum 4"Pump Sludge 4" Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/10/2020 | 02:05 PM
11/19/2020 | Alternative | Initial Visit | 124-STS-2379 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Rejected | EHD - Three Rivers | Miller's Septic Service | 1942001063 | K.R. Trapper | Davis | 3.000000 | 3000 | Multiflo FTB | None | Pump | Distribution Box | Aggregate Trench | None | 1800.000000 |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | Musty | Clear | [15 empty] | Initial Visit - Three individual systems Primary Septic Tanks - three - normal operating level - effluent screens serviced. Aeration Units - Three - normal operating levels - all compressors serviced. Pump Tanks - Three - normal operating level - pumps, float sensors, controls all operating properly. Distribution issues - being addressed by re-setting pump rest / run times - further evaluation required. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 11/20/2020 | 07:30 AM
09/24/2020 |  | Initial Visit | 234-18-342 | Chesapeake | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Chesapeake | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | Installer called stating the relay is bad. Serviced system. Checked the pump, panel, & floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. The grade on the pipe in the Clearstream is not okay. Re-wired panel for pump float and override float. Replaced the relay. Needs new risers and lids - something ran over them - 2 -12" x 20", 2 - 6" x 20", 1- 20" lid, 1 -EZ Set 18" riser, flat ring, lid, and 6 tubes of sealer. The timer is set to 2 minutes every 1 hour. Bad until risers are fixed. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. |  | 09/24/2020 | Jan 1 1900 12:00PM
01/08/2020 |  | Routine, Scheduled | 195-Discharge-34616 Fleet Rd. | Washington County | This AOSS should now return to normal function after having provided the above stated routine maintenance. | Approved | EHD - Mount Rogers | DEEL, DENNY M | 1942001097 | DENNY | DEEL |  |  |  | None | Gravity | None | Alternative Discharge | Chlorine | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens"] |  | Musty | Clear | [15 empty] | [Comments]: Installs Own Tablets | This AOSS should now return to normal function after having provided the above stated routine maintenance. |  | 02/05/2020 | Jan 1 1900 4:54PM
06/03/2020 |  | RoutineScheduled | SP-03-361 | King George | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Ecoflo | none | Pump | Gravity | Pad | Not Applicable |  | ["Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Attached Growth Medium" ,"Effluent Screens" ,"Level Sensor Operation"] | ["SludgeScum Accumulation" ,"Attached Growth Medium" ,"Effluent Screens" ,"Level Sensor Operation" ,"Septic Tank Baffles"] | YES | [15 empty] | Will be sent separately | Inspected | Effluent filter housing is broken, will send proposal for replacement. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
01/16/2020 |  | Reportable Incident | 2016-143-0166 | Henrico County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Henrico |  |  |  |  | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | [Comments]: Owner called due to the red light being on and backing up in the bathrooms. Serviced system. Checked the pump, panel, & floats (ok). Cleaned the filter in the Clearstream. Changed the filter in the aerator and changed the diffuser in the Clearstream. Installed a re-build kit on the aerator. The timer is set to 6 minutes every 2 hours. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/16/2020 | 12:00 PM
10/28/2020 |  | RoutineScheduled | {FIPSCode}-STS-69032 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Wastemaster Inc |  | Timothy | Jenkins | 2.000000 |  | ATU |  | Pump | Pressure | Drip |  |  | [] | [] | [18 empty] | In for service and inspection. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 11/05/2020 | 11:20 AM
02/05/2020 |  | Routine, Scheduled |  | Loudoun County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | None | Pump | Distribution Box | Aggregate Trench | [23 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/02/2020 | 04:43 AM
10/03/2020 |  | RoutineScheduled | {FIPSCode}-STS-13220 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Wastemaster Inc |  | Timothy | Jenkins |  |  | Sequencing Bat Reactor |  |  | Gravity | Discharge | UV |  | [] | [] |  | Musty | Clear | 6.600000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 10/22/2020 | 12:40 PM
03/18/2020 |  | Routine, Scheduled | 10-125-104 | Dickenson County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Cumberland Plateau | DEEL, DENNY M | 1942001097 | DENNY | DEEL |  |  | Norweco Singulair ATU | None | Gravity | None | Alternative Discharge | Chlorine | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens"] |  | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/08/2020 | Jan 1 1900 1:01PM
10/02/2020 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump | Drip | Elevated Sand Mound | UV Light |  | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  |  | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 10/02/2020 | Jan 1 1900 11:15AM
11/16/2020 |  | RoutineScheduled | 69160235 | Frederick | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | none | none | Gravity | Gravity |  | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation"] | ["BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/26/2021 | 09:04 AM
06/08/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | SES MidAtlantic LLC | 1942001203 | James | Green |  |  | Delta Environmental Products, DF Series | none | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"SludgeScum Accumulation"] |  | NA | [15 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. Compressor needs replacing. | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 |  | 04/15/2021 | 09:00 AM
08/28/2020 |  | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Lord Fairfax | Greenway Engineering | 1942001008 | Jeremy | Ferguson | 1.000000 | 1000 | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","Level Sensor Operation","Effluent Screens","SludgeScum Accumulation"] | ["Level Sensor Operation","SludgeScum Accumulation","Effluent Screens","Attached Growth Medium"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 08/28/2020 | 04:15 PM
12/03/2020 |  | RoutineScheduled | S-09-111-0151 | Botetourt | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Alleghany-Roanoke | Onsite Wastewater Services - May Supply | 1942001627 | Drew | Shull | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | INSPECTION COMPLETED BY DKS | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/28/2021 | Jan 1 1900 5:41AM
09/30/2020 |  | RoutineScheduled |  | Rockingham | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Pressure | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced lid on riser | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/26/2021 | 09:04 AM
11/14/2020 |  | RoutineScheduled | 109-17-0094 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1000 | EZ Treat |  | Pump | Gravity | Trenches |  |  | ["None"] | ["None"] | [18 empty] | Annual inspection. 6" of solids in septic tank. 18" of solids in recirculation tank. Spray nozzles have good spray patterns, they do not need cleaning. Cleaned septic tank filter. septic tank filter was clogged restricting flow from septic tank to recirculation tank. Normal solids accumulation on filter over a year's timeframe. Tested floats, pumps and alarm. Effluent quality is excellent. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 11/25/2020 | 07:03 PM
06/20/2020 |  | RoutineScheduled | 133 15 0241 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1500 | Advantex |  | Pump | Gravity | Trenches |  |  | ["None"] | ["None"] | [18 empty] | 6" of solids in septic tank. Flushed treatment unit spray manifold. Cleaned septic tank filter. Tested floats, pumps and alarm. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 09/29/2020 | 07:03 PM
02/21/2020 |  | Routine, Scheduled |  | Loudoun County | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Paid | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | Delta Environmental Products, DF Series | None | Pump | Distribution Box | Aggregate Trench | [22 empty] | [Comments]: Pump tank needs pumped out | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 03/02/2020 | 04:43 AM
04/29/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim |  |  | Best 1 | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | The best 1 tank needs pumped out | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 |  | 04/14/2021 | 04:27 PM
01/27/2020 |  | Routine, Scheduled | 108-14-0011 | Bath County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Central Shenandoah | AYRES, HUNTER E | 1942001166 | HUNTER | AYRES |  |  | Septic Tank Only | Septic Tank Only | None | None | None | None |  | ["None"] | ["None"] | [18 empty] | [Comments]: Filters checked and cleaned. No apparent leaks in system or drain field area. Control panels operating properly. System did not need to be pumped. Lids properly secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/04/2020 | 07:47 PM
06/02/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Ecoflo | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Ponding on the house side of the Eco Flo. Recommending repair company to homeowner. | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 |  | 05/27/2021 | 01:26 PM
06/19/2020 |  | Routine/Scheduled | 07-163-0143 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chickahominy | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. |  |  | Clearstream ATU |  | Pump | Distribution Box |  |  |  | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | Replaced pump station alarm panel | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 06/19/2020 | Jan 1 1900 3:00AM
03/03/2020 |  | Routine, Scheduled | 03-165-0209 | Northampton County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Eastern Shore | DUER, PETE C | 1942001051 | PETE | DUER | 1.000000 | 1250 | Septic Tank Only | Puraflo | Pump | None | None | None |  | ["None"] | ["None"] | [18 empty] | [Comments]: Aoss Inspection. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/27/2020 | 12:14 PM
06/10/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/27/2021 | 01:26 PM
04/13/2020 |  | RoutineScheduled | {FIPSCode}-STS-5225 | Tazewell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. |  | Denny | Deel |  |  | WHITEWATER |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
08/26/2020 | Alternative | Routine/Scheduled | 128-08-116 | Essex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 500 | Biomicrobics MicroFAST | None | Pump | Drip | Drip Tubing | None | 450.000000 |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | Musty | Clear | [15 empty] | Routine service conducted. Trash tank - normal operating level Aeration - normal operating level - blower serviced Pump tank - discharge pump serviced, float sensors and controls operating properly Drip Controls - manual - effluent screen serviced | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 08/28/2020 | 02:30 PM
08/19/2020 | Alternative | Reportable Incident | 133-STS-105901 | Northumberland | This AOSS should now return to normal function after having provided the above state routine maintenance | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001063 | K.R. Trapper | Davis | 2.000000 | 2000 | None | None | Gravity | Distribution Box | Aggregate Trench | None | 450.000000 |  | ["Dispersal System Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | [17 empty] | Septic tanks pumped empty to facilitate repairs. Primary & Secondary septic tanks pumped empty. New Conveyance lines installed. New 8 port concrete distribution box installed New header lines installed. | This AOSS should now return to normal function after having provided the above state routine maintenance |  | 08/25/2020 | 07:30 AM
03/11/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Paid | EHD - Fairfax | MCKIM, STEPHEN E | 1934000043 | STEPHEN | MCKIM |  |  | Septic Tank Only | Septic Tank Only | None | None | None | None |  | ["SludgeScum Accumulation"] | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | [18 empty] | [Comments]: Septic/Atu and pump tank need pumped out | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 04/20/2020 | Jan 1 1900 10:40AM
03/09/2020 |  | Routine, Scheduled |  | Loudoun County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim |  |  | Best 1 | None | Gravity | Distribution Box | Aggregate Trench | [5 empty] | YES | YES | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/12/2020 | 02:21 PM
08/11/2020 |  | Routine, Scheduled | 175-07-0389 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Orenco Advantex |  |  |  |  | None |  | ["Blower/Compressor/Aerator Operation","Dispersal System Operation","Effluent Screens","Recirculation Pump"] | ["Blower/Compressor/Aerator Operation","Dispersal System Operation","Effluent Screens","Recirculation Pump"] |  | Good | Clear | [15 empty] | Spin filter cleaned. Pump Amps 10.78/12.52 Water Meter Reading 540990 Septic Sludge 10" Scum 2" ATU Sludge 12" Scum 0 Pump Sludge 3" Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 08/11/2020 | 11:48 AM
01/07/2020 | Alternative | Routine/Scheduled | 157-06-0336 | Mathews | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | Serviced system. Checked the pump, panel, & floats (ok). Cleaned the filter in the Clearstream and cleaned the filter in the aerator. Changed the diffuser in the Clearstream. Dis-connected the alarm float because it was tripping breaker on house. Pumped out septic tank. Wire from panel to Clearstream alarm is bad - need to run 40' of conduit & wire to replace it. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. |  | 01/07/2020 | 12:00 PM
07/29/2020 |  | RoutineScheduled | 13-195-124-SP | Washington | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Mount Rogers | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | FAST |  | Gravity | Gravity | Mound | UV | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","Disinfection"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
06/25/2020 |  | Reportable Incident | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance | Approved | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green | [9 empty] | ["Disinfection"] | ["Disinfection"] | [18 empty] | Replaced JET UV bulb,chord & test tube. Sampling in progress. | This AOSS should now return to normal function after having provided the above state routine maintenance |  | 06/25/2020 | Jan 1 1900 4:00PM
02/18/2020 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | McKim Construction | 1942001330 | Michelle | McKim | [9 empty] | [] | [] | [8 empty] | 02/18/2020 | Pump Chamber | 14.000000 | [5 empty] | Attached to this report |  | BOD sample | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 01/10/2022 | Jan 1 1900 10:00AM
05/21/2020 |  | RoutineScheduled | SD-07-065 | Orange | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"BlowerCompressorAerator Operation" ,"SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | We recommend pumping the septic tank due to solids accumulation. The pump settings did not appear to be correct. We have consulted with the designer and plan to make a follow-up visit in the near future. | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 |  | 04/09/2021 | 03:25 PM
09/29/2020 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump | Drip | Elevated Sand Mound | UV Light |  | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  | 6.54 | 4.020000 | 6.100000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 09/29/2020 | Jan 1 1900 9:30AM
09/18/2020 |  |  |  | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | McKim Construction | 1942001330 | Michelle | McKim | 2.000000 |  |  |  | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 11/13/2020 | Jan 1 1900 11:15AM
07/14/2020 |  |  | 157-18-0085 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Church View Septic Service Inc. | 1942001302 | Charles | Langford | 1.000000 | 1000 | Aquasafe |  | Pump |  | Pad | Not Applicable |  | ["None"] | ["None"] | [17 empty] | Pumped Out |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 09/22/2020 | 12:00 AM
12/21/2020 |  | RoutineScheduled | SD-09-10 | Culpeper | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/09/2021 | 03:25 PM
11/02/2020 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump | Drip | Elevated Sand Mound | UV Light |  | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  |  | 7.000000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 11/02/2020 | Jan 1 1900 10:30AM
09/22/2020 |  | Follow-Up |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Media was replaced and the system appears to be functioning as designed. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/27/2021 | 01:26 PM
06/26/2020 | Alternative | Routine/Scheduled | 166-03-800 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 3.000000 | 2600 | Clearstream |  | Pump | Distribution Box | Aggregate Trench |  |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | [17 empty] | Tanks were pumped by owners request. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 06/25/2020 | 03:00 PM
03/27/2020 |  | Routine, Scheduled | 11-120-0142A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesterfield | Madison Environmental LLC |  | Larry | Madison, Jr. |  |  | Norweco Singulair ATU |  | Pump |  |  |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Lab results not reported by Operator, EHS chose "No" in order to allow saving updated entry. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/27/2020 | Jan 1 1900 3:30AM
10/27/2020 |  | RoutineScheduled |  | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 2705051738 | Joshua | Hott |  |  | Septic | Puraflo | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [7 empty] | 10/27/2020 | Sample Chamber | [6 empty] | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
06/22/2020 |  | RoutineScheduled | 179-06-0252-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Recirculation Pump" ,"Attached Growth Medium" ,"SludgeScum Accumulation"] | ["Effluent Screens" ,"Recirculation Pump" ,"Attached Growth Medium"] | YES | [15 empty] | Will be sent separately | Inspected | We recommend pumping the Septic Tank, Avantex Tank and Pump Tank due to scum & sludge accumulation. The drainfield lines have settled. We recommend adding topsoil where the lines have settled. We also recommend removing the small tree next to the distribution box. | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 |  | 04/09/2021 | 03:25 PM
02/19/2020 |  | Routine, Scheduled | 12-197-099 | Wise County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Lenowisco | DEEL, DENNY M | 1942001097 | DENNY | DEEL |  |  | Clearstream ATU | None | Pump | Drip | Drip Tubing | None | 200.000000 | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump"] |  | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/03/2020 | Jan 1 1900 11:03AM
06/23/2020 |  | RoutineScheduled | 107-09-0001 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Onsite Wastewater Services - May Supply | 1942001022 | Sara | Tusing | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | inspection DS | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 05/28/2021 | 05:41 AM
05/20/2020 |  | RoutineScheduled | 033-07-0183-SP | Caroline | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Recirculation Pump"] | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/09/2021 | 03:25 PM
07/29/2020 |  | RoutineScheduled |  | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - New River | Montgomery Sanitation Services, Inc. | 1942001003 | Tim | Conner | 1.000000 | 1500 gallons | Microfast |  | Gravity | Gravity | Trenches | Not Applicable |  | ["on"] | ["on"] | YES | Septic | Discolored | [5 empty] | 07/29/2020 | Sample Chamber | [6 empty] | Attached to this report | Pumped Out | NO SAMPLE WAS TAKEN; NO RECORD OF SAMPLE BEING TAKE; SAMPLE IS DUE. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 08/06/2020 | 10:25 AM
06/13/2020 |  | Follow-Up | 175-02-0035 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | Aquarobic Services | 1934000142 | Michael | Blake |  |  | none | none | Pump | Gravity | Pad | Not Applicable |  | ["Distribution Pump Operation" ,"Level Sensor Operation" ,"SludgeScum Accumulation" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Level Sensor Operation" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | On site for alarm in remote alarm box. Alarm in control panel not activated because alarm float had been taped up in a higher position. Adjusted elevations for all 3 floats. Found screws loose for lid on j-box at tank and gasket missing. Terminal strip has rust spots. Blower was locked up. Worked on blower and eventually got it running. Blower was installed on wrong side of manway which pulls manifold out of position, and prevents pump from being mounted on a stand. Both manways have evidence of infiltration and need to be resealed. Heavy pump is only supported by a rope and is putting stress on discharge piping. Pump amps are high. Recommend pumping of tank to remove towels and debris. Recommend new manifold and addition of separate blower housing to protect blower. Filterbed is overgrown, needs maintenance. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 07/01/2022 | 10:30 AM
02/19/2020 |  | Routine, Scheduled |  | Prince William County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Biomicrobics MicroFAST |  | Pump |  |  | UV Light |  | ["BlowerCompressorAerator Operation","Disinfection"] | ["BlowerCompressorAerator Operation","Disinfection"] |  | Good | Clear | [5 empty] | 02/19/2020 |  | 23.000000 |  | 326.000000 | 12.000000 |  |  |  |  | [Comments]: Pump Amps 6.40 ETM 918h Cycles 6121Septic Sludge 7" Scum 3"ATU Sludge 6" Scum 0Pump Sludge 2" Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/19/2020 | 10:30 AM
12/29/2020 | Alternative | RoutineScheduled | 171-18-378 | Shenandoah | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Lord Fairfax | Valley Soil & Environmental Consulting, LLC | 1942001218 | John | Lam | 2.000000 | 3000 | Advantex AX-25RTN |  | Pump | Pressure | Drip | Not Applicable | 160.000000 | ["Effluent Screens","Control Operation"] | ["Effluent Screens","Control Operation"] | YES | Musty | Clear | [14 empty] | Inspected | Cleaned septic tank effluent screen; measured 6" of sludge in septic tank; opened drip dispersal return line to field flushed system drip tubing and reset return pressure to 10 psi; recirculation pump: 11.15 amps, 51,836 cycles; drip system pump: 7.6 amps, 55.1 hours, 503 cycles. Advantex system control panel set to serve 8 persons per day at average flow of 400 gpd | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 01/29/2021 | 12:00 AM
06/09/2020 |  | RoutineScheduled | 07-192-233 | Tazewell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. |  | Denny | Deel |  |  | Whitewater |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
08/18/2020 |  | Reportable Incident | 199-STS-5871 | York | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Peninsula | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | None | None | Gravity | Distribution Box | Aggregate Trench | None | 450.000000 |  | ["Dispersal System Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | [17 empty] | Septic tank pumped to facilitate repair. Septic tank pumped to facilitate repair. New Conveyance line from Septic tank to distribution box. New 8 port concrete distribution box installed New header lines installed Distribution box balanced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 08/25/2020 | Jan 1 1900 2:30PM
05/15/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/14/2021 | 04:27 PM
10/22/2020 |  | RoutineScheduled |  | Rockingham | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Pad | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter"] | ["Control Operation" ,"Auxiliary Filter"] | NA | [7 empty] | 10/22/2020 |  | 21.000000 | [5 empty] | Will be sent separately | Inspected | Lab Sample Normal | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/26/2021 | 09:04 AM
10/02/2020 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump | Distribution Box | Gravel-Less Trench | UV Light |  | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  |  | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 10/02/2020 | Jan 1 1900 2:30PM
03/03/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Fairfax | Hott, Joshua D. | 1942001301 | Joshua | Hott | 1.000000 | 1500 | Septic Tank Only | Puraflo | Pump | Distribution Box | Aggregate Trench | None |  | ["None"] | ["None"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/18/2020 | Jan 1 1900 3:38PM
05/20/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Payment | EHD - Loudoun | Great Falls Septic Service, Inc | 1942001301 | Josh | Hott |  |  | Delta Environmental Products, UC Series | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/27/2021 | 11:51 AM
07/17/2020 |  | RoutineScheduled | 099-07-0015-SP | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock |  |  | joel | pinnix | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
04/24/2020 |  | Reportable Incident | 2016-143-0141 | Henrico | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Henrico | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | Owner called due to it backing up in house. Serviced system. Checked the pump and panel (ok). Cleaned the filter in the Clearstream. Need to pump it down and re-attach flap. Changed the diffuser in the Clearstream and changed the filter in the aerator. Fixed the grade on the Clearstream pipe. The alarm float in the Clearstream needs to be adjusted. The pressure switch on the aerator is not hooked up. The UV is not working - the circuirt board is good but needs a new tube assembly, cord, and bulb. Installed orifice in the return line. The timer is set to 4 minutes every 1.5 hours. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. |  | 04/24/2020 | 12:00 PM
09/23/2020 |  |  | 139-06-0079 | Greene | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Aiternative Systems Inspection Services, LLC | 1942001047 | Wesley | Basore | 1.000000 | 500 | Biomicrobics |  | Pump | Pressure | Drip | Not Applicable |  | [] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 09/26/2020 | 09:55 AM
01/09/2020 |  | Routine, Scheduled | 171-12-0238 | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Lord Fairfax | Cubbage, Harrison Lee, II | 1942001021 | Harrison | Cubbage | 1.000000 | 1500 |  | Biomicrobics MicroFAST | Pump | Drip | Drip Tubing | None |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","SludgeScum Accumulation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","SludgeScum Accumulation"] |  | Musty | Clear | [15 empty] | [Comments]: Microfast Tank Pumped 1-16-20 Pump Tank Sludge/Scum Accumulations:3"/0" Pump Settings: Off 2hrs On 10min ETM-603.50Hr Cycle COunt-3628 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/18/2020 | 12:19 PM
08/18/2020 | Alternative | Reportable Incident | -STS-15915 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Western Tidewater | Miller's Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | None | None | Pump | Distribution Box | Aggregate Trench | None | 450.000000 |  | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | [17 empty] | Pumped by Goodman's Septic to facilitate repairs Maintenance / Repair. Rebuilt pump forcemain - Replaced conveyance line from pump chamber to distribution box New 8 port distribution box installed - timed New header lines installed | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 08/25/2020 | Dec 30 1899 2:30PM
09/29/2020 |  | RoutineScheduled | 069040428 | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Greenway Engineering | 1942001008 | Jeremy | Ferguson | 1.000000 | 1250 | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens","Level Sensor Operation","SludgeScum Accumulation","Attached Growth Medium"] | ["Attached Growth Medium","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 10/01/2020 | 08:00 AM
10/23/2020 |  | RoutineScheduled | 177-11-0140-SP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | EcoPod | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Attached Growth Medium" ,"SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation" ,"Attached Growth Medium"] | NA | [15 empty] | Will be sent separately | Inspected | We recommend pumping the Septic Tank, the Aerobic Treatment Unit and the Pump Tank due to sludge accumulation. | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 |  | 04/09/2021 | 03:25 PM
12/01/2020 | Alternative | RoutineScheduled | 136-17-0286 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [8 empty] | 12/01/2020 | [10 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
07/23/2020 |  | RoutineScheduled | 107-02-0800 (LEGACY ALT. SYSTEM) | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Onsite Wastewater Services - May Supply | 1942001022 | Sara | Tusing | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 05/28/2021 | 05:41 AM
07/10/2020 |  | RoutineScheduled | 179-17-0324-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump" ,"Attached Growth Medium" ,"Auxiliary Filter"] | ["Effluent Screens" ,"Recirculation Pump" ,"Distribution Pump Operation" ,"Auxiliary Filter" ,"Attached Growth Medium"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 |  | 04/09/2021 | 03:25 PM
06/22/2020 |  | RoutineScheduled | SD-10-109 | Culpeper | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | EcoPod | none | Pump | Gravity |  | Chlorination |  | ["Attached Growth Medium" ,"BlowerCompressorAerator Operation"] | ["Attached Growth Medium" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | The sand filter is holding less water than has been observed during recent inspections but is still holding water. We again recommend replacing the sand in the sand filter. | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 |  | 04/09/2021 | 03:25 PM
04/28/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/27/2021 | 01:26 PM
10/23/2020 |  | RoutineScheduled | 181-05-0369 | Rockbridge | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Central Shenandoah | Hunter E. Ayres, General Contractor | 1942001166 | Hunter | Ayres | 1.000000 | 1500 | Biomicrobics MicroFAST |  | Gravity | Gravity | Trenches | Not Applicable |  | ["SludgeScum Accumulation","Auxiliary Filter","Control Operation"] | ["Control Operation","Auxiliary Filter","SludgeScum Accumulation"] | NA | [16 empty] | Pumped Out | Filter checked and cleaned. System was pumped and cleaned. No apparent leaks in system or drain field area. Control panel not functioning, so new one was installed. Lid properly secured. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 10/30/2020 | 01:15 PM
04/02/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Fairfax | MCKIM, STEPHEN E | 1934000043 | STEPHEN | MCKIM |  |  | Septic Tank Only | Septic Tank Only | None | None | None | None |  |  | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/20/2020 | Jan 1 1900 10:18AM
05/12/2020 |  | Reportable Incident | 179-09-0177-SR | Stafford | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation"] | ["Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Repeat alarms. Both tanks in high level. Put panel in and out of test mode, all working correctly. Solenoid valves appear to be closing correctly. Owner said that he had checked toilets, none malfunctioning. He will also attempt to verify correct operation of water treatment system. Alarms could be due to infiltration but nothing could be inspected in tanks due to high water level. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
09/21/2020 |  | RoutineScheduled | Sd-02-803 | Fauquier | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 2.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  | ["Level Sensor Operation" ,"Auxiliary Filter" ,"Control Operation"] | ["Control Operation" ,"Auxiliary Filter" ,"Level Sensor Operation"] | NA | [15 empty] | Will be sent separately | Inspected | K-rain zoner valve leaks from mildly to badly, depending on what zone it is on. It dosed 2 or more zones simultaneously in 4 out of 6 test cycles. Installed a low-flow stem & disc kit. Appeared to help a little, but could not overcome the pressure loss from the leak. Recommend replace the zoner valve. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
11/17/2020 |  | Follow-Up | 10-197-A1 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | Wise Co Health Dept |  | Rodney | Neece |  |  | Jet | [14 empty] | 0.000000 | Tablets are now in the contact chambers | [11 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 11/17/2020 | 12:00 AM
09/08/2020 |  | Routine/Scheduled | C-05-111-0182 | Botetourt | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Alleghany-Roanoke | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Delta Environmental Products, DF Series |  | Pump | Drip | Drip Tubing | None |  | ["None"] | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 09/08/2020 | Jan 1 1900 12:45PM
06/25/2020 | Alternative | RoutineScheduled | SD-94-93 | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | [6 empty] | tank only |  | Gravity | Pressure | Trenches | Not Applicable |  | ["None"] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 06/25/2020 | 12:00 AM
08/03/2020 |  | RoutineScheduled | 099-06-0122-SP | King George | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Distribution Pump Operation" ,"Recirculation Pump" ,"Auxiliary Filter" ,"Attached Growth Medium"] | ["Distribution Pump Operation" ,"Recirculation Pump" ,"Auxiliary Filter" ,"Attached Growth Medium"] | NA | [15 empty] | Will be sent separately | Inspected | We recommend replacing the cracked checkvalve. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/09/2021 | 03:25 PM
02/07/2020 |  | Routine, Scheduled | 09-100-0441 | Accomack County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Eastern Shore | DUER, PETE C | 1942001051 | PETE | DUER | 1.000000 | 1250 | Septic Tank Only | Delta Environmental Products, DF Series | Pump | None | None | None |  | ["None"] | ["None"] | [18 empty] | [Comments]: Aoss Inspection. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/10/2020 | 02:31 PM
10/15/2020 |  | RoutineScheduled | SD-08-194 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | EZ Treat Sandfilter | EZ Treat Sandfilter | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump"] | ["Recirculation Pump"] | NA | [15 empty] | Will be sent separately | Inspected | Semi-Annual Inspection: Please trim back the bushes around the tank lids before Spring. | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 |  | 04/09/2021 | 03:25 PM
09/15/2020 |  | Follow-Up |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Gravity | Gravity |  | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | replaced broken d-box and inspected. | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 |  | 04/14/2021 | 04:27 PM
10/19/2020 |  | Pump-Out Only |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | POWELLS PLUMBING, INC. | 1942001036 | Kurt | Holthaus |  |  | Puraflo | [6 empty] | ["Sludge/Scum Accumulation"] | ["Sludge/Scum Accumulation"] | N/A | [17 empty] | Pumped septic. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 11/19/2020 | 02:00 PM
08/11/2020 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 2705051738 | Joshua | Hott | 1.000000 | 1500 | Septic | Puraflo | Pump | Gravity | Trenches | Not Applicable |  | ["None"] | ["None"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
12/17/2020 | Alternative | Reportable Incident | 151-16-0007 | Lancaster | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [18 empty] | Aerator alarm. Pump was jammed with debris. Cleaned and restarted. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  |  | 12:00 AM
10/21/2020 |  | RoutineScheduled | 07-197-A7 | Wise |  | Approved | EHD - Lenowisco | VDH |  | Brad | Stallard | [12 empty] | None | Clear | 7.500000 | 5.000000 | [13 empty] | No lab samples collected |  |  |  | 12:00 AM
02/26/2020 |  | Initial Visit | NYII-BC6MUC | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesapeake | Farmer's Septic Service, Inc. |  | Emily | Brady | [9 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [10 empty] | 4.000000 |  | 1.000000 | [5 empty] | [Comments]: Serviced system. Checked the pump, panel, & floats (ok). Cleaned the filter and diffuser in the Clearstream, cleaned the filter in the aerator, cleaned the mesh screen in the spinfilter, and cleaned the UV light bulb. Replaced the pressure switch on the aerator - it was burnt up. The timer is set to 4.5 minutes every 2 hours. Took initial BOD & Fecal samples. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/26/2020 | Jan 1 1900 12:00PM
02/17/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Fairfax | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Orenco Advantex | None | Pump | Distribution Box | Aggregate Trench |  |  | ["Attached Growth Medium","Effluent Screens","Recirculation Pump"] | ["Attached Growth Medium","Effluent Screens","Recirculation Pump"] | [18 empty] | [Comments]: Several of the tubes for the recirculation pump filter have broken. We recommend replacing the filter. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/02/2020 | Jan 1 1900 11:52AM
11/10/2020 |  | RoutineScheduled | 177-06-0476-SWP | Spotsylvania | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Attached Growth Medium" ,"Control Operation"] | ["Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"BlowerCompressorAerator Operation" ,"Attached Growth Medium" ,"Auxiliary Filter" ,"Control Operation" ,"Dispersal System Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Media is beginning to clog again, need to contact manufacturer rep! On 2-10-20 we pulled fast unit and cleaned media! | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
01/21/2020 |  | Routine, Scheduled | SD-04-185 | Fauquier County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Whitewater ATU | None | Pump | Drip | Drip Tubing |  |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Distribution Pump Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Distribution Pump Operation"] |  | YES | YES | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/04/2020 | 07:46 AM
07/30/2020 |  | Reportable Incident | 199-STS-5843 | York | This AOSS should now return to normal function after having provided the above state routine maintenance | Approved | EHD - Peninsula | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | None | None | Gravity | Distribution Box | Aggregate Trench | None | 450.000000 |  | ["Dispersal System Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | [17 empty] | Install - Repair - Replace partially collapsed septic tank. New 1000g concrete septic tank with effluent screen installed. New 4" conveyance line installed New 6 port concrete distribution box installed - balanced. Three laterals confirmed - header lines spliced. | This AOSS should now return to normal function after having provided the above state routine maintenance |  | 08/07/2020 | Jan 1 1900 7:00AM
12/15/2020 |  | RoutineScheduled | 175-19-0030 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/ Advantex | Pump Tank | Pump | Gravity | Drip | Not Applicable |  | ["None"] | ["None"] | NA | [9 empty] | 56.000000 | [7 empty] | Septic tank-5"sludge 0"scum/ Pump Tank-1"sludge/ Advantex unit in good shape. No pump out needed at this time. Discharge Pump cycles-3649/ discharge run-479h 30m/ High counts-14/ Low counts-7/ Recirc. pump cycles-53591/Recirc. pump run-299h 16m/ High-2/ Low-12/ Installed new 24" riser | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
01/10/2020 |  | Routine, Scheduled | 03-125-273 | Dickenson County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Cumberland Plateau | DEEL, DENNY M | 1942001097 | DENNY | DEEL |  |  | Norweco Singulair ATU | None | Gravity | None | Alternative Discharge | Chlorine | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens"] |  | Musty | Clear | [15 empty] | [Comments]: 5 Blue Crystal 8 Bio Max Added | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/05/2020 | Jan 1 1900 3:17PM
09/15/2020 |  | RoutineScheduled | 019-STS-29347 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1000 | NONE, LPD System |  | Pump | Pressure | Trenches |  |  | ["None"] | ["None"] | [18 empty] | Annual inspection. 6" of solids in septic tank. Flushed low pressure dose system laterals. Tested alarm. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 10/26/2020 | 07:03 PM
11/23/2020 |  | RoutineScheduled | 061-STS-21826 | Fauquier | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001068 | David | Stewart | 3.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  | ["Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Level Sensor Operation" ,"BlowerCompressorAerator Operation" ,"Control Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Attached Growth Medium"] | ["Attached Growth Medium" ,"Control Operation" ,"Dispersal System Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | YES | [15 empty] | Will be sent separately | Inspected | ARV in front of church is missing mushroom cap and valve box lid. Septic tank needs to be pumped out. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
12/31/2020 |  | RoutineScheduled | 08-165-0265 | Northampton | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Bundick Well & Pump | 1942001051 | Peter | Duer | 2.000000 | 9000 | Septic Tank | MicroFast | Pump | Pressure |  |  | 4200.000000 | [] | ["None"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 01/06/2021 | 02:45 PM
11/18/2020 |  |  | 06-113-157 | Buchanan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 11/18/2020 |  | 12.700000 |  |  | 2.900000 |  |  | Attached to this report |  | BOD: 12.7 TSS: 2.90 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 11/18/2020 | Jan 1 1900 3:00PM
10/13/2020 |  | RoutineScheduled | 09-184-5003 | Scott | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Effluent Screens"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Effluent Screens"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
08/20/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | SES MidAtlantic LLC | 1942001203 | James | Green | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/15/2021 | 09:00 AM
12/18/2020 |  | RoutineScheduled | 177-07-0409-SR | Spotsylvania | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity |  | UV |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | We recommend replacing the alarm light bulb on the UV panel. We recommend replacing the Advantex vent cap. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/09/2021 | 03:25 PM
02/25/2020 |  | Follow-Up |  | Loudoun County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | Delta Environmental Products, DF Series | None | Pump | Drip | Drip Tubing | [22 empty] | [Comments]: Air line for air blower was fixed. A new 4 zone zoner was replaced. All componants are working as they should | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/12/2020 | 02:21 PM
10/12/2020 | Alternative | Routine/Scheduled | 150-15-0041 | King William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | Clearstream |  | Pump | Manifold | Aggregate Trench | UV Light | 600.000000 |  | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | Musty | Clear | [15 empty] | Routine service Trash Tank - normal operating level - effluent screen serviced. Aeration Tank - normal operating level - air compressor serviced. U.V. Disinfection - Obsidian - functioning properly Discharge Tank - normal operating level - pump serviced - float sensors & controls operating properly. Diversion valve serviced - no indications of surfacing present. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 10/16/2020 | 08:30 AM
08/10/2020 |  | Routine/Scheduled |  | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump | Drip |  | None |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  |  | 7.000000 | 5.000000 | [13 empty] | Replaced alarm float | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 08/10/2020 | Jan 1 1900 10:15AM
04/16/2020 |  | Initial Visit | 171-15-024 | Shenandoah | This AOSS should now return to normal function after having provided the above stated routine maintenance. | Approved | EHD - Lord Fairfax | SEAL, CHARLES K | 1934000144 | CHARLES | SEAL | 1.000000 |  |  | Biomicrobics MicroFAST | Pump | Manifold | Drip Tubing | None |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation","SludgeScum Accumulation"] | [18 empty] | [Comments]: Repairs made to leaking air pipe and leak in drip field. Spin filter blown apart and replaced | This AOSS should now return to normal function after having provided the above stated routine maintenance. |  | 04/22/2020 | 12:29 PM
03/11/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Fairfax | KLEINDL, JAMES LEE | 1942001380 | JAMES LEE | KLEINDL | 1.000000 | 1500 | Biomicrobics MicroFAST | Septic Tank Only | Pump | Drip | Drip Tubing | UV Light |  | ["SludgeScum Accumulation"] | ["Auxiliary Filter","Disinfection","SludgeScum Accumulation"] | [18 empty] | [Comments]: replace uv bulb | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/12/2020 | Jan 1 1900 9:13PM
07/13/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim |  |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/14/2021 | 04:27 PM
05/21/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | none | none | Pump | Gravity | Mound | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | The blower only functions when the contactor is held in. The pump does not seem to be working at all. The dainfield mound has grass that is waist high and needs to be mowed. | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 |  | 05/27/2021 | 01:26 PM
01/10/2020 |  | Routine, Scheduled |  | Loudoun County | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Paid | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | None | Pump | Distribution Box | Aggregate Trench | [22 empty] | [Comments]: Was unable to inspect pods. Informed homeowner they need to cut bushes down around pods. We were unable to get to them to open up. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 01/15/2020 | 06:36 AM
08/06/2020 |  | Follow-Up |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Gravity | Gravity |  | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Sections of the first d-box header lines were dug up and replaced. They were full of tree roots that had gotten into them System is in working condition | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 |  | 04/14/2021 | 04:27 PM
02/05/2020 |  | Reportable Incident | SP-05-227 | Stafford County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001350 | Mike | Cook |  |  | Orenco Advantex | None | Pump | Distribution Box | [23 empty] | [Comments]: Homeowner called due to alarm. Replaced failed N98 pump and recirc (timer) float. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/06/2020 | 10:23 AM
10/22/2020 |  | Routine/Scheduled | 2018-143-0242 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Henrico | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. |  |  | Clearstream ATU |  | Pump |  |  |  |  | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 10/22/2020 | 10:00 AM
05/22/2020 |  | RoutineScheduled | 107-07-0038 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Onsite Wastewater Services - May Supply | 1942001022 | Sara | Tusing | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Pressure | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 05/28/2021 | 05:41 AM
06/19/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Payment | EHD - Loudoun | Great Falls Septic Service, Inc | 1942001301 | Josh | Hott | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/27/2021 | 11:51 AM
10/26/2020 |  | RoutineScheduled | 179-10-0047-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump"] | ["Distribution Pump Operation" ,"Attached Growth Medium" ,"Effluent Screens" ,"Recirculation Pump"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 |  | 04/09/2021 | 03:25 PM
11/03/2020 |  | RoutineScheduled | 061-17-321 | Fauquier | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Rappahannock-Rapidan | Wastemaster Inc |  | Timothy | Jenkins | 2.000000 |  | ATU |  | Pump | Pressure | Drip |  |  | [] | ["SludgeScum Accumulation"] | [18 empty] | All tanks full to top. Multiflo has overflowed all over ground. Effluent filter binded but pit full of surface water. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. |  | 11/20/2020 | 11:55 AM
06/25/2020 |  | Routine/Scheduled | 2011-143-0003 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Henrico | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. |  |  | SludgeHammer |  | Pump | Distribution Box |  |  |  | ["Attached Growth Medium","Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Attached Growth Medium","Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 06/25/2020 | 10:00 AM
03/05/2020 |  | Routine, Scheduled | 061-17-02 | Fauquier County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Biomicrobics MicroFAST | None | Pump | Distribution Box | Aggregate Trench |  |  | ["Attached Growth Medium","BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/06/2020 | 02:45 PM
01/27/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Fairfax | KLEINDL, JAMES LEE | 1942001380 | JAMES LEE | KLEINDL | 1.000000 | 1500 | Orenco Advantex | Septic Tank Only | Pump | Distribution Box | Aggregate Trench | None |  |  | ["Effluent Screens","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/03/2020 | Jan 1 1900 6:59PM
07/01/2020 |  | RoutineScheduled | 11-160-0106 | Montgomery | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - New River | King's Alternative Septic | 1942001112 | William | King, II | 2.000000 | 2500 | Delta DF60 |  | Pump | Pressure | Drip | Not Applicable | 150.000000 | ["Auxiliary Filter","Effluent Screens"] | ["Auxiliary Filter","Effluent Screens"] | YES | [17 empty] | Cleaned blower filter, cleaned effluent screens and replaced spin filter; system is working correctly. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 07/10/2020 | 12:00 AM
07/16/2020 |  | Routine/Scheduled | 234-03-11324 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesapeake | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | PremierTech, EFX |  | Gravity | None | Alternative Discharge | Chlorine | 450.000000 |  | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | Musty | Clear | [15 empty] | Routine service conducted. Primary septic tank in normal operating level - effluent screen serviced. Minor leakage noted at inlet and outlet risers. Pump basin - at normal operating level - pump, float sensors operating properly - minor bulging noted to unit - no fractures present. EcoFlo Biofilter - unit appears to be out of level. Minor fracture noted at roof of unit - tipping bucket, trays and peatmoss serviced. Chlorination unit and Dechlorination unit intact functional, clean and tablets present. Supplemental air unit functioning. Discharge point clear of debris. No laboratory samples contracted for. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 07/17/2020 | Jan 1 1900 9:00AM
06/25/2020 |  | RoutineScheduled | 177-10-0229-ST | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | EcoPod | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 |  | 04/09/2021 | 03:25 PM
06/18/2020 |  | RoutineScheduled | 033-06-0257-SWP | Caroline | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Dispersal System Operation" ,"Recirculation Pump" ,"Attached Growth Medium"] | ["Dispersal System Operation" ,"Recirculation Pump" ,"Attached Growth Medium"] | NA | [15 empty] | Will be sent separately | Inspected | We removed roots that had grown into the distribution box. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/09/2021 | 03:25 PM
12/07/2020 |  |  | {FIPSCode}-STS-19119 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | Wise Coounty Health Dept |  | Rodney | Neece | 1.000000 |  | ATU |  | Gravity | Gravity | Discharge | Chlorination |  |  |  |  | Musty | Clear | 6.200000 | 5.000000 |  | 0.000000 | Tablets are present | [11 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12/07/2020 | 12:00 AM
09/14/2020 |  | Reportable Incident | 05-120-0723A | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Old Dominion Onsite, Inc. | 1942001503 | Jason | Hackler | 1.000000 | 1500 | Orenco Advantex |  | Pump | Manifold | Spray Irrigation | UV Light |  |  |  | N/A | [17 empty] | Alarm reported. Found system alarming upon arrival. Found the recirc valve mostly closed. Opened valve. System appears to be operating normally. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 09/14/2020 | Jan 1 1900 2:25PM
07/16/2020 |  | RoutineScheduled | SWP-04-761 | Spotsylvania | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Attached Growth Medium" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | ["Control Operation" ,"Distribution Pump Operation" ,"Attached Growth Medium" ,"Effluent Screens" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | YES | [15 empty] | Will be sent separately | Inspected | Treatment was very bad; sheets were clogged with Biofilm. Tanks require a pump out. Top seam of both tanks have roots growing in and need to be resealed. Risers leak. Inlet pipe to pump tank is severely settled. Wedge lid on pump tank has roots. Pump tank outlet leaks. Replaced redundant float in recirc. Proposal for repairs to be sent to homeowner. | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
03/03/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Fairfax | Ware, Michele P | 1942001165 | Michele | Ware |  |  | Septic Tank Only | Septic Tank Only | None | None | None | None |  |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/11/2020 | Jan 1 1900 1:40PM
09/10/2020 |  | RoutineScheduled | 17-192-154 | Tazewell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. |  | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Control Operation","BlowerCompressorAerator Operation","Disinfection"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
04/16/2020 |  | Routine/Scheduled | 04-120-0199A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesterfield | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1500 | Orenco Advantex | None | Pump | Distribution Box | Aggregate Trench | None |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | [17 empty] | Upon arrival, the System was found flooded. In the Recirculation Tank, the Inlet Line & Riser were leaking, the Forcemain Line was found broken (repaired onsite with Homeowner approval), and water-tight Splice Box was found flooded; the Discharge Tank Riser and Forcemain Line were leaking | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/17/2020 | Jan 1 1900 3:24PM
09/11/2020 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Fairfax | McKim Construction | 1942001330 | Michelle | McKim | 2.000000 |  | 1500 | 2000 | Pump | Pressure | Drip | UV |  | ["Disinfection"] | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Disinfection","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | YES | [17 empty] | UV light and cp need replaced not working | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. |  | 10/24/2020 | 12:00 AM
03/11/2020 |  | Routine, Scheduled |  | Loudoun County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | None | None | Pump | Manifold | [24 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/16/2020 | 11:28 AM
11/04/2020 |  | RoutineScheduled | 033-18-0126-SP | Caroline | This AOSS is not functioning as designed or in accordance with the performance/Maintenance requirements | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Norweco Singulair ATU | none | Pump | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Attached Growth Medium" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Attached Growth Medium" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter" ,"Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected | There is a large wet area at the distal end of the drip dispersal area where effluent is coming to the ground surface. We recommend contacting an Alternative Onsite Soil Evaluator for repair options. | This AOSS is not functioning as designed or in accordance with the performance/Maintenance requirements |  | 04/09/2021 | 03:25 PM
01/14/2020 |  | Routine, Scheduled | 03-197-179 | Wise County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Lenowisco | DEEL, DENNY M | 1942001097 | DENNY | DEEL |  |  | Norweco Singulair ATU | None | Gravity | Distribution Box | Aggregate Bed | None | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Effluent Screens","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Effluent Screens"] |  | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/05/2020 | Jan 1 1900 4:27PM
05/01/2020 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Eco Virginia | 1942001235 | William | Poindexter | 1.000000 |  | Biomicrobics MicroFAST | Biomicrobics MicroFAST | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 |  | 06/03/2021 | 05:53 AM
10/14/2020 |  | RoutineScheduled | 107-07-0177 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Onsite Wastewater Services - May Supply | 1942001627 | Drew | Shull | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 05/28/2021 | 05:41 AM
08/17/2020 |  | Reportable Incident | 2016-143-0150 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | Owner called due to the red light being on and alarm going off. Serviced system. Checked the pump, panel, & floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. Installed a mesh screen for the spinfilter. Replaced the UV light bulb. There is visible wetness on the drainfield - could be from rain - need to keep an eye on it. The weir filter was stopped up. Clearstream and pump tank need to be pumped and cleaned out. No gauge or valve on return. Return is in septic tank not in pump tank. Needs a 6" x 12" riser on the septic tank. The timer is set to 6 minutes every 1 hour. Tanks need to be pumped and cleaned - service tech should be there when doing so - should flush dripfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 08/17/2020 | 12:00 PM
11/03/2020 |  | Routine/Scheduled |  | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Ecoflo |  | Pump |  |  | None |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  |  | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 11/03/2020 | Jan 1 1900 9:15AM
01/17/2020 |  | Routine, Scheduled |  | Loudoun County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim |  |  | None | None | Gravity | Distribution Box | Aggregate Trench | [5 empty] | YES | YES | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/02/2020 | 04:43 AM
01/15/2020 |  | Routine, Scheduled | 234-17-0299 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesapeake | R & K Septic, Inc. |  | John | Butt, Jr |  |  | Clearstream ATU |  | Pump | Drip | Elevated Sand Mound | UV Light |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] |  |  | 4.38 | 7.070000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/15/2020 | Jan 1 1900 3:15PM
12/02/2020 |  | Initial Visit | 182-98-0112 (LEGACY ALT. SYSTEM) | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Central Shenandoah | Onsite Wastewater Services - May Supply | 1942001627 | Drew | Shull |  |  | none | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | THIS SYSTEM RECEIVED A STARTUP INSPECTION ON 12-02-2020 AND WAS COMPLETED BY DKS. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 06/09/2022 | 04:10 PM
12/15/2020 |  | Routine/Scheduled |  | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump | Drip | Elevated Sand Mound | UV Light |  | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  |  | 8.000000 | 3.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 12/15/2020 | Jan 1 1900 1:00PM
10/23/2020 | Alternative | Initial Visit | 157-xx-legacy | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | None | None | Pump | Manifold | Aggregate Trench | None | 450.000000 |  | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | [17 empty] | Real Estate Inspection Real Estate Inspection Primary Septic Tank - normal operating level - pumped for inspection. Pump Tank - piggy back operation - demand dose - normal operating level Low Pressure Pipe distribution - septic tank effluent - manifold valve needs replaced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 10/26/2020 | 07:30 AM
10/27/2020 |  | RoutineScheduled | SWP-01-575 | Spotsylvania | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | ["Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/09/2021 | 03:25 PM
11/06/2020 |  | Initial Visit | 179-STS-87971 | Stafford | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation" ,"Level Sensor Operation" ,"Control Operation"] | ["Distribution Pump Operation" ,"Level Sensor Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Set date and time in panel. Set floats, then ran pumps to get flow rate. Programmed run and rest times. RSV stinger came up a little short. Installer to add 1.5" to make it 18" long. Timed all 3 d-boxes. Installer to add tee to lower box. Installer to ask builder to extend pipe past tanks for sump pump discharge. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
04/02/2020 |  | Routine, Scheduled |  | Loudoun County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | None | None | Pump | Distribution Box | Aggregate Trench | [23 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/12/2020 | 02:21 PM
06/23/2020 |  | Routine/Scheduled | 09-160-0029 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Delta Environmental Products, DF Series |  | Pump | Drip | Drip Tubing | None | 796.000000 | ["None"] | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | Homeowner is having treatment unit and pump tank pumped out this week. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 06/23/2020 | 01:00 PM
09/03/2020 |  | RoutineScheduled | 69160431 | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 2705110225 | Larry | Royston | [9 empty] | ["None"] | ["None"] | YES | [16 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 09/23/2020 | 12:00 AM
02/12/2020 |  | Routine, Scheduled | 033-STS-86675 | Caroline County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Ware, Michele P | 1942001165 | Michele | Ware |  |  | Septic Tank Only | Septic Tank Only | None | None | None | None |  |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/13/2020 | 11:32 AM
01/09/2020 |  | Routine, Scheduled |  | Louisa County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Blue Ridge | Dominion Septic, Inc | 1942001350 | Mike | Cook | 1.000000 |  | None | None | Pump | Distribution Box | Aggregate Trench |  |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/16/2020 | 01:20 PM
09/22/2020 |  | Routine/Scheduled | 04-174-0112 | Prince George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Crater | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. |  |  | Puraflo |  | Pump |  |  |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | Peat moss will require replacement in the next year or two. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 09/22/2020 | Jan 1 1900 10:00AM
06/18/2020 |  | RoutineScheduled | 107-09-0136 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Onsite Wastewater Services - May Supply | 1942001022 | Sara | Tusing | 2.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | inspection Ds | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 05/28/2021 | 05:41 AM
03/25/2020 |  | Routine, Scheduled |  | Prince William County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green | 1.000000 |  | Puraflo |  | Pump |  |  | None |  | ["Effluent Screens"] | [19 empty] | [Comments]: Pump Amps 13.7 ETM 404.74h Cycle 7100Septic Sludge 6" Scum 2"Pump Sludge 0 Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/25/2020 | 08:45 AM
06/24/2020 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Chesapeake | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | Serviced system. Checked the pump, panel, & floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream, changed the filter in the aerator, and changed the mesh screen in the spinfilter. Inlet pipe in the Clearstream is cocked up and backgrading - should be fixed. UV pipe in between tanks appears to have settled - pipe is not on grade - should be fixed. The septic tank needs to be pumped - appears sewer line coming into the septic tank is backgrading to the house - should be fixed. There is standing water on the edge of the mound system does not appear to be leaking from the mound at this time. Recommend adding dirt & grading to divert surface water from the mound | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 06/24/2020 | Jan 1 1900 12:00PM
10/02/2020 |  | Initial Visit | 087-STS-6220 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Old Dominion Onsite, Inc. | 1942001549 | Russell | Revis | [9 empty] | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Level Sensor (Float) Operation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Level Sensor (Float) Operation"] | N/A | [17 empty] | checked float, pump and aerator operation. Took BOD sample. System appears to be working well. Aerator run time: 464:45 Sludge pump: 14:41 Discharge pump: 7:52 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 10/02/2020 | 01:25 PM
10/12/2020 |  | RoutineScheduled | 177-07-0219-SWP | Spotsylvania | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Distribution Pump Operation" ,"BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation" ,"Distribution Pump Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/09/2021 | 03:25 PM
07/20/2020 |  | Routine/Scheduled | 2015-143-0013 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Old Dominion Onsite, Inc. | 1942001503 | Jason | Hackler | 1.000000 | 1500 | Orenco Advantex |  | Pump | Drip | Drip Tubing | UV Light |  | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump","Sludge/Scum Accumulation"] | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump","Sludge/Scum Accumulation"] | N/A | [17 empty] | Cleaned effluent filter, flushed manifold, flushed spin filter and drip field. Reset pressure to 12 psi. Crystal on UV is black. System appears to be operating normally. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 07/20/2020 | 01:00 PM
07/08/2020 | Alternative | Reportable Incident | 136-14-0335 | Gloucester | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | Owner called due to an alarm. Serviced system. Checked the pump, panel, & floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. Installed a re-build kit on the aerator. Replaced the O-Ring in the pump union. The septic tank needs pumping. The timer is set to 3 minutes every 2 hours. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 07/08/2020 | 12:00 PM
01/24/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Fairfax | BLEVINS, JOEL R, SR | 1934000415 | JOEL | BLEVINS |  |  | Microfast | Septic Tank Only | None | None | None | None |  | ["None"] | ["None"] | [18 empty] | [Comments]: Compressor is strong. Blower box has settled and caused the compressor to be at a bad angle. Need to raise the box 4". Cleaned the air filter and the ditches are dry. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/03/2020 | Jan 1 1900 12:31PM
06/02/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | SES MidAtlantic LLC | 1942001203 | James | Green |  |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | ATU needs pumping. Air pressure loss in line to ATU. Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 |  | 04/15/2021 | 09:00 AM
01/10/2020 |  | Routine, Scheduled | 00032279 | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Lord Fairfax | SEAL, CHARLES K | 1934000144 | CHARLES | SEAL | 1.000000 |  |  | Sandfilter, Recirculating | Pump | Distribution Box | Aggregate Trench | None |  | ["None"] | ["None"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/10/2020 | 02:34 PM
10/27/2020 |  | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Greenway Engineering | 1942001008 | Jeremy | Ferguson | 1.000000 | 1000 | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 10/29/2020 | 03:10 PM
12/12/2020 |  | RoutineScheduled | 139-06-0409 | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | dovel enterprises |  | jerry | dovel | [9 empty] | [] | [] | YES | None | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 11/30/2020 | 12:00 AM
04/06/2020 |  | Routine, Scheduled | SWP-03-282 | King George County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Ecoflo | None | Pump | Distribution Box | Aggregate Trench |  |  | ["Distribution Pump Operation","Level Sensor Operation"] | ["Distribution Pump Operation","Level Sensor Operation"] | [18 empty] | [Comments]: Home is for sale. Vent inside Ecoflo pod has developed a few small cracks, not unusual for these units and is not posing any problems. Septic tank does not need pumping. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/27/2020 | 04:14 AM
09/24/2020 |  | Reportable Incident | 073-STS-94345 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | None | None | Pump | Distribution Box | Aggregate Trench | None | 450.000000 | ["Dispersal System Operation","Distribution Pump Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | ["Dispersal System Operation","Distribution Pump Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | [17 empty] | Pumped septic tank & pump tank empty to effect repair / replacement. Replaced / installed new septic tank and pump tank per HD permit 136-20-0219. Distribution Box found to be deteriorated - replaced distribution box with new - spliced to header lines. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 10/06/2020 | 07:00 AM
11/06/2020 |  | RoutineScheduled | 05-192-015 | Tazewell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Trenches | Not Applicable | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","Effluent Screens"] | ["BlowerCompressorAerator Operation","Control Operation","Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
08/17/2020 |  | RoutineScheduled | SD-13-059 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Soils, Inc. | 1940001392 | Markham | Smith | 1.000000 | 1500 | Mirofast 0.75 ATU in a Hanover 1500 top seam tank |  | Gravity | Gravity | Pad | Not Applicable |  | [] | ["BlowerCompressorAerator Operation","Attached Growth Medium"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 09/03/2020 | 08:30 AM
07/01/2020 |  | RoutineScheduled | 69150025 | Frederick | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | none | none | Pump | Gravity |  | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [7 empty] | 07/01/2020 |  | 48.000000 | [5 empty] | Will be sent separately | Inspected | Removed clog between tanks Turned blower back to on | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance |  | 04/26/2021 | 09:04 AM
09/22/2020 |  | RoutineScheduled | 154-05-1089 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | RCWWS | 1942001335 | Randy | Gray | 1.000000 | 1000 | Puroflo |  | Gravity | Pressure | Trenches |  | 75.000000 | ["None","None"] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 09/22/2020 | 07:03 PM
06/22/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/27/2021 | 01:26 PM
10/26/2020 |  | RoutineScheduled | SP-05-606 | Caroline | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Control Operation" ,"Attached Growth Medium" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | ["Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Control Operation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"Attached Growth Medium" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | FAST media is clogged, treatment is poor. Trough is under water. Small leak around conduit at pump tank. Need to redo 3? vent to 6? vent. RO float stuck on needs to be replaced. Proposal to be sent to owner for repairs. | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
06/22/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Onsite Wastewater Services - May Supply | 1942001022 | Sara | Tusing | 2.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Inspected by DKS | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/28/2021 | 05:41 AM
11/17/2020 |  | RoutineScheduled | 179-11-0093-SP | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | DCM Septic LLC | 1942001350 | Michael | Cook | 3.000000 |  | 0-4 | 0-4 | Pump | Gravity | Trenches | Not Applicable | 600.000000 | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | None | Clear | [14 empty] | Inspected | system cleaned and filters cleaned. no pump out needed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 11/17/2020 | 12:00 PM
08/28/2020 |  | RoutineScheduled | 179-06-0145-SP | Stafford | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Recirculation Pump" ,"Attached Growth Medium"] | ["Effluent Screens" ,"Recirculation Pump" ,"Attached Growth Medium"] | YES | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/09/2021 | 03:25 PM
01/02/2020 |  | Routine, Scheduled | 136-03-0011 | Gloucester County | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Three Rivers | Farmer’s Septic Service, Inc. |  | Ross | Cole | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | [Comments]: Serviced system. Checked the pump, panel, & floats (ok). Cleaned the filter in the Clearstream and cleaned the filter in the septic tank. Changed the diffuser in the Clearstream and changed the filter in the aerator. Installed a re-build kit on the aerator. Put a weight on the pump float. Pump tank needs to be pumped and cleaned out to install a spinfilter screen. Visible wetness on the drainfield due to the K-Rain Valve leaks. The pressure switch on the aerator is not hooked up. The timer is set to 10 minutes every 3 minutes at this time - need to get the plans from the owner to check the timer settings. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 01/02/2020 | 12:00 PM
08/01/2020 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 | Pending Payment | EHD - Loudoun | WasteMaster, Inc. | 1942001062 | Tim | Jenkins |  |  | Multiflo FTB | none | Gravity | Gravity |  | Chlorination |  |  |  | NA | [5 empty] | 2.200000 | [9 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 |  | 06/21/2021 | 10:37 AM
11/05/2020 |  | RoutineScheduled | {FIPSCode}-STS-15876 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Wastemaster Inc |  | Timothy | Jenkins | 2.000000 |  | Recirculating Sand Filter |  | Gravity | Gravity | Discharge | Chlorination |  | [] | [] |  | Musty | Clear | 6.900000 |  |  | 2.200000 | [12 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 11/20/2020 | 02:05 PM
06/09/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/14/2021 | 04:27 PM
03/26/2020 |  | Follow-Up | 033-12-0066-SWP | Caroline County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | EZ Treat Sandfilter | None | Pump |  |  |  |  | ["None"] | ["None"] | [18 empty] | [Comments]: Re-sealed all riser joints and grommets. Installed riser over inlet wedge lid on septic tank in order to seal and provide future access. Met EZ Treat personnel on site and assisted with plastic welding of pod seam. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/01/2020 | 06:33 AM
01/09/2020 |  | RoutineScheduled | 171-05-0599 | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | SEAL’S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal | 1.000000 |  | tank only |  | Gravity | Pressure | Trenches |  |  | ["Dispersal System Operation"] | ["Dispersal System Operation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 01/09/2020 | 12:00 AM
01/30/2020 |  | Routine, Scheduled | SP-04-544 | Stafford County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | None | Pump | Distribution Box | Aggregate Trench |  |  | ["Attached Growth Medium","None","Recirculation Pump"] | ["Attached Growth Medium","None","Recirculation Pump"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/02/2020 | 11:52 AM
03/30/2020 |  | Routine, Scheduled |  | Loudoun County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | Orenco Advantex | None | Pump | Distribution Box | Aggregate Trench | [23 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/12/2020 | 02:21 PM
09/05/2020 |  | RoutineScheduled | 2049-97-153 | Prince William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Prince William | Wastemaster Inc |  | Timothy | Jenkins | 2.000000 |  | Recirculating Sand Filter |  | Pump | Gravity | Discharge | Chlorination |  | [] | [] | [18 empty] | System in alarm upon arrival. Pump tank overflowing. Pump contractor pulls in both auto and hand but pump is not pumping | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. |  | 09/11/2020 | 12:30 PM
01/09/2020 |  | Routine, Scheduled | {FIPSCode}-STS-71778 | Caroline County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Ware, Michele P | 1942001165 | Michele | Ware |  |  | Septic Tank Only | Septic Tank Only | None | None | None | None |  |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/13/2020 | 12:46 PM
03/05/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Biomicrobics MicroFAST |  |  |  |  | None |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] |  | Good | Good | [15 empty] | [Comments]: Pump 1 Amps 11.14 ETM 35h 56m Cycles 808Pump 2 Amps 11.20 ETM 35h 15m Cycles 788Septic Sludge 6" Scum 6"ATU Sludge 13" Scum 0Pump Sludge 1" Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/05/2020 | Jan 1 1900 12:21PM
06/30/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/14/2021 | 04:27 PM
05/26/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/27/2021 | 01:26 PM
10/07/2020 |  | RoutineScheduled | 153-STS-20238 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic/EZ-Treat Recirc Tank | Pump Tank | Pump | Pressure | Drip | Not Applicable |  | ["None"] | ["None"] | NO | [9 empty] | 55.000000 | [7 empty] | septic-6"sludge 2"scum/Recirc-0"sludge/ Pump Tank-0"sludge/ No pump out needed at this time. Counts: Pump-561 ETM-120h 32m/ Peak-4 ETM-0 (n/a)/ High-11 ETM-0m/ Zone1-178 ff-10/ Zone2-177 ff-10/ Zone3-175 ff-10/ Water Meter-0032154.08/ No breakout or spongy areas on the drip field. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
01/10/2020 |  | Routine, Scheduled |  | Warren County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Lord Fairfax | Ferguson, Jeremy | 1942001008 | Jeremy | Ferguson | 1.000000 | 1000 | Ecoflo | None | Pump | Drip | Drip Tubing | None |  |  | ["Control Operation","Disinfection","SludgeScum Accumulation"] | [18 empty] | [Comments]: System is in compliance with approved plans and health department regulations. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/31/2020 | 04:16 PM
09/21/2020 |  | RoutineScheduled | SD-06-66 | Madison | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock-Rapidan | Onsite Wastewater Services - May Supply | 1942001022 | Sara | Tusing | 1.000000 |  | Best 1 | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Inspected by DS | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/28/2021 | 05:41 AM
05/15/2020 |  | RoutineScheduled | 107-02-0308 (LEGACY ALT. SYSTEM) | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Onsite Wastewater Services - May Supply | 1942001022 | Sara | Tusing | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Pressure | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | INSPECTION BY DS | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 05/28/2021 | 05:41 AM
04/06/2020 |  | Routine, Scheduled |  | Page County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Lord Fairfax | SEAL, CHARLES K | 1934000144 | CHARLES | SEAL | 1.000000 |  | Septic Tank Only | Biomicrobics MicroFAST | Pump | Manifold | Drip Tubing | None |  | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/22/2020 | 03:17 PM
06/06/2020 |  | RoutineScheduled | 109-07-0420 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 2.000000 | 2500 | Advantex |  | Gravity | Gravity | Trenches |  |  | ["None"] | ["None"] | [18 empty] | 5" of solids in septic tank. Cleaned recirculation basket filter. Flushed treatment unit spray manifold. Tested floats, pump and alarm. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 09/24/2020 | 07:03 PM
12/09/2020 |  | RoutineScheduled | 88-197-173 | Wise | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | EHD - Lenowisco | Wise County Health Dept |  | Rodney | Neece | 1.000000 |  | ATU |  | Gravity | Gravity | Discharge | Chlorination | [10 empty] | Dechlorine tablets are now located in the chambers. | [11 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12/09/2020 | 12:00 AM
11/12/2020 |  | RoutineScheduled | 177-16-0382-SP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter" ,"Attached Growth Medium" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump"] | ["Control Operation" ,"Distribution Pump Operation" ,"Attached Growth Medium" ,"Auxiliary Filter" ,"Effluent Screens" ,"Recirculation Pump"] | YES | [15 empty] | Will be sent separately | Inspected | We recommend replacing the EZ Set riser on the Pump Tank and replacing the 4" pump sleeve with a 6" sleeve. The sewer line has settled at the septic tank inlet. We recommend excavating by machine & re-leveling or replacing this pipe. Alarm appeared to be caused by clogging filters. All floats, pumps, and controls are working properly. | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 |  | 04/09/2021 | 03:25 PM
05/01/2020 |  | Routine, Scheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | EZ Treat Sandfilter |  |  |  |  | None |  | ["Effluent Screens"] | ["Effluent Screens"] |  | Good | [16 empty] | Pump Amps 9.68 Pump Amps 12.34/11.18 Septic Sludge 12" Scum 0 ATU Sludge 3" Scum 0 Pump Sludge 2" Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 05/01/2020 | Jan 1 1900 4:50PM
04/29/2020 |  | RoutineScheduled | 099-STS-89039 | King George | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Ecoflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | ["Attached Growth Medium" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | YES | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
05/28/2020 |  | Reportable Incident | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance | Approved | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green | [9 empty] | ["Disinfection"] | ["Disinfection"] | [18 empty] | Replaced UV Bulb #1 under warranty. | This AOSS should now return to normal function after having provided the above state routine maintenance |  | 05/28/2020 | Jan 1 1900 2:00PM
03/18/2020 |  | Routine, Scheduled |  | Prince William County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Orenco Advantex |  | Pump | Drip | Drip Tubing |  |  | ["Control Operation","Effluent Screens"] | ["Control Operation","Effluent Screens"] |  | Good | Clear | [5 empty] | 03/18/2020 |  | 8.000000 | [7 empty] | [Comments]: Spin filter cleaned.Pump Amps 10.67 ETM 63h 8m Cycles 11334Pump Amps 11.77 ETM 31h 41m Cycles 209Water Meter Reading 19700Septic Sludge 1" Scum 2"ATU Sludge 0 Scum 0Pump Sludge 0 Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/18/2020 | 08:58 AM
05/12/2020 |  | RoutineScheduled | 175-18-0404 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Prince William | Septic Works LLC | 1942001080 | michael | smith | 1.000000 |  | Orenco Advantex | none | Gravity | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/25/2021 | 08:10 AM
10/09/2020 |  | RoutineScheduled | 069040830 | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Greenway Engineering | 1942001008 | Jeremy | Ferguson | 1.000000 | 1500 | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 10/09/2020 | 12:30 PM
05/21/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | 1.000000 |  | Orenco Advantex | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NO | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/28/2021 | 06:02 AM
07/08/2020 |  | Routine, Scheduled | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green | [7 empty] | None |  | ["Level Sensor (Float) Operation"] | [19 empty] | Zone 1 has water coming to surface. Turned off. Needs follow up visit. Pump Amps 12.5 Water Meter Reading 2445670 Septic Sludge 4" Scum 0.25 Pump Sludge 1" Scum 0 | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 07/08/2020 | Jan 1 1900 9:23AM
05/26/2020 |  | Routine/Scheduled | 19-120-0235A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. |  |  | Norweco Singulair ATU |  | Gravity | Distribution Box |  |  |  | ["Blower/Compressor/Aerator Operation","Control Operation","Effluent Screens","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Effluent Screens","Sludge/Scum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 05/26/2020 | Jan 1 1900 1:30AM
12/08/2020 |  | RoutineScheduled | 182-08-0414 | Rockingham | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Central Shenandoah | Onsite Wastewater Services - May Supply | 1942001627 | Drew | Shull | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | inspection ms | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/28/2021 | 05:41 AM
12/11/2020 |  | RoutineScheduled | SD-06-63 | Madison | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Rappahannock-Rapidan | Old Dominion Engineering | 1942001085 | Michael | Craun | 1.000000 |  | Microfast 0.5 |  | Pump |  | Trenches |  |  | ["Control Operation","BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | YES | [18 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12/14/2020 | 01:30 PM
09/11/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | Ecoflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | A bod/tss sample was taken | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 |  | 04/14/2021 | 04:27 PM
01/14/2020 |  | Routine, Scheduled | 033-06-0191-SP | Caroline County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001350 | Mike | Cook | 1.000000 |  | Puraflo | None | Pump | Distribution Box | Aggregate Bed |  |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | [Comments]: We will resend proposal for repajrs | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/16/2020 | 01:20 PM
10/04/2020 |  | RoutineScheduled | SD-06-77 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Soils, Inc. | 1942001004 | Markham | Smith | 2.000000 |  | Puraflo |  | Pump | Gravity | Trenches | Not Applicable |  | ["None"] | ["Attached Growth Medium","SludgeScum Accumulation","Level Sensor Operation","Septic Tank Baffles"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12/04/2020 | 02:00 PM
12/09/2020 |  | RoutineScheduled | 07-184-004 | Scott | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | MULTIFLO |  | Gravity | Gravity | Mound | Not Applicable | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
03/17/2020 |  | Follow-Up |  | Fairfax County | This AOSS should now return to normal function after having provided the above stated routine maintenance. | Approved | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green | [9 empty] | ["Disinfection"] | ["Disinfection"] | [18 empty] | [Comments]: Installed new UV Unit. | This AOSS should now return to normal function after having provided the above stated routine maintenance. |  | 03/17/2020 | Jan 1 1900 2:00PM
11/30/2020 |  | Routine/Scheduled | 05-137-0189 | Goochland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chickahominy | Miller's Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1500 | Orenco Advantex |  | Pump | Distribution Box | Aggregate Trench | None | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | None | Clear | [15 empty] | Routine Service Processing Tank - normal level - RSV, Recirc Pump & effluent screen serviced. Treatment Module - media drapes & spray grid serviced. Pump Tank - normal operating level - pump, float sensors & controls operating properly Distribution Box - concrete - intact - all laterals accepting effluent. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 12/01/2020 | Jan 1 1900 8:00AM
03/25/2020 |  | Routine, Scheduled |  | Loudoun County | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Paid | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | None | None | Pump | Distribution Box | Aggregate Trench | [22 empty] | [Comments]: septic tank and atu | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 04/12/2020 | 02:21 PM
02/09/2020 |  | Routine, Scheduled | SD-15-62 | Culpeper County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | Brown, Jason W | 1942001049 | Jason | Brown | 1.000000 | 1000 | Septic Tank Only | Aqua Safe ATU | Gravity | None | Alternative Discharge | UV Light |  |  |  |  | earthy,musty | clear | [15 empty] | VENIS File Names: O&M Log informal inspection 2-9-20.odt | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/10/2020 | 03:47 PM
09/08/2020 |  | Reportable Incident | 2007-143-0175 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Old Dominion Onsite, Inc. | 1942001549 | Russell | Revis | [9 empty] | ["Blower/Compressor/Aerator Operation","Distribution Pump Operation","Level Sensor (Float) Operation"] | ["Blower/Compressor/Aerator Operation","Distribution Pump Operation","Level Sensor (Float) Operation"] | N/A | [17 empty] | replaced discharge pump and control panel contactor. Cleaned air filter | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 09/09/2020 | 01:10 PM
07/03/2020 | Alternative | RoutineScheduled | 115-06-0044 | Campbell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 300 | Best 1 |  | Gravity | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | NA | Musty | [15 empty] | Inspected | Sludge level-6" Scum layer on top- 12" Sludge layer on bottom- Treatment has good aeration - Discharge Clear effluent, trace of sludge- Cleaned effluent screen -no sludge or scum buildup alarm test operational. Cleaned blower airfilter. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 07/30/2020 | 05:30 PM
03/30/2020 |  | Routine, Scheduled |  | Loudoun County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim |  |  | None | None | Gravity | Distribution Box | Aggregate Bed | [5 empty] | YES | YES | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/12/2020 | 02:21 PM
07/28/2020 | Alternative | RoutineScheduled | 166-09-072 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Church View Septic Service Inc. | 1942001302 | Charles | Langford | 1.000000 | 1000 | Ecoflo |  | Pump |  | Trenches | Not Applicable |  | ["Distribution Pump Operation"] | ["Distribution Pump Operation"] | YES | None | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 09/22/2020 | 12:00 AM
04/01/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | Creighton, Cameron Ellis | 1942001137 | Cameron | Creighton | 1.000000 |  | Orenco Advantex | None | Pump | Distribution Box | Aggregate Trench | None | [22 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/02/2020 | Jan 1 1900 11:56AM
06/09/2020 |  |  | 18-120-0390AR | Chesterfield | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Chesterfield | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Advantex |  | Pump |  | Trenches |  |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | ["Attached Growth Medium","Control Operation","Recirculation Pump","Distribution Pump Operation"] | [18 empty] | Pump line is broken leaving the tank, 1" recirc pipe inside the tank is also broken | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. |  | 09/17/2020 | 12:00 AM
06/01/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Orenco Advantex | Orenco Advantex | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/27/2021 | 01:26 PM
10/17/2020 |  | RoutineScheduled | VPDES-92-1 | Madison | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Wastemaster Inc |  | Timothy | Jenkins |  |  | ATU |  |  | Gravity | Discharge | Chlorination |  | [] | [] |  | Musty | Clear | 7.200000 | 6.100000 | 45.000000 | 2.200000 |  | 10/17/2020 |  | 4.000000 |  |  | 10.300000 |  |  | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 11/16/2020 | 02:15 PM
10/13/2020 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Fairfax | FIVE STAR SEPTIC INC | 1944001248 | AARON | GOINS | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
11/10/2020 |  | RoutineScheduled | XWP-98-643 | Spotsylvania | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  | ["Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Attached Growth Medium" ,"Control Operation"] | ["Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Attached Growth Medium" ,"Control Operation"] | YES | [15 empty] | Will be sent separately | Inspected | Few grass on septic tank inlet wedge lid and pump tank. Peat is totally degraded and very low (1/2 full) needs replaced. Pods are full of roots and therefore we could not properly mix up peat. Discharge pipe has drain back hole, allow dose for 63 gallons. Proposal for repairs to be sent to home owner. | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
11/25/2020 |  | Routine/Scheduled | 05-163-0066 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chickahominy | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1500 | Orenco Advantex | None | Pump | Distribution Box | Aggregate Trench | None | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | None | Clear | [15 empty] | Routine Service Processing Tank - normal level - RSV, recirc pump & effluent screen serviced. Treatment Module - media drapes & spray grid serviced. Pump Tank - normal level - pump serviced - float sensors & controls operating properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 11/30/2020 | Jan 1 1900 8:30AM
06/22/2020 |  | Routine, Scheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | EZ Treat Sandfilter |  | Pump | Drip | Drip Tubing | UV Light |  | ["Disinfection","Effluent Screens"] | ["Disinfection","Effluent Screens"] | [18 empty] | Zone two is soft no water surfacing. Pump Amps 9.34 ETM 433 hrs 5 mins Cycles 8427 Water Meter Reading 118260 Septic sludge 1" Scum 0 ATU Sludge 0 Scum 0 Pump Sludge 3" Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 06/22/2020 | Jan 1 1900 12:44PM
02/24/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Biomicrobics MicroFAST |  | Pump | Drip | Drip Tubing | None |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] |  | Good | Good | [15 empty] | [Comments]: Spin filter cleaned.Pump 1 Amps 7.95 ETM 817h 24m Cycles 3547Pump 2 Amps 7.97Water Meter Reading 235300Septic Sludge 11" Scum 4’ATU Sludge 12" Scum 0Pump Sludge 0.50 ScumCheck valves in D/F need to be checked. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/24/2020 | Jan 1 1900 9:28AM
08/05/2020 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Gravity | Gravity |  | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Sale inspection on a Alternative septic system. The state requires that the septic system be inspected EVERY year and filed with the state and county. The septic control panel is a interior demand dose. There is 1 pvc cleanout. The pvc sewer line was camera snaked and was clear. The septic tank filter is a T filter that was cleaned. The filter manufacture recommend the filter be cleaned every 6 months. There is a concrete riser over the outlet side of the tank. Septic tank was pumped out by another company 7 months ago. The pump tank, pump, floats and force main were inspected. The valve box was in working condition. The LPD drain field was inspected. At time of inspection all components inspected were in working condition. | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 |  | 04/14/2021 | 04:27 PM
11/06/2020 |  | RoutineScheduled | {FIPSCode}-STS-17787 | Scott |  |  | EHD - Lenowisco |  |  | John | Hyder |  |  | Jet |  | Gravity |  |  | Chlorination | 450.000000 |  |  |  | None | Clear | 7.000000 | 5.000000 |  |  | chlorine residual 0 | [10 empty] | No laboratory tests performed. Field inspection only. |  |  |  | 12:00 AM
02/03/2020 | Alternative | Routine, Scheduled | 234-12-12 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesapeake | R & K Septic, Inc. |  | John | Butt, Jr |  |  | Clearstream ATU |  | Pump | Drip | Elevated Sand Mound | UV Light |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] |  |  | 4.96 | 7.710000 | 5.000000 | [13 empty] | [Comments]: Replaced UV bulb | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/03/2020 | Dec 30 1899 9:30AM
05/21/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | GRASS AND WEEDS AROUND TANKS, VALVE BOX AND FIRST DRAIN LINE INFORMED HOME OWNER THEY NEED TO CUT IT DOWN WE WERE ABLE TO INSPECT | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/14/2021 | 04:27 PM
12/12/2020 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 | Pending Payment | EHD - Loudoun | WasteMaster, Inc. | 1942001062 | Tim | Jenkins | 1.000000 |  | none | none | Siphon | Gravity |  | Chlorination |  |  |  | NA | [5 empty] | 1.800000 | [9 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 |  | 06/21/2021 | 10:37 AM
08/07/2020 |  | RoutineScheduled | 179-16-0020-SWP | Stafford | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Attached Growth Medium" ,"Control Operation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | ["Control Operation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Attached Growth Medium" ,"Effluent Screens" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | YES | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
08/12/2020 |  | RoutineScheduled | {FIPSCode}-STS-83661 | Spotsylvania | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Attached Growth Medium"] | ["Effluent Screens" ,"Attached Growth Medium"] | YES | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/09/2021 | 03:25 PM
05/01/2020 |  | RoutineScheduled | 107-14-0170 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Pump | Pressure | Drip | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 06/02/2021 | 12:00 AM
01/27/2020 |  | Routine, Scheduled | 181-01-0144 (LEGACY ALT. SYSTEM) | Rockbridge County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Central Shenandoah |  |  |  |  | 1.000000 | 1500 |  | Biomicrobics MicroFAST | Pump | Drip | Drip Tubing | None |  | ["None"] | ["None"] | [18 empty] | [Comments]: Filters checked and cleaned. Control panels functioning properly. No apparent leaks in system or drain field area. System did not need to be pumped. Lids properly secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/04/2020 | 30-12-1899 10:57 PM
11/18/2020 |  | RoutineScheduled | 069-03-0070 | Frederick | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Rejected | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 2705110222 | Larry | Royston | [9 empty] | ["BlowerCompressorAerator Operation"] | ["None"] | YES | [16 empty] | Inspected | Blower not working | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. |  | 01/19/2021 | 12:00 AM
08/25/2020 | Alternative | Routine/Scheduled | 136-14-0022 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | Delta Environmental Products, UC Series | None | Pump | Distribution Box | Aggregate Trench | None | 450.000000 |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | Musty | Clear | [15 empty] | Annual service conducted. Primary septic tank - slightly high due to clogged effluent screen - screen serviced, tank returned to normal operating level. Processing Tank - at normal operating level - compressor serviced. Discharge Tank - at normal operating level - pump, float sensors and controls operating properly. Distribution box at normal level - 2 speed balancers replaced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 08/28/2020 | 01:00 PM
11/05/2020 |  | Routine/Scheduled | 199-03-0071 | York | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Peninsula | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1500 | Orenco Advantex |  | Pump | Distribution Box | Aggregate Bed | None | 450.000000 |  | ["Attached Growth Medium","Blower/Compressor/Aerator Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | None | Clear | [15 empty] | Routine service Processing Tank - normal operating level - RSV, recirc pump, effluent screen serviced. Treatment Module - media drapes & spray grid serviced. Pump Tank - normal operating level - pump, float sensors & controls operating properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 11/06/2020 | Jan 1 1900 11:00AM
05/14/2020 |  | Routine, Scheduled | 175-15-0447 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Delta Environmental Products, DF Series |  |  |  |  | None |  | ["Blower/Compressor/Aerator Operation"] | ["Blower/Compressor/Aerator Operation"] |  | Good | Good | [15 empty] | Pump Amps 10.86 ETM 690 h Cycles 4792 Water Meter Reading 135090 Septic Sludge 6" Scum 11" ATU Sludge 13" Scum 0 Pump Sludge 6" Scum | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 05/14/2020 | 03:47 PM
01/16/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Fairfax | SEAMON, CHARLIE L | 1942001108 | CHARLIE | SEAMON |  |  | Septic Tank Only | Microfast | Pump | Distribution Box | Aggregate Trench | None |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | [18 empty] | [Comments]: Performance Inspection: Microfast to Drainfield. Septic tank-3"sludge 0"scum/ATU-0"sludge/Pump Tank-0"sludge.Tanks were pumped out several weeks ago. Blower air filter cleaned. Peak-13/High-10/P1 counts-489 ETM-24h26m/P2 counts-478 ETM-24h 11m. Hydromatic SPD 50 pumps-49gpm (115V). No breakout or spongy areas on the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/10/2020 | Jan 1 1900 6:36AM
10/17/2020 |  | RoutineScheduled | SD-00-290 | Culpeper | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Rappahannock-Rapidan | Wastemaster Inc |  | Timothy | Jenkins | 2.000000 |  | ATU | Polishing Sand Filter |  | Gravity | Discharge |  |  | [] | [] | [18 empty] | In to replace multiflo aerator found bad on previous visit. Replaced aerator with new unit. Checked operation. All okay | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 11/05/2020 | 11:45 AM
12/10/2020 |  | Initial Visit | 149-STS-10653 | Prince George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Crater | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | PremierTech, EFX |  | Pump | Distribution Box | Aggregate Trench | None | 450.000000 | ["Attached Growth Medium"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | Musty | Clear | [15 empty] | Septic tank pumped by CWS - supervised by Miller Staff Initial Visit Primary Septic tank - normal level - effluent screen serviced. BioFilter - Fiberglass - Intact - Peatmoss in poor condition - requires replacement - raked / turned. Pump Basin - plastic - intact - pump, float sensors and controls operating. Distribution Box - concrete - intact - all laterals accepting effluent. 12/18/2020 - septic tank pumped empty - scheduled peat change for week of 12/21 - 12/23. 12/22/2020 - Biofilter changeout conducted. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 12/23/2020 | Jan 1 1900 8:15AM
10/30/2020 |  | RoutineScheduled | 1870800063 | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  |  |  | 7.390000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 11/06/2020 | 03:30 PM
11/02/2020 |  | Reportable Incident | 2017-143-0155 | Henrico | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Henrico | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | Owner called due water coming out. Breakers were tripped. Serviced system. Checked the pump, panel, & floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. The UV is not working - replaced the ballast, bulb, and cord - brought the circuit board back to try and repair. The timer is set to 3 minutes every 4 hours. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. |  | 11/02/2020 | 12:00 PM
04/18/2020 |  | RoutineScheduled | SD-86-373 | Culpeper | This AOSS is functioning as designed and in accord | Approved | EHD - Rappahannock-Rapidan | Wastemaster |  | Douglas | Crooks | 1.000000 |  |  |  | gravity |  | discharge | Chlorine |  | [] | [] |  | Low | Clear | 6.700000 |  |  | 1.800000 |  | 04/18/2020 |  | 6.000000 |  |  | 4.600000 |  |  | Attached to this report |  | Functioning as Designed | This AOSS is functioning as designed and in accord |  |  | 12:00 AM
01/30/2020 |  | Routine, Scheduled |  | Louisa County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Blue Ridge | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | None | Pump | Distribution Box | Aggregate Bed |  |  | ["Attached Growth Medium","Effluent Screens","Recirculation Pump"] | ["Attached Growth Medium","Effluent Screens","Recirculation Pump"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/02/2020 | 11:52 AM
06/20/2020 |  | Follow-Up | 196.02.143 | Westmoreland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Dominion Septic, Inc | 1942001068 | David | Stewart |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Replaced low level float in recirc. Repaired broken wire on recirc alarm. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 04/13/2021 | 11:22 AM
02/20/2020 |  | Routine, Scheduled |  | Prince William County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Prince William | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Biomicrobics MicroFAST | None | Pump | Distribution Box | Aggregate Trench |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/25/2020 | 07:16 AM
07/07/2020 |  | Follow-Up |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Homeowner had the septic tank pumped. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/27/2021 | 01:26 PM
09/03/2020 |  | RoutineScheduled |  | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 2705051738 | Joshua | Hott | 1.000000 | 1250 | Septic | Puraflo | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
12/04/2020 |  | Follow-Up | 177-17-0017-SP | Spotsylvania | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart |  |  | EZ Treat Sandfilter | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Replaced EZ Treat alarm horn and alarm light. Installed 4? stub on RSV. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
07/08/2020 |  | RoutineScheduled | 075-STS-31475 | Goochland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | GeoEnvironmental Services, Inc. | 1942001010 | Peter | Mamunes | 1.000000 | 1250 | EZ Treat |  | Pump | Pressure | Drip | Not Applicable | 600.000000 | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 07/13/2020 | Jan 1 1900 3:15PM
09/14/2020 | Alternative | Reportable Incident | 151-15-125 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | Owner called due to it bubbling up by the green cap. Serviced system. Checked the pumps & floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. Replaced the relay in the 600 NC3T panel. Fixed the UV. Replaced the timer, replaced the alarm light bulb, and replaced the buzzer. The mute button on the pump tank panel is bad - needs to be replaced. The timer is set to 4 minutes every 2.5 hours. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 09/14/2020 | 12:00 PM
03/31/2020 |  | Routine, Scheduled |  | Prince William County | This AOSS should now return to normal function after having provided the above stated routine maintenance. | Paid | EHD - Prince William | SEAMON, CHARLIE L | 1942001108 | CHARLIE | SEAMON |  |  | Septic Tank Only | Microfast | Pump | Manifold | Drip Tubing | UV Light |  | ["BlowerCompressorAerator Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation"] | [8 empty] | 03/31/2020 |  | 10.000000 | [5 empty] | Attached to this report |  | [Comments]: Performance Inspection and sample: Microfast to Jet UV Light to Delta Drip.Septic-0"sludge 0"scum Microfast-0"sludge/Pump tank-0"sludge. NOTE the Septic/Microfast tank has paint in it and needs to be pumped out before it starts coating the media. Blower air filter cleaned.Counts: Pump start-3580 Pump run-475/High-6/Override-7 w/m-13,186 VENIS File Names: Greenwood Farm Dr. 3651.pdf | This AOSS should now return to normal function after having provided the above stated routine maintenance. |  | 04/09/2020 | 01:25 PM
09/14/2020 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump | Drip | Elevated Sand Mound | UV Light |  | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  |  | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 09/14/2020 | Jan 1 1900 8:00AM
05/29/2020 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Eco Virginia | 1942001235 | William | Poindexter |  |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Effluent Screens" ,"SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation" ,"SludgeScum Accumulation" ,"Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected | recommended clearing DF | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 |  | 06/03/2021 | 05:53 AM
02/03/2020 |  | Routine, Scheduled | ST-05-12 | Caroline County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Ware, Michele P | 1942001165 | Michele | Ware |  |  | Septic Tank Only | Septic Tank Only | None | None | None | None |  |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/05/2020 | 08:37 AM
03/31/2020 |  | Routine, Scheduled |  | Prince William County | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Paid | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Delta Environmental Products, DF Series |  |  |  |  | None |  | ["BlowerCompressorAerator Operation","Level Sensor Operation"] |  |  | Not treated | Bad | [15 empty] | [Comments]: Compressor is bad. Timer float needs replacing.Spin filter cleaned.Pump Amps 9.60 Cycles 54393Water Meter Reading 1078310Septic Sludge 6" Scum 0.50ATU Sludge 5" Scum 0.25Pump Sludge 4" Scum 0 | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 03/31/2020 | 09:54 AM
02/04/2020 |  | Routine, Scheduled |  | Prince William County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Prince William | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | None | Pump | Distribution Box | Aggregate Trench |  |  | ["Attached Growth Medium","Effluent Screens","Recirculation Pump"] | ["Attached Growth Medium","Effluent Screens","Recirculation Pump"] | [18 empty] | [Comments]: The junction box inside the Advantex tank is broken where it connects to the tank. This will need to be replaced if wiring issues arise or if there is a potential sale of the property. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/02/2020 | 11:52 AM
01/09/2020 |  | Routine, Scheduled | 171-11-0273 | Shenandoah | This AOSS should now return to normal function after having provided the above stated routine maintenance. | Approved | EHD - Lord Fairfax | Cubbage, Harrison Lee, II | 1942001021 | Harrison | Cubbage | 1.000000 | 1000 |  | Delta Environmental Products, DF Series | Pump | Drip | Drip Tubing | None |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Level Sensor Operation"] |  | Musty | Clear | [15 empty] | [Comments]: Replaced Middle Float. Pump Settings: Off 2.5Hr On 10.5min Water Meter: 200.40 Sludge/Scum Accumulations: Septic Tank-12"/4" Clarifier: 12"/0" Pump Tank-3"/0" | This AOSS should now return to normal function after having provided the above stated routine maintenance. |  | 01/18/2020 | 12:08 PM
03/18/2020 |  | Routine, Scheduled | 2016-143-0233 | Henrico County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Henrico |  |  |  |  | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | [Comments]: Serviced system. Checked the pump, panel, & floats (ok). Cleaned the filter and the diffuser in the Clearstream. Changed the filter in the aerator. The septic tank inlet tee was stopped up - full of grease - tech freed it up. The timer is set to 6 minutes every 2 hours. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/18/2020 | 12:00 PM
11/05/2020 |  | RoutineScheduled |  | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Wastemaster Inc |  | Timothy | Jenkins | 2.000000 |  | Recirculating Sand Filter |  | Pump | Gravity | Discharge | Chlorination |  | [] | [] |  | Musty | Clear | 7.400000 |  |  | 2.200000 | [12 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 11/20/2020 | Jan 1 1900 2:10PM
12/09/2020 |  | RoutineScheduled | 061-17-506 | Fauquier | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Rappahannock-Rapidan | McKim Construction | 1942001330 | Michelle | McKim |  |  |  |  | Pump | Gravity | Trenches |  |  | [] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 12/18/2020 | 11:40 AM
08/03/2020 |  | RoutineScheduled | SD-03-7 | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Wastemaster Inc |  | Timothy | Jenkins | 2.000000 |  | ATU | Polishing Sand Filter | Gravity | Gravity | Discharge | Chlorination |  | [] | [] |  | Musty | Clear | 7.400000 |  |  | 2.200000 | [11 empty] | EHS entered visit date based on history of report sent to EHD | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 03:00 PM
06/10/2020 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump | Distribution Box |  | None |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  |  | 5.480000 | 4.800000 | [13 empty] | Replaced aerator | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 06/10/2020 | Jan 1 1900 9:30AM
03/06/2020 |  | Reportable Incident |  | Fairfax County | This AOSS should now return to normal function after having provided the above stated routine maintenance. | Paid | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green | [9 empty] | ["Disinfection"] | ["Disinfection"] | [18 empty] | [Comments]: Installed new UV Bulb. | This AOSS should now return to normal function after having provided the above stated routine maintenance. |  | 03/06/2020 | Jan 1 1900 4:00PM
03/27/2020 |  | Routine, Scheduled | 04-172-0145A | Powhatan County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesterfield | Madison Environmental LLC |  | Larry | Madison, Jr. |  |  | Puraflo |  | Pump | Manifold | Aggregate Bed |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | [Comments]: Septic riser is cracked and should be replaced. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/27/2020 | Jan 1 1900 10:00AM
06/02/2020 |  | RoutineScheduled |  | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | FIVE STAR SEPTIC INC | 1944001248 | AARON | GOINS | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 06/02/2020 | 12:00 AM
01/07/2020 |  | Routine, Scheduled | 2013-143-0160 | Henrico County | This AOSS should now return to normal function after having provided the above stated routine maintenance. | Approved | EHD - Henrico | [7 empty] | Septic Tank Only | None | None | None | None | [22 empty] | This AOSS should now return to normal function after having provided the above stated routine maintenance. |  | 02/12/2020 | 11:09 AM
03/02/2020 |  | Routine, Scheduled |  | Loudoun County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim |  |  | Best 1 | None | Pump | Distribution Box | Aggregate Trench | [5 empty] | YES | YES | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/12/2020 | 02:21 PM
05/12/2020 |  | Routine/Scheduled | 124-STS-2379 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Rejected | EHD - Chickahominy | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1500 | Orenco Advantex | None | Pump | Distribution Box | Aggregate Trench | None |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | [17 empty] | Recirculation Pump and Floats have exceeded expected life span; the Hinges for the Advantex Media Unit Lid were found broken, the Support Struts had failed, and the Media Sheets have exceeded their expected life; the Discharge Pump and Floats have exceeded their expected life, and groundwater is leaking into the Riser; the Control Panel has exceeded its expected life | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 05/16/2020 | Jan 1 1900 4:08PM
02/17/2020 |  | Routine, Scheduled | 182-12-0146 | Rockingham County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Central Shenandoah |  |  |  |  | 1.000000 | 1500 |  | Biomicrobics MicroFAST | Pump | Drip | Drip Tubing | None |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation"] |  | Musty | Clear | [15 empty] | [Comments]: Added solution to media to help with sludge. Pump Settings: Off 2hrs On 5min ETM-318.92Hr Cycle Count-5513 Sludge/Scum Accumulations: Comp.1-16"/6" Comp.2-16"/0" Pump Tank-8"/0" | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/22/2020 | 30-12-1899 04:10 PM
09/30/2020 |  | RoutineScheduled | 04-120-0399A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Wastemaster Inc |  | Timothy | Jenkins | 2.000000 |  | Advantex |  | Pump | Pressure | Drip |  |  | ["SludgeScum Accumulation"] | [] | [18 empty] | Recommend having system pumped out. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 10/09/2020 | Jan 1 1900 12:55PM
08/21/2020 |  | RoutineScheduled | 101-06-0677 | Albemarle | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Blue Ridge | Onsite Wastewater Services - May Supply | 1942001627 | Drew | Shull | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Pressure | Drip | Not Applicable |  |  |  | NA | None | Clear | [13 empty] | Will be sent separately | Inspected | INSPECTION COMPLETED ON 08-21-2020 BY DKS | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 06/09/2022 | 04:10 PM
01/16/2020 |  | Routine, Scheduled | 234-13-18 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesapeake | R & K Septic, Inc. |  | Craig | Van Holten |  |  | Clearstream ATU |  | Pump | Distribution Box |  |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | [Comments]: Replaced aerator | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/16/2020 | Jan 1 1900 4:00PM
03/18/2020 |  | Routine, Scheduled | {FIPSCode}-STS-67375 | Spotsylvania County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Biomicrobics MicroFAST | None | Pump | Drip | Drip Tubing |  |  | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation","Distribution Pump Operation"] | ["Attached Growth Medium","Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation","Distribution Pump Operation"] | [18 empty] | [Comments]: We recommend pumping the Septic Tank and the Aerobic Treatment Unit due to sludge accumulation. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/06/2020 | 02:45 PM
09/09/2020 |  | Routine/Scheduled | 154-17-0263 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Old Dominion Onsite, Inc. | 1942001134 | John | Ewing | 1.000000 | 1000 | Puraflo |  | Pump | Distribution Box | Aggregate Bed | None | 250.000000 | ["Control Operation","Dispersal System Operation"] | ["Control Operation","Dispersal System Operation"] | N/A | [17 empty] | System appeared to be operating correctly. Dispersal is getting overgrown and should be mowed regularly. Discharge ETM 105 h 59 min | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 09/09/2020 | 08:57 AM
04/22/2020 |  | RoutineScheduled |  | Warren | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Control Operation"] | ["Auxiliary Filter" ,"Control Operation"] | NA | [7 empty] | 04/22/2020 |  | 45.000000 | [5 empty] | Will be sent separately | Inspected | Recommend having all tanks pumped. Contact us at 540-860-8086 to have this performed. Lab Results attached | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/26/2021 | 09:04 AM
06/09/2020 | Alternative | RoutineScheduled | 128.13.0046 | Essex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers |  |  | joel | pinnix | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
03/27/2020 |  | Routine, Scheduled | SD-10-247 | Fauquier County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | JENKINS, TROY C, JR | 1942001050 | TROY | JENKINS |  |  | Septic Tank Only | Septic Tank Only | None | None | None | None | 11810.000000 | ["Control Operation"] | ["Control Operation"] |  |  |  | 7.160000 |  |  |  |  | 03/27/2020 | Effluent PS | 12.000000 |  |  | 7.800000 |  |  | Attached to this report |  | [Pumpout Comments]: System was not pumped | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/14/2020 | 01:15 PM
03/31/2020 |  | Routine, Scheduled |  | Warren County | This AOSS should now return to normal function after having provided the above stated routine maintenance. | Paid | EHD - Lord Fairfax | Cubbage, Harrison Lee, II | 1942001021 | Harrison | Cubbage | 1.000000 | 1500 | Septic Tank Only | Biomicrobics MicroFAST | Pump | Drip | Drip Tubing | None |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation"] |  | Musty | Clear | [15 empty] | [Comments]: Replaced oring on spin clean filter Pump Settings: Off 2hrs On 10min ETM-589.44Hr Cycle COunt-6193 Sludge/Scum Accumulations: Comp.1-13"/6" Comp.2-12"/0" Pump Tank-6"/0" | This AOSS should now return to normal function after having provided the above stated routine maintenance. |  | 04/06/2020 | 12:53 PM
04/09/2020 |  | Routine, Scheduled | VPDES-92-1 | Madison County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | JENKINS, TIMOTHY R | 1942001062 | TIMOTHY | JENKINS | 1.000000 |  | Multiflo ATU | Septic Tank Only | None | Drip | Alternative Discharge | Chlorine |  | ["None"] | ["None"] |  | Musty | Clear | 6.800000 |  |  | 2.200000 | [12 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/22/2020 | 01:54 AM
01/30/2020 |  | Follow-Up |  | Prince William County | This AOSS should now return to normal function after having provided the above stated routine maintenance. | Paid | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green | [9 empty] | ["Level Sensor Operation"] | ["Level Sensor Operation"] | [18 empty] | [Comments]: Installed new float. | This AOSS should now return to normal function after having provided the above stated routine maintenance. |  | 01/30/2020 | 01:30 PM
12/30/2020 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Gravity | Gravity |  | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | An inspection of a conventional pump septic system. The septic control panel is an interior demand dose. There was 1 pvc cleanout near the house. The sewer line was camera snaked and was clear. The septic tank was pumped out and the tank was inspected for any leaks or cracks none were seen. The pump tank, pump, floats and force main were inspected . The 8 port concrete d-box was dug up it was 6" under the ground and all 6 header lines were camera snaked and clear. The drain field was probed and dry. At time of inspection all components were in working condition. | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 |  | 04/14/2021 | 04:27 PM
05/12/2020 |  | RoutineScheduled | 01-197-376 | Wise | This AOSS is functioning as designed and in accord | Approved | EHD - Lenowisco | Septic Inc |  | Denny | Deel |  |  |  |  | Gravity | None | Alternative Discharge | Chlorine | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens"] | true | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accord |  |  | 12:00 AM
04/09/2020 |  | Routine, Scheduled | 179-STS-90578 | Stafford County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Puraflo | None | Pump | Distribution Box | Aggregate Trench |  |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [18 empty] | [Comments]: Septic tank needs to be pumped out. Few roots at wedge lid on septic and pump tanks. Proposal for repairs to be sent to homeowner: Reseal all pipe penetrations on tanks. Repair broken conduit at panel and replace panel port. Repair settled pump line. Add inlet riser to septic tank in order to seal opening and provide access for maintenance. Seal pump tank wedge lid. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/27/2020 | 04:14 AM
07/14/2020 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Gravity | Gravity |  | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | sale inspection on a conventional pump septic system. Septic control panel is a interior demand dose. There is 1 pvc clean out near the house. The sewer line was camera snaked and was clear. Septic tank has a 6" pvc pipe for access. The pump tank, pump, floats and force main were inspected . The concrete lid needs to be replaced it is starting to crumble. The 6 port concrete d-box was dug up it was 12" under the ground. All 4 header lines were camera snaked and were clear. Drain field was probed and dry. At this time all components are in working condition except the pump tank lid that needs replaced. | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 |  | 04/14/2021 | 04:27 PM
05/01/2020 |  | Follow-Up |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | SES MidAtlantic LLC | 1942001203 | James | Green | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Pressure | Drip | Not Applicable |  | ["Dispersal System Operation"] | ["Dispersal System Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Repaired leak in hydraulic unit. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/15/2021 | 09:00 AM
02/19/2020 |  | Routine, Scheduled | {FIPSCode}-STS-86477 | Spotsylvania County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Norweco Singulair ATU | None | Gravity | Distribution Box | Aggregate Trench |  |  | ["Effluent Screens","Recirculation Pump"] | ["Effluent Screens","Recirculation Pump"] | [18 empty] | [Comments]: Recommend removing outer riser to secure spacer and reinstall riser. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/02/2020 | 11:52 AM
10/20/2020 |  | Follow-Up | 2015-143-0147 | Henrico | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Henrico | Wastemaster Inc |  | Timothy | Jenkins | [9 empty] | [] | [] | [18 empty] | In for alarm. ound pump tank high level. Floats twisted up. Installed new float ree to seperate the folats to avoid twisting. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 11/05/2020 | 11:55 AM
09/18/2020 |  | RoutineScheduled | 133 05 0920 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Advantex AX20 |  | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | NA | [16 empty] | Inspected | System pumped out last year. Septic zone 1" scum 14" new color sludge- Recirc zone 4" sludge Newish color, Bio filter minimally dirty -c leaned, Flushed and brushed manifold, sprayed off media, No alarms since jan 2018, Ran system in test mode, All functional | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 09/19/2020 | 09:30 AM
09/22/2020 |  | RoutineScheduled | 187190125 | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Greenway Engineering | 1942001008 | Jeremy | Ferguson | 1.000000 | 1530 | Microfast | none | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","SludgeScum Accumulation"] | NA | [7 empty] | 09/22/2020 | Pump Chamber | 5.070000 | [8 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 09/29/2020 | 03:55 PM
09/23/2020 |  | RoutineScheduled |  | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic-11"sludge 2"scum | Recirc Tank-5" sludge | Gravity | Gravity | Trenches | Not Applicable |  | ["Effluent Screens","Recirculation Pump","Other"] | ["Effluent Screens","Recirculation Pump","Other"] | YES | [17 empty] | Septic Tank-11"sludge 2"scum/ Recirc. Tank-5"sludge/ Replaced 9 spray heads in the EZ-Treat unit/ Cleaned clogged septic filter/ Cleaned clogged recirc. pump intake for EZ-Treat. Recommend aeration and grass seed on the drainfield. No ponding or breakout on the drainfield. System now functioning as designed. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  |  | 12:00 AM
10/08/2020 |  | RoutineScheduled | 177-STS-92603 | Spotsylvania | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Rappahannock | Wastemaster Inc |  | Timothy | Jenkins | 2.000000 |  |  |  | Pump | Pressure | Drip |  |  | [] | [] | [18 empty] | Owner reports high level alarm. and water coming out under lid. Pump discharge piping has separated. Repaired piping. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 10/08/2020 | 12:30 PM
11/23/2020 |  | RoutineScheduled | 061-16-250 | Fauquier | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 5.000000 |  | Bio Barrier | Bio Barrier | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | Biweekly inspection. Peak count in surge dosing panel up to 1056 (22 new cycles). Cleaned spin filter and air filter for atu #2 (the only one in use). In the past 14 days, an average of 2,277.3 gals per day at 287.2 gals per dose (avg.) was pumped to the dripfield for a total of 31,883 gallons. | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
09/22/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | UV |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/27/2021 | 01:26 PM
08/08/2020 |  | RoutineScheduled | 2070-01-153 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Wastemaster Inc |  | Timothy | Jenkins | 2.000000 |  | Recirculating Sandfilter |  | Pump | Gravity | Discharge | Chlorination |  | [] | [] |  | Musty | Clear | 6.600000 |  |  | 2.200000 | [12 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 09/03/2020 | 01:40 AM
12/30/2020 |  | Routine, Scheduled | 175-11-0491 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | EcoPod |  |  |  |  | None |  | ["Blower/Compressor/Aerator Operation"] | ["Blower/Compressor/Aerator Operation"] |  | Acceptable | Clear | [15 empty] | Spin filter cleaned. Pump Amps 8.27 ETM 2651 Cycles 36015 Water Meter Reading 0853.580 Septic Sludge 8" Scum 2" Pump Sludge 0 Scum 0 On 5 mins 1 sec Off 1 hr 55 mins | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 12/30/2020 | 04:30 PM
05/07/2020 |  | RoutineScheduled | 179-12-0057-SWP | Stafford | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Clearstream | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation" ,"Level Sensor Operation" ,"Control Operation" ,"BlowerCompressorAerator Operation" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | ["Distribution Pump Operation" ,"Level Sensor Operation" ,"Septic Tank Baffles" ,"BlowerCompressorAerator Operation" ,"Control Operation" ,"SludgeScum Accumulation"] | NA | [15 empty] | Will be sent separately | Inspected | ATU needs pumped, pump out scheduled for 5/19 by Marshalls. BOD collected waiting on results. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
04/22/2020 |  | Follow-Up |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | SES MidAtlantic LLC | 1942001203 | James | Green |  |  | Biomicrobics MicroFAST | none | Pump | Pressure | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Dispersal System Operation"] | ["Dispersal System Operation" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Installed new compressor and repaired LPD lateral. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/15/2021 | 09:00 AM
05/18/2020 |  | RoutineScheduled | 154-03-0039 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Enviro-Klean Co. | 1942001087 | michael | clark | [9 empty] | [] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 05:30 AM
11/17/2020 |  | RoutineScheduled | 109-06-0255 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1000 | Multiflo |  | Pump | Pressure | Drip | Not Applicable |  | [] | [] | NA | [16 empty] | Inspected | Septic Tank 3" scum, 16" sludge, Good Aeration. Some sludge build up on deck. Pump Tank 6" sludge, Pump Pulls 6.96 Amps. 240v. Pump Alarm Panel is still operational. Drainfield appears fine, System Operational | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 11/19/2020 | 09:30 AM
01/30/2020 |  | Routine, Scheduled | {FIPSCode}-STS-67316 | Spotsylvania County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Delta Environmental Products, DF Series | None | Pump | Drip | Drip Tubing |  |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Distribution Pump Operation"] | [18 empty] | [Comments]: There is a large bush next to the headworks box that should be removed so the filter can be serviced. The headworks box has settled and the spin filter housing is lodged. Please let is know when it has been removed so we can dig up the housing for the box & reinstall the spin filter housing to service the filter. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/02/2020 | 11:52 AM
12/01/2020 |  | Routine/Scheduled | 147-16-0007 | James City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Peninsula | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | Serviced system. Checked the pump, panel, & floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. The timer is set to 2 minutes every 2 hours. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12/01/2020 | Jan 1 1900 12:00PM
04/18/2020 |  | Pump-Out Only |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | POWELLS PLUMBING, INC. | 1942001036 | Kurt | Holthaus |  |  | Microfast | [6 empty] | ["Sludge/Scum Accumulation"] | ["Sludge/Scum Accumulation"] | N/A | [17 empty] | Pumped Microfast | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 07/10/2020 | 01:31 PM
04/30/2020 |  | Initial Visit | 085-STS-31789 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 600.000000 |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump","Septic Tank Baffles","Sludge/Scum Accumulation"] | NA | None | Clear | [15 empty] | System start-up / commissioning | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 04/30/2020 | Jan 1 1900 12:30PM
01/31/2020 |  | Follow-Up |  | Loudoun County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | None | Pump | Distribution Box | [23 empty] | [Comments]: sample box lid was replaced | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/12/2020 | 02:21 PM
07/27/2020 |  | Routine/Scheduled | 13-137-0174 | Goochland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chickahominy | Miller's Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1500 | Orenco Advantex | None | Pump | Distribution Box | Aggregate Trench | None | 600.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | None | Clear | [15 empty] | Routine service conducted. Primary septic tank at normal level Processing tank at normal level - RSV, Effluent screen, recirculation pump serviced. AdvanTex Module - media drapes serviced, distribution grid serviced. Distribution box at normal level | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 07/28/2020 | Jan 1 1900 7:50AM
11/18/2020 |  | RoutineScheduled | 107-05-0464 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Garland Easter Septic Service | 1942001206 | Garland | Easter |  |  |  |  | Pump | Pressure | Drip | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 06/02/2021 | 12:00 AM
09/23/2020 |  | Follow-Up | 175-15-0477 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green | [9 empty] | ["Disinfection"] | ["Disinfection"] | [18 empty] | Replaced UV Bulb. | This AOSS should now return to normal function after having provided the above state routine maintenance |  | 09/23/2020 | 01:30 PM
09/21/2020 |  | Routine/Scheduled | 2008-143-0012 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Henrico | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 500 | Biomicrobics MicroFAST | None | Pump | Drip | Drip Tubing | None | 450.000000 |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | Musty | Clear | [15 empty] | Routine Service Trash Tank in normal operating level Aeration Tank - operating - compressor serviced. Pump Tank - Normal operating level - pump, float sensors and controls operating properly. Drip Field - serviced drip screen - no indications of surfacing. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 10/05/2020 | 07:30 AM
10/01/2020 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump | Drip | Elevated Sand Mound | UV Light |  | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 10/01/2020 | Jan 1 1900 11:45AM
10/15/2020 |  | Reportable Incident | 036-STS-34328 | Charles City | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Approved | EHD - Chickahominy | Old Dominion Onsite, Inc. | 1942001549 | Russell | Revis | [9 empty] | ["Dispersal System Operation"] |  | N/A | [17 empty] | Alarm is being caused by water coming in from drain field after rain events. System components are working well but are unable to deal with the amount of water coming in. Manually pumped the recirc down to operating level. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. |  | 10/15/2020 | Jan 1 1900 10:00AM
07/11/2020 |  | RoutineScheduled | 067-STS-38687 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 2000 | MicroFast |  | Pump | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | [18 empty] | Replaced blower on 6-13-2020. Blower was still operational, but bearings were loud and failing. 12" in septic tank. 6" in MicroFast septic tank. 12" in treatment unit. 0" in pump tank. Aeration appears to be slightly better after changing blower. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 09/25/2020 | 07:03 PM
01/03/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Fairfax | Hott, Joshua D. | 1942001301 | Joshua | Hott |  |  | Septic Tank Only | Septic Tank Only | None | None | None | None | [22 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/25/2020 | Jan 1 1900 3:43PM
06/02/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Atu and pump tank need to be pumped out | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 |  | 04/14/2021 | 04:27 PM
06/11/2020 |  | RoutineScheduled | 179-STS-91627 | Stafford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Wastemaster Inc |  | Timothy | Jenkins | 2.000000 |  | Recirculating Sand Filter |  | Pump | Gravity | Discharge | Chlorination |  | ["SludgeScum Accumulation"] | [] |  | Musty | Clear | 6.600000 |  |  | 1.400000 | [11 empty] | Bucket of unidentifiable substance should be removed from #1 filter. Weeds in both filters are dead. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 04:40 PM
06/04/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/27/2021 | 01:26 PM
11/25/2020 |  | Reportable Incident | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance | Approved | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green | [9 empty] | ["None"] | ["None"] | [18 empty] | Sealed inlet, outlets & mid seams on septic & pump tanks. | This AOSS should now return to normal function after having provided the above state routine maintenance |  | 11/25/2020 | Jan 1 1900 4:00PM
11/05/2020 |  | RoutineScheduled | 17-137-0175 | Goochland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | GeoEnvironmental Services, Inc. | 1942001010 | Peter | Mamunes | 1.000000 | 1500 | EZ Treat Sandfilter |  | Pump | Pressure | Trenches |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["SludgeScum Accumulation","Recirculation Pump","Level Sensor Operation","Dispersal System Operation","Distribution Pump Operation","Control Operation","Attached Growth Medium"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 11/10/2020 | Jan 1 1900 2:30PM
05/07/2020 | Alternative | Routine/Scheduled | 151-09-0161 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | Ecoflo | None | Pump | Distribution Box | Aggregate Trench | None |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | The Septic Tank has an outdated Filter (we recommend its replacement during your next scheduled pumping service); the Pump and Floats are near/past their expected life, and the existing electrical connections at the Pump Tank are susceptible to ground water infiltration | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 06/26/2020 | 03:42 PM
08/19/2020 |  | RoutineScheduled | SR-98-350 | Spotsylvania | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Control Operation" ,"Distribution Pump Operation" ,"SludgeScum Accumulation"] | ["Auxiliary Filter" ,"Control Operation" ,"Distribution Pump Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Tanks in high level. Slow drip rate due to dirty disc filters. Repaired big leak at inlet side of solenoid valve for zone 1. Cleaned out holes that were plugged in sand filter h-pipes. Tanks need pumped out, owner to make arrangements. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
10/01/2020 |  | RoutineScheduled | 154-08-0192 | Louisa | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Blue Ridge | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Attached Growth Medium"] | ["Attached Growth Medium" ,"Recirculation Pump"] | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/09/2021 | 03:25 PM
04/14/2020 |  | RoutineScheduled | 181-06-0082 | Rockbridge | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Central Shenandoah | Onsite Wastewater Services - May Supply | 1942001022 | Sara | Tusing | 1.000000 |  | Orenco Advantex | none | Pump | Gravity |  | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/28/2021 | 05:41 AM
02/12/2020 |  | Routine, Scheduled | 093-06-0388 | Isle of Wight County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Western Tidewater | R & K Septic, Inc. |  | John | Butt, Jr |  |  | Clearstream ATU |  | Pump | Drip |  | UV Light |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] |  |  |  | 7.970000 | 3.000000 | [13 empty] | [Comments]: Replaced aerator | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/12/2020 | Jan 1 1900 11:00AM
04/17/2020 |  | Routine, Scheduled | 2005-143-0109 | Henrico County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Henrico | [8 empty] | Pump | Drip |  |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/17/2020 | 01:30 AM
05/20/2020 |  | Reportable Incident | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance | Approved | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green | [9 empty] | ["Level Sensor (Float) Operation"] | ["Level Sensor (Float) Operation"] | [18 empty] | Replaced 3 control floats. | This AOSS should now return to normal function after having provided the above state routine maintenance |  | 05/20/2020 | Jan 1 1900 1:30PM
10/02/2020 |  | Pump-Out Only |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | POWELLS PLUMBING, INC. | 1942001036 | Kurt | Holthaus |  |  | Microfast | [6 empty] | ["Sludge/Scum Accumulation"] | ["Sludge/Scum Accumulation"] | N/A | [17 empty] | Pumped Microfast and pump chamber. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 11/19/2020 | 02:24 PM
06/01/2020 |  | RoutineScheduled | 15-183-119 | Russell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 06/01/2020 |  | 3.350000 |  |  | 1.200000 |  |  | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 06/01/2020 | 12:00 AM
10/06/2020 | Alternative | Routine/Scheduled | 159-10-124 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | Serviced system. Checked the pump, panel, & floats (ok). Cleaned the filter in the Clearstream and cleaned the filter in the septic tank. Changed the diffuser in the Clearstream and changed the filter in the aerator. Pumped the septic tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 10/06/2020 | 12:00 PM
09/10/2020 |  | RoutineScheduled | 2061-99-153 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Wastemaster Inc |  | Timothy | Jenkins | 2.000000 |  | Recirculating Sand Filter |  | Pump | Gravity | Discharge | Chlorination |  | [] | [] |  | Musty | Clear | 6.700000 |  |  | 2.200000 | [12 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 10/06/2020 | 01:25 PM
04/23/2020 |  | Routine/Scheduled | 093-02-0108 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | Serviced system. Checked the pump, panel, & floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. The septic tank needs additional risers on it so it can be properly inspected in the future. The timer is set to 1 minute every 3 hours. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 04/23/2020 | Jan 1 1900 12:00PM
08/17/2020 |  | Reportable Incident |  | Suffolk | This AOSS should now return to normal function after having provided the above state routine maintenance | Pending Payment | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Whitewater ATU |  | Gravity |  |  | None |  | ["Control Operation"] | ["Control Operation"] | N/A | [17 empty] | Replaced junction box and rewired alarm float in DWW tank | This AOSS should now return to normal function after having provided the above state routine maintenance |  | 08/17/2020 | Jan 1 1900 8:30AM
12/13/2020 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Wastemaster Inc |  | Timothy | Jenkins |  |  | ATU |  |  |  | Drip | Chlorination |  | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
05/07/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/27/2021 | 01:26 PM
12/09/2020 |  | RoutineScheduled | 182-05-0061 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | None | Clear | 7.540000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12/17/2020 | 03:05 PM
04/22/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | SES MidAtlantic LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Effluent Screens" ,"Level Sensor Operation" ,"Auxiliary Filter"] | ["Effluent Screens" ,"Auxiliary Filter"] | YES | [15 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. Needs new timer float. | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 |  | 04/15/2021 | 09:00 AM
06/01/2020 |  | RoutineScheduled | 12-192-118 | Tazewell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. |  | Denny | Deel |  |  | WHITEWATER |  | Gravity | Gravity | Discharge | UV | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Effluent Screens"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Effluent Screens"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
10/09/2020 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Fairfax | FIVE STAR SEPTIC INC | 1944001248 | AARON | GOINS | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 10/09/2020 | 12:00 AM
07/28/2020 |  | RoutineScheduled |  | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Soils, Inc. | 1940001392 | Markham | Smith | 2.000000 | 9000 | Mirofast 1.5 in a Hanover 4000 top seam tank |  | Pump | Gravity | Trenches | Not Applicable | 431.000000 | [] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Dispersal System Operation","Distribution Pump Operation","Septic Tank Baffles","SludgeScum Accumulation"] | NA | None | [6 empty] | 06/28/2002 | Sample Chamber | 73.000000 | [5 empty] | Attached to this report |  | Both Pump are running at 51.4 GPM 6in of scum 12+ Sludge Pump out is Recommend | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 07/31/2020 | Jan 1 1900 10:35AM
04/17/2020 |  | Routine, Scheduled | 175-05-0626 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Delta Environmental Products, DF Series |  |  |  |  | None |  | ["Blower/Compressor/Aerator Operation"] | ["Blower/Compressor/Aerator Operation"] |  | Good | Clear | [15 empty] | Spin filter cleaned. Pump Amps 7.89 ETM 1 h Cycles 128144 Water Meter Reading 829020 Septic Sludge 6" Scum 0.50 ATU Sludge 4" Scum 2" Pump Sludge 3" Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/17/2020 | 03:04 PM
10/13/2020 |  | Routine/Scheduled | 2019-143-0005 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Old Dominion Onsite, Inc. | 1942001549 | Russell | Revis | [9 empty] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation"] | N/A | [17 empty] | Took BOD and fecal samples. Changed UV bulb. Cleaned air filter. Flushed both drip field zones and spin filter. Checked float and pump operation in discharge tank. Adjusted recirculation setting from 30 to 18 as there was too much water recirculating. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 10/13/2020 | 02:15 PM
03/20/2020 |  | Routine, Scheduled | SD-06-303 | Culpeper County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | CLARK, MICHAEL J | 1934000023 | MICHAEL | CLARK |  |  | Septic Tank Only | Septic Tank Only | None | None | None | None |  |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/01/2020 | 04:04 AM
03/18/2020 |  | Routine, Scheduled | 177-17-0150-SWP | Spotsylvania County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | None | Pump | Distribution Box | Aggregate Trench |  |  | ["Attached Growth Medium","None","Recirculation Pump"] | ["Attached Growth Medium","None","Recirculation Pump"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/06/2020 | 02:45 PM
09/21/2020 |  |  | 06-142-0282 | Hanover | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Microfast | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [18 empty] | Replace microfast blower | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 09/24/2020 | 12:00 AM
03/18/2020 |  | Routine, Scheduled | 171-06-0028 | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Lord Fairfax | Cubbage, Harrison Lee, II | 1942001021 | Harrison | Cubbage | 1.000000 | 1500 |  | Orenco Advantex | Pump | Drip | Drip Tubing | None |  | ["Auxiliary Filter","Control Operation","Dispersal System Operation"] | ["Auxiliary Filter","Control Operation","Dispersal System Operation"] |  | Musty | Clear | [15 empty] | [Comments]: Recirc Pump- Off 19.7min On .3min ETM-1012.0Hr Cycle Count-95041 Discharge Pump- Off 2hrs On 12min ETM-816.9HR Cycle Count-19997 Sludge/Scum Accumulations: Comp.1-8"/1" Comp.2- 8"/0" Pump Tank-3"/0" | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/29/2020 | 12:11 PM
09/29/2020 |  | RoutineScheduled |  | Rockingham | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Dispersal System Operation" ,"Auxiliary Filter"] | ["Control Operation" ,"Dispersal System Operation" ,"Auxiliary Filter"] | NA | [7 empty] | 09/29/2020 |  | 27.000000 | [5 empty] | Will be sent separately | Inspected | Lab Sample Normal | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/26/2021 | 09:04 AM
12/03/2020 |  | RoutineScheduled | 179-18-0318-SWP | Stafford | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Septic Works LLC | 1942001080 | michael | smith | 1.000000 |  | Orenco Advantex | none | Gravity | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/25/2021 | 08:10 AM
03/30/2020 |  | Initial Visit |  | Warren | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Review | EHD - Lord Fairfax | Greenway Engineering | 1942001008 | Jeremy | Ferguson | 1.000000 | 1500 | Microfast | none | Pump | Pressure | Drip | Not Applicable |  | ["Level Sensor Operation","SludgeScum Accumulation","BlowerCompressorAerator Operation"] | ["SludgeScum Accumulation","Level Sensor Operation","BlowerCompressorAerator Operation"] | NA | [7 empty] | 03/30/2020 | Sample Tap | 62.000000 | [5 empty] | Attached to this report |  | Septic tank needs pumped out. would not allow me to attach sample results | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. |  | 07/21/2020 | 11:10 AM
03/26/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Puraflo |  | Pump |  |  | None |  | ["Effluent Screens"] | ["Effluent Screens"] |  | Good | [16 empty] | [Comments]: Pump Amps 13.45/14.57 ETM 2495h/2319h Cycles 2031/1998Pump Amps 9.74/12.10 ETM 489605/211 Cycles 803/748Septic Sludge 10" Scum 0Pump Sludge 1"/0 Scum 1"/0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/26/2020 | Jan 1 1900 8:45AM
06/26/2020 |  | RoutineScheduled | 177-13-0135-SWP | Spotsylvania | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Septic Works LLC | 1942001080 | michael | smith | 1.000000 |  | Orenco Advantex | none | Gravity | Gravity |  | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/25/2021 | 08:10 AM
11/07/2020 |  | RoutineScheduled | 139160023 | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | dovel enterprises |  | jerry | dovel | 2.000000 | 1000 | 1000 |  | Pump | Pressure |  |  |  | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 11/10/2020 | 12:00 AM
01/24/2020 |  | Initial Visit | 041-STS-259463 | Chesterfield | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Chesterfield | Old Dominion Onsite, Inc. |  | Jason | Hackler | 1.000000 | 1250 | Ecoflo |  | Pump | Distribution Box | Aggregate Trench | None | [21 empty] | [Comments]: Ecoflo In Broken and leaking. Peat needs to be changed. System appears to be operating. Ecoflo needs to be replaced. Lab results not reported by Operator, EHS chose "No" in order to allow saving updated entry. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 01/24/2020 | Jan 1 1900 10:20AM
09/09/2020 |  | Follow-Up | SD-09-107 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Wastemaster Inc |  | Timothy | Jenkins | 2.000000 |  | ATU | Sequencing Bat Reactor | Pump | Gravity | Discharge | UV |  | [] | [] |  | Musty | Clear | 6.400000 | [6 empty] | 1.800000 |  | 140.000000 | 9.200000 |  |  | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 10/09/2020 | 12:30 PM
06/26/2020 |  | RoutineScheduled | 177-07-0034-SP | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Dispersal System Operation" ,"Effluent Screens" ,"Recirculation Pump" ,"Attached Growth Medium"] | ["Dispersal System Operation" ,"Effluent Screens" ,"Attached Growth Medium"] | YES | [15 empty] | Will be sent separately | Inspected | Alarm call by owner - performed annual inpsection as well. We recommend removing the small trees growing at the end of the drainfiled lines. We recommend maintaining this area in a mowed condition. | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 |  | 04/09/2021 | 03:25 PM
06/29/2020 | Alternative | Reportable Incident | 157-13-0094 | Mathews | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | Serviced system. Checked the pump, panel, & floats (ok). Cleaned the filter and cleaned the diffuser in the Clearstream. Changed filter in the aerator. Installed a re-build kit on the aerator. The septic tank needs pumping and pump the trash from the bottom of the Clearstream when doing so. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 06/29/2020 | 12:00 PM
03/02/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Biomicrobics MicroFAST |  |  |  |  | None |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] |  | Good | Clear | [15 empty] | [Comments]: Pump 1 Amps 10.92 ETM 20h 36m Cycles 396Pump 2 Amps 10.65Septic Sludge 6" Scum 6"ATU Sludge 5" Scum 0Pump Sludge 0 Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/02/2020 | Jan 1 1900 10:40AM
02/13/2020 |  | Routine, Scheduled |  | Prince William County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Biomicrobics MicroFAST |  | Pump |  |  | None |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] |  | Good | Good | [15 empty] | [Comments]: Pump Amps 10.20 ETM 37h 16m Cycles 833Septic Sludge 6" Scum 1"ATU Sludge 10" Scum 1"Pump Sludge 0.25 Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/13/2020 | 10:47 AM
03/11/2020 |  | Routine, Scheduled | 182-16-0242 | Rockingham County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Central Shenandoah |  |  |  |  | 1.000000 |  |  | Orenco Advantex | Pump | Manifold | Drip Tubing | None |  | ["Auxiliary Filter","Recirculation Pump","Septic Tank Baffles"] | ["Auxiliary Filter","Recirculation Pump","Septic Tank Baffles"] | [18 empty] | [Comments]: recirc pump screen clogged with hair. Excessive hair in baffle filter | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/16/2020 | 30-12-1899 01:29 PM
08/24/2020 |  | Routine, Scheduled | -STS-20143 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | EZ Treat Sandfilter |  | Pump | Drip | Drip Tubing | UV Light |  | ["Disinfection"] | ["Disinfection"] | [8 empty] | 08/24/2020 | Pump tank | 28.000000 |  | 137.000000 | [5 empty] | Spin filter cleaned. Pump Amps 9.87 ETM 124 hrs Cycles 936 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 08/24/2020 | 11:45 AM
05/26/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Norweco panel is malfunctioning. Repairs to be made. | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 |  | 05/27/2021 | 01:26 PM
05/26/2020 |  | RoutineScheduled | 15-103-0077 | Amelia | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Piedmont | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Advantex AX20 |  | Pump | Gravity |  | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [16 empty] | Inspected | Sludge level-Minimal scum-6" sludge in Septic zone of tank - Recirculation zone 10" sludge - Cleaned Biofilter (a bit dirty), Brushed and flushed manifold, cleaned rsv, sprayed off media, tested float switches, flushed system. Ran in test mode, Alarm functional. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 07/26/2021 | Jan 1 1900 9:30AM
07/27/2020 | Alternative | Routine/Scheduled | 136-05-818 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | None | None | Pump | Distribution Box | Aggregate Trench | None | 450.000000 |  | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | [17 empty] | Real estate transfer inspection Real Estate Inspection - septic pumped for inspection. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 07/28/2020 | 08:15 AM
11/24/2020 |  | RoutineScheduled | SD-05-543 | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Brown's Septic Inspections LLC |  | Jason | Brown | 3.000000 | 2000 gal | Septic | Multi-Flo | Gravity | Pressure | Drip | Not Applicable |  | [] | [] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 11/29/2020 | 07:40 AM
05/07/2020 |  | RoutineScheduled | 69150230 | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Greenway Engineering | 1942001008 | Jeremy | Ferguson | 1.000000 | 1500 | Microfast | none | Pump | Pressure | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation","Control Operation","SludgeScum Accumulation","Level Sensor Operation"] | ["BlowerCompressorAerator Operation","Control Operation","SludgeScum Accumulation","Level Sensor Operation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 07/21/2020 | 09:40 AM
03/19/2020 |  | Routine, Scheduled |  | Prince William County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Prince William | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Delta Environmental Products, DF Series | None | Pump |  | Spray Irrigation |  |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/06/2020 | 02:46 PM
01/06/2020 |  | Routine, Scheduled | {FIPSCode}-STS-2437 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesapeake | R & K Septic, Inc. |  | John | Butt, Jr |  |  | Puraflo |  | Pump |  |  | None |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] |  |  |  | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/06/2020 | Jan 1 1900 7:30AM
08/25/2020 |  | Routine/Scheduled | 14-160-0108 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Biomicrobics MicroFAST |  | Pump | Drip | Drip Tubing | None | 258.000000 | ["None"] | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 08/25/2020 | 04:00 PM
08/26/2020 |  | RoutineScheduled | 06-197-A6 | Wise | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | JET |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
05/12/2020 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Aquarobic Services | 1934000142 | Michael | Blake |  |  | none | none | Pump | Gravity | Mound | Not Applicable |  | ["Level Sensor Operation" ,"Auxiliary Filter"] | ["Level Sensor Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | Routine inspection. Air pre-filter cleaned as maintenance. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 07/01/2022 | 10:30 AM
07/27/2020 |  |  | 069050422 | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 2705110225 | Larry | Royston | [9 empty] | ["None"] | ["None"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 07/28/2020 | 12:00 AM
01/23/2020 |  | Routine, Scheduled |  | Prince William County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Prince William | KLEINDL, JAMES LEE | 1942001380 | JAMES LEE | KLEINDL | 1.000000 | 1500 | Biomicrobics MicroFAST | Septic Tank Only | Pump | Drip | Drip Tubing | None |  |  | ["Auxiliary Filter"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/03/2020 | 06:36 PM
10/27/2020 |  | Routine/Scheduled |  | Frederick | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Review | EHD - Lord Fairfax | POWELLS PLUMBING, INC. | 1942001036 | Kurt | Holthaus | 1.000000 | 1000 | Norweco Singulair ATU |  | Pump | Drip | Drip Tubing |  | 600.000000 | ["Attached Growth Medium","Blower/Compressor/Aerator Operation","Effluent Screens","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Effluent Screens"] | N/A | [17 empty] | Annual Inspection - Pump chamber needs to be pumped, drainfield needs mowed and repair cleanout. Serviced aerator and effluent screen(s). | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. |  | 11/18/2020 | 10:26 AM
08/11/2020 | Alternative | Initial Visit | 073-STS-94586 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | Advanced Septic | None | Pump | Manifold | Elevated Sand Mound | None | 450.000000 |  | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | [17 empty] | STE Elevated Mound Septic tank below normal level - needs further evaluation. Pump tank being manually pumped by property owner - Float sensor weight has fallen off, causing float sensor to fail to activate. Replaced weight and returned system to normal operation. NOTE - No known service for last 5 years as reported by property owner - has several "leaks" found at primary septic tank and pump tank that need to be addressed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 08/12/2020 | 10:30 AM
04/04/2020 |  | Routine, Scheduled | 177-06-0306-SWP | Spotsylvania County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | JENKINS, TIMOTHY R | 1942001062 | TIMOTHY | JENKINS | 1.000000 |  | Aero-flo ATU | None | Pump | None | Alternative Discharge | UV Light |  | ["None"] | ["None"] |  | Musty | Clear | 7.200000 | 6.200000 | 7.800000 |  |  | 04/04/2020 | Effluent | 4.000000 |  | 0.000000 | 7.800000 | 0.000000 | 0.000000 | Will be sent separately |  | [Lab Comments]: Functioning as Designed [Comments]: Functioning as Designed | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/20/2020 | 12:10 PM
10/09/2020 |  | Routine, Scheduled | 175-03-0596 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Aquarobic Mini Plant |  |  | Manifold | Elevated Sand Mound | None |  | ["Blower/Compressor/Aerator Operation"] | ["Blower/Compressor/Aerator Operation"] |  | Acceptable | Tan | [15 empty] | Pump Amps 6.72 Blower Amps 2.69 Septic Sludge 1" Scum 0 On 20 mins Off 23 hrs 40 mins | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 10/09/2020 | 10:50 AM
07/30/2020 |  | Routine/Scheduled |  | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump | Distribution Box |  | None |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  | 1.94 | 7.750000 | 3.500000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 07/30/2020 | Jan 1 1900 3:00PM
07/27/2020 |  | RoutineScheduled | 101-13-0334 | Albemarle | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Blue Ridge | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 2.000000 |  | Ecoflo | none | Pump | Gravity | Drip | Not Applicable |  | ["Level Sensor Operation" ,"Control Operation" ,"Auxiliary Filter"] | ["Level Sensor Operation" ,"Control Operation" ,"Auxiliary Filter"] | NA | [7 empty] | 07/27/2020 | [7 empty] | Will be sent separately | Inspected | Control panel alarmed after new owners shocked the well. Panel still showing a high level status a week later. Splice box in tank was full of water and causing a false high level alarm. Suctioned out splice box, replaced wire nuts for all float switches, and retested. R.O. float switch was stuck on, replaced it. Collected effluent sample for BOD test. Treatment looks good in Microfast unit, but a fungus may be beginning to grow. Recommend Microfast tank be pumped out ASAP. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
10/23/2020 |  | Initial Visit | 199-09-0066 | James City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Peninsula | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | Clearstream |  | Pump | Distribution Box | Aggregate Trench | None | 450.000000 |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | Musty | Clear | [15 empty] | Initial Visit Primary Septic tank - leaking riser - normal operating level. Aeration Tank - normal operating level - HLA inoperable - compressor serviced. Pump Tank - riser below grade! - normal operating level - HLA inoperable - pump, ON/OFF float sensor operational, controls operational. Distribution Box - normal operating level - heavy root intrusion present - removed - all laterals accepting effluent. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 10/26/2020 | Jan 1 1900 7:45AM
03/02/2020 |  | Routine, Scheduled | 177-11-0235-SWP | Spotsylvania County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001350 | Mike | Cook | 1.000000 |  | None | None | Pump |  |  |  |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | [Comments]: Pump tank needs pumped ASAP | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/18/2020 | 06:42 AM
08/25/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/27/2021 | 01:26 PM
04/06/2020 |  | RoutineScheduled | 18-142-0215 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | [11 empty] | NA | [17 empty] | At the time of maintenance, the service expert reported tat all components were functioning properly and the system was operational. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 04/06/2020 | Jan 1 1900 10:47AM
04/02/2020 |  | RoutineScheduled | 107-06-0875 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Onsite Wastewater Services - May Supply | 1942001022 | Sara | Tusing | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 05/28/2021 | 05:41 AM
04/24/2020 |  | RoutineScheduled |  | Fairfax | This AOSS is functioning as designed and in accord | Approved | EHD - Fairfax | ESS | 19420001050 | Troy | Jenkins | 2.000000 |  |  | Septic Tank Only | None | Drip | Drip Tubing | None | 281.000000 | [] | [] |  |  |  | 6.510000 |  |  |  |  | 04/24/2020 | Pump Chamber | 5.000000 |  |  | 8.000000 | 28.100000 |  | Attached to this report |  |  | This AOSS is functioning as designed and in accord |  | 05/13/2020 | Jan 1 1900 12:18PM
12/11/2020 |  | Follow-Up | SWP-04-472 | Stafford | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Resealed both concrete risers on tanks. Installed riser on septic tank inlet to make water tight and provide access for future maintenance. Sealed wedge lid on pump tank. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
08/14/2020 |  | RoutineScheduled | 12-100-0389 | Accomack | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Bundick Well & Pump | 1942001051 | Peter | Duer | 1.000000 | 1250 | Septic Tank | Puraflo | Pump | Pressure | Pad | Not Applicable | 300.000000 | ["None"] | ["None"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 08/18/2020 | 12:40 PM
10/20/2020 |  | RoutineScheduled |  | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 2705051738 | Joshua | Hott | 1.000000 | 1500 | Septic Tank | Puraflo | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
06/09/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | SES MidAtlantic LLC | 1942001203 | James | Green | 1.000000 |  | EcoPod | none | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/15/2021 | 09:00 AM
02/04/2020 |  | Routine, Scheduled | 177-15-0207 | Spotsylvania County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001350 | Mike | Cook |  |  | Orenco Advantex | None | Pump | Drip | Drip Tubing | UV Light |  | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/25/2020 | 07:16 AM
06/02/2020 |  | RoutineScheduled | 108-10-0010 | Bath | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Central Shenandoah | Onsite Wastewater Services - May Supply | 1942001627 | Drew | Shull | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/28/2021 | 05:41 AM
06/03/2020 |  | Routine, Scheduled | 175-17-0410 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Biomicrobics Retrofast |  | Pump | Drip | Drip Tubing | UV Light |  | ["Blower/Compressor/Aerator Operation","Disinfection"] | ["Blower/Compressor/Aerator Operation","Disinfection"] |  | Good | Clear | [15 empty] | Spin filter cleaned. Pump Amps 10.2 Amps ETM 364 hrs Cycles 2555 Water Meter Reading 008545 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 06/03/2020 | 03:46 PM
05/28/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Payment | EHD - Loudoun | Great Falls Septic Service, Inc | 1942001301 | Josh | Hott | 1.000000 |  | none | none | Gravity | Pressure | Pad | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/27/2021 | 11:51 AM
10/17/2020 |  | RoutineScheduled | SD-02-374 | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Wastemaster Inc |  | Timothy | Jenkins | 2.000000 |  | ATU |  |  | Gravity | Discharge | Chlorination |  | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 10:05 AM
03/06/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green |  |  |  |  | Pump | Manifold | Aggregate Trench | None |  | ["Effluent Screens"] | ["Effluent Screens"] | [18 empty] | [Comments]: Pump 1 Amps 18.00 Pump 2 Amps 15.43Septic Sludge 5" Scum 1"Pump Sludge 2" Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/06/2020 | Jan 1 1900 2:44PM
07/29/2020 |  | RoutineScheduled |  | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - New River | MONTGOMERY SANITATION |  | Tim | Conner | 2.000000 | Christiansburg |  |  | Pump | Pressure | Trenches | Not Applicable |  | ["on"] | ["on"] | YES | Musty | Clear | [5 empty] | 08/14/2020 | Sample Chamber | [6 empty] | Attached to this report | Inspected | EVERYTHING FUNCTIONING PROPERLY AT THIS TIME. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 08/14/2020 | 12:00 PM
10/02/2020 |  | Routine, Scheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Orenco Advantex |  |  |  |  | None |  | ["Attached Growth Medium","Dispersal System Operation","Recirculation Pump"] | ["Attached Growth Medium","Dispersal System Operation","Recirculation Pump"] |  | Acceptable | Clear | [15 empty] | Pump Amps 11.60/8.74/8.81 Septic Sludge 5" Scum 3" ATU Sludge 4" Scum 0 Pump Sludge 0 Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 10/02/2020 | Jan 1 1900 11:39AM
03/03/2020 |  | Routine, Scheduled |  | Louisa County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Blue Ridge | Ware, Michele P | 1942001165 | Michele | Ware |  |  | Septic Tank Only | Septic Tank Only | None | None | None | None |  |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/11/2020 | 02:29 PM
11/21/2020 |  | RoutineScheduled | 175-13-0175 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Wastemaster Inc |  | Timothy | Jenkins | 2.000000 |  | EZ Treat |  | Pump | Gravity | Discharge | UV |  | [] | [] |  | Musty | Clear | 7.400000 | 7.100000 |  |  |  | 11/21/2020 |  | 3.000000 |  | 0.800000 | 3.100000 |  |  | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12/09/2020 | 01:35 PM
08/22/2020 |  | RoutineScheduled | C-122-15-0004 | Craig | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Alleghany-Roanoke | King's Alternative Septic | 1942001094 | David | King | 2.000000 | 1500 | Biomicrobics Microfast 00.5 |  | Pump | Pressure | Drip | Not Applicable | 100.000000 | ["Effluent Screens"] | ["Effluent Screens"] | YES | [17 empty] | Cleaned Effluent Screens; system is working correctly | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 10/26/2020 | 12:00 AM
03/11/2020 |  | Routine, Scheduled | 033-06-0020-SP | Caroline County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Ware, Michele P | 1942001165 | Michele | Ware |  |  | Septic Tank Only | Septic Tank Only | None | None | None | None |  |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/12/2020 | 12:13 PM
03/02/2020 |  | Routine, Scheduled | {FIPSCode}-STS-4588 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesapeake | R & K Septic, Inc. |  | Robbie | Van Holten |  |  | Hoot |  | Pump | Drip | Elevated Sand Mound | UV Light |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] |  |  |  | 7.000000 | 5.000000 | [13 empty] | [Comments]: Replaced UV Bulb | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/02/2020 | Jan 1 1900 10:30AM
09/02/2020 |  | RoutineScheduled |  | Warren | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Dispersal System Operation" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"Dispersal System Operation" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [7 empty] | 09/02/2020 |  | 2.000000 | [5 empty] | Will be sent separately | Inspected | Lab Sample Normal Adjusted return line psi to proper setting Recommend french drain to keep groundwater from drainfield | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/26/2021 | 09:04 AM
07/01/2020 |  | Routine/Scheduled | 800-03-0514 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Western Tidewater | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | PremierTech, EFX |  | Pump | Distribution Box | Aggregate Trench | None | 450.000000 | ["Attached Growth Medium"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | [17 empty] | Inspection conducted for real estate transfer - last documented service by this company occurred 2014. Primary septic tank serviced - effluent screen serviced. Peatmoss Biofilter media serviced - reported in good condition. EcoFlo module reported to be fractured - needs to be assessed whether it can be repaired or requires replacment. System is functional. Discharge pump basin intact - pump, float sensors and control panel functioning as designed. 07/27/2020 - peatmoss biofilter media replacement conducted. Technicians noted addition fractures found in treatment module below media ... processing tank will require replacement in future as fractures are not repairable. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 07/28/2020 | Jan 1 1900 8:30AM
06/12/2020 |  | RoutineScheduled | 15-120-0355AR | Chesterfield | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Chesterfield | Stamie E. Lyttle Co. | 1942001470 | Eric | Tambourine | [9 empty] | [] | [] | [19 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 06/12/2020 | 12:00 AM
02/20/2020 |  | Follow-Up | SWP-04-220 | Spotsylvania County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart |  |  | Orenco Advantex | None | Pump | Distribution Box | [23 empty] | [Comments]: Resealed both Advantex risers, repaired broken recirc pump line. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/25/2020 | 07:16 AM
06/05/2020 |  | RoutineScheduled | SP-05-117 | Stafford | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Best 1 | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | YES | [15 empty] | Will be sent separately | Inspected | Zoeller N98 went bad while testing, replaced effluent pump (Barnes SP50), pump out needed 1st compartment, 3rd compartment septic tank and pump tank. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
07/15/2020 | Alternative |  | 166-09-270 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers |  |  | joel | pinnix | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
04/01/2020 |  | Reportable Incident | 05-183-070 | Russell |  |  | EHD - Cumberland Plateau | SEPTIC, Inc. |  |  |  | 1.000000 | 1000 |  |  | Gravity | Gravity | Absorption Field |  | 75.000000 | [19 empty] | Pumped Out |  |  |  |  | 12:00 AM
06/26/2020 |  | Reportable Incident | 09-120-0116 | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesterfield | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | Hoot |  | Pump | Distribution Box | Aggregate Trench | None | 600.000000 |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | [17 empty] | Repairs / upgrades conducted ... new risers installed on aeration and discharge side of treatment system to correct groundwater leakage issue. New HiBlow compressor installed and elevated off ground, all connections verified. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 06/29/2020 | Jan 1 1900 7:30AM
01/08/2020 |  | Follow-Up |  | Prince William County | This AOSS should now return to normal function after having provided the above stated routine maintenance. | Paid | EHD - Prince William | SEAMON, CHARLIE L | 1942001108 | CHARLIE | SEAMON |  |  | Septic Tank Only | Puraflo | Gravity | None | Alternative Discharge | UV Light | [6 empty] | 6.200000 | [6 empty] | 25.000000 |  |  | 8.000000 |  |  | Attached to this report |  | [Lab Comments]: E.coli >2420 [Comments]: Results of Samples and sign at discharge point installed. | This AOSS should now return to normal function after having provided the above stated routine maintenance. |  | 02/14/2020 | 06:43 AM
06/17/2020 |  | Reportable Incident | 19-137-0056 | Goochland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | Owner called due to the alarm going off. Serviced system. Checked the pump, panel, & floats (ok). Cleaned the filter in the Clearstream and cleaned the UV light bulb. Changed the diffuser in the Clearstream, changed the filter in the aerator, and changed the mesh screen in the spinfilter. The pump tank needs to be pumped and cleaned out. Need to get the plans for the timer settings. The timer was set at 3.75 minutes every 6 hours changed it to 8 minutes every 2 hours. The drainfield had wetness - has been raining - but looked good. Did not take initial samples. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 06/17/2020 | Jan 1 1900 12:00PM
10/26/2020 | Alternative | Routine/Scheduled | 04-112-122 | Brunswick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Southside | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. |  |  | Orenco Advantex |  | Pump |  |  |  |  | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump","Sludge/Scum Accumulation"] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump","Sludge/Scum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 10/26/2020 | 10:00 AM
03/17/2020 |  | Reportable Incident | 179-17-0167-SP | Stafford County | This AOSS should now return to normal function after having provided the above stated routine maintenance. | Approved | EHD - Rappahannock | SES Mid Atlantic | 1942001203 | Michael | Green | [9 empty] | ["Level Sensor Operation"] | ["Level Sensor Operation"] | [18 empty] | [Comments]: Installed new alarm float. | This AOSS should now return to normal function after having provided the above stated routine maintenance. |  | 03/17/2020 | 04:00 PM
04/14/2020 |  | Routine, Scheduled |  | Albemarle County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Blue Ridge | CLARK, MICHAEL J | 1934000023 | MICHAEL | CLARK |  |  | Septic Tank Only | Septic Tank Only | None | None | None | None |  |  | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/19/2020 | 04:16 AM
09/15/2020 |  | Routine/Scheduled | 2009-143-0132 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Old Dominion Onsite, Inc. | 1942001503 | Jason | Hackler | 1.000000 | 1500 | Hoot |  | Pump | Drip | Drip Tubing | None |  | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Level Sensor (Float) Operation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Level Sensor (Float) Operation"] | N/A | [17 empty] | Air filter cleaned. System appears to be operating normally. Need dirt over the manifold and valve boxes raised. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 09/15/2020 | 12:39 PM
10/28/2020 |  | RoutineScheduled | 047-STS-21307 | Culpeper | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | ["BlowerCompressorAerator Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation"] | NA | [7 empty] | 10/28/2020 | [7 empty] | Will be sent separately | Inspected | 6-month inspection and first BOD sample. Cleaned air filter. Infiltration observed at riser joint on atu tank. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
04/23/2020 | Alternative | Reportable Incident | 119-STS-93371 | Middlesex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | None | None | Gravity | Distribution Box | Aggregate Trench | None | 450.000000 |  | ["Dispersal System Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | Strong | [16 empty] | Existing system is a COSS gravity to distribution box and absorption field. Have permit proposal issued to local HD to add a STEP collection tank to pump "In-Law" suite to existing distribution box, with conditional use of reduced occupancy. Note - existing absorption field located under a building addition. Unknown if appropriate inspection / permits obtained. Absorption field inspected and powerwashed and appears to be functioning as designed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/23/2020 | 04:00 PM
03/27/2020 |  | Routine, Scheduled |  | Loudoun County | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Paid | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | None | Pump | Distribution Box | Aggregate Trench | [22 empty] | [Comments]: pod 3 and 6 are full of water and peat fiber in the rest of pods appears bad. a bod/tss sample was taken waiting for results | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 04/12/2020 | 02:21 PM
09/03/2020 |  | RoutineScheduled | 177-11-0231-SR | Spotsylvania | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | UV |  | ["Auxiliary Filter" ,"Control Operation" ,"Disinfection" ,"Level Sensor Operation" ,"Recirculation Pump"] | ["Control Operation" ,"Disinfection" ,"Auxiliary Filter" ,"Level Sensor Operation" ,"Recirculation Pump"] | NA | [15 empty] | Will be sent separately | Inspected | Routine inspection. Rinsed uv housing, cleaned sleeve and replaced uv lamp. Cleaned recirc pump intake. Measured 38 psi on return line during test cycle. In the past 30 days, system averaged 6.4 discharge cycles/ day at 8.6 minutes each. Recirc pump still in override mode at departure. Septic tank will probably need pumping by next year's inspection. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
10/29/2020 |  | RoutineScheduled | 107-03-0163 (LEGACY ALT. SYSTEM) | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Onsite Wastewater Services - May Supply | 1942001627 | Drew | Shull | 2.000000 |  | Biomicrobics MicroFAST | none | Pump | Pressure | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 05/28/2021 | 05:41 AM
08/20/2020 |  | RoutineScheduled | 2016-143-0245 | Henrico | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Henrico | Stamie E. Lyttle Co. | 1942001470 | Eric | Tambourine | [9 empty] | [] | [] | [19 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. |  |  | 12:00 AM
05/13/2020 |  | RoutineScheduled | 187090016 | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Greenway Engineering | 1942001008 | Jeremy | Ferguson | 1.000000 | 1500 | Advantex | none | Pump | Pressure | Drip | Not Applicable |  | ["Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 07/22/2020 | 09:15 AM
04/04/2020 |  | Routine, Scheduled | -STS-92277 | Spotsylvania County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | JENKINS, TIMOTHY R | 1942001062 | TIMOTHY | JENKINS | 1.000000 |  | Aero-flo ATU | Septic Tank Only | Pump | None | Alternative Discharge | UV Light |  | ["None"] | ["None"] |  | Musty | Clear | 6.800000 | 5.300000 |  |  |  | 04/04/2020 | Effluent | 4.000000 |  | 0.000000 | 3.000000 |  |  | Will be sent separately |  | [Lab Comments]: Functioning as Designed [Comments]: Functioning as Designed | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/20/2020 | 12:24 PM
10/21/2020 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Gravity | Gravity |  | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Septic inspection on a conventional pump system. The state requires that all conventional septic tank must be pumped out EVERY 5 years and filed with the state and county. The septic control panel is an exterior demand dose. There are 2 pvc cleanouts near the house. The sewer line was camera snaked and was clear. The septic tank has a plastic riser . The septic tank was pumped out and the filter was cleaned. The filter manufacture recommends that the filter be cleaned every 6 months. The pump tank, pump, floats and force main were inspected. The 9 port plastic splitter and both 9 port plastic d-boxes were dug up they were 12" under the ground. All header lines were camera snaked and were clear. the drain field was probed and dry. At time of inspection the septic system was in working condition. | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 |  | 04/14/2021 | 04:27 PM
06/03/2020 |  | RoutineScheduled | 04-118-0080 | Charles City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | GeoEnvironmental Services, Inc. | 1942001010 | Peter | Mamunes | 1.000000 | 1500 | Orenco Advantex |  | Pump | Pressure | Trenches | Not Applicable | 450.000000 | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 06/18/2020 | Jan 1 1900 3:45PM
07/29/2020 | Alternative | Routine/Scheduled | 157-15-0031 | Mathews | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Sludge/Scum Accumulation"] | N/A | [17 empty] | Serviced system. Checked the pump, panel, & floats (ok). Cleaned the filter and the diffuser in the Clearstream. Changed the filter in the aerator. Replaced the UV light bulb. Replaced the buzzer. The septic tank should be pumped out and the Clearstream needs pumping as well. The septic needs additional risers on it to be properly inspected in the future. The timer is set to 2 minutes every 3 hours. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 07/29/2020 | 12:00 PM
06/08/2020 |  | RoutineScheduled |  | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | [9 empty] | ["Dispersal System Operation"] | ["Dispersal System Operation"] | [18 empty] | Septic tank had 4" sludge and 3" scum Filters in head works box were clogged. Cleaned filters and tested system Registers in control panel were Peak- 1128 H/L-55 W/M- 1112362 | This AOSS should now return to normal function after having provided the above state routine maintenance. |  |  | 12:00 AM
08/26/2020 |  | Follow-Up | 175-06-0625 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Prince William | Wastemaster Inc |  | Timothy | Jenkins | 2.000000 |  |  |  | Pump | Pressure | Drip |  |  | [] | ["Distribution Pump Operation"] | [18 empty] | In to replace pump. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 09/15/2020 | 02:05 PM
01/10/2020 |  | Routine, Scheduled |  | Warren County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Lord Fairfax | EDMONSON, MICHAEL W | 1942001541 | MICHAEL | EDMONSON | 1.000000 | 1000 | Puraflo | Septic Tank Only | Pump | Distribution Box | Aggregate Trench | None | 200.000000 | ["None"] | ["None"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/19/2020 | 12:23 PM
12/21/2020 |  | RoutineScheduled |  | Augusta | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity |  | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Distribution Pump Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Distribution Pump Operation"] | NO | [15 empty] | Will be sent separately | Inspected | Repaired pump electrical Installed riser on septic tank | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance |  | 04/26/2021 | 09:04 AM
02/10/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Fairfax | Hott, Joshua D. | 1942001301 | Joshua | Hott |  |  | Septic Tank Only | Septic Tank Only | None | None | None | None |  | ["Level Sensor Operation"] | ["Level Sensor Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/25/2020 | Jan 1 1900 3:52PM
03/06/2020 |  | Follow-Up |  | Manassas | This AOSS should now return to normal function after having provided the above stated routine maintenance. | Paid | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green | [9 empty] | ["Dispersal System Operation"] | ["Dispersal System Operation"] | [18 empty] | [Comments]: Installed new spin filter assembly. | This AOSS should now return to normal function after having provided the above stated routine maintenance. |  | 03/06/2020 | 02:00 PM
04/14/2020 |  | Routine, Scheduled | 2007-143-0121 | Henrico County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Henrico |  |  |  |  | 1.000000 |  |  | Ecoflo | Pump | Distribution Box | Aggregate Bed |  |  | ["Attached Growth Medium","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [18 empty] | [Comments]: Peat was really wet in both pods. Augered peat and is draining now. Peat will need to be replaced by next year. Proposal to be sent to homeowner. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/27/2020 | 04:14 AM
06/02/2020 |  | Routine/Scheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | POWELLS PLUMBING, INC. | 1942001036 | Kurt | Holthaus | 1.000000 | 1000 | Puraflo |  | Pump | Distribution Box | Aggregate Trench |  | 450.000000 | ["Effluent Screens"] | ["Effluent Screens"] | N/A | [17 empty] | Annual Inspection - Serviced effluent screen(s). | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 06/16/2020 | 01:04 PM
04/01/2020 |  | Routine, Scheduled | 15-165-0017 | Northampton County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Eastern Shore | DUER, PETE C | 1942001051 | PETE | DUER | 2.000000 | 3000 | Septic Tank Only | EZ Treat Sandfilter | Pump | None | None | None |  | ["None"] | ["None"] | [18 empty] | [Comments]: AOSS Inspection. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/02/2020 | 12:57 PM
08/12/2020 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Payment | EHD - Fairfax | FIVE STAR SEPTIC INC | 1944001248 | AARON | GOINS | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
01/27/2020 |  | Routine, Scheduled |  | Northumberland County | This AOSS should now return to normal function after having provided the above stated routine maintenance. | Paid | EHD - Three Rivers | PINNIX, JOEL S | 1934000193 | JOEL | PINNIX |  |  | Septic Tank Only | Septic Tank Only | None | None | None | None | [21 empty] | [Comments]: Alarm due high water - clogged ATU filter. Cleaned filter. | This AOSS should now return to normal function after having provided the above stated routine maintenance. |  | 02/01/2020 | 12:36 PM
04/23/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Alarm is not working | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 |  | 04/14/2021 | 04:27 PM
07/08/2020 |  | RoutineScheduled | 03-165-0033 | Northampton | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Eastern Shore | Bundick Well & Pump | 1942001051 | Peter | Duer | 1.000000 | 1000 | Septic Tank | Purflo | Pump | Pressure | Pad | Not Applicable | 450.000000 | ["None"] | ["None"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 07/15/2020 | 02:30 PM
09/16/2020 |  |  | 2009-143-0101 | Henrico | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Microfast | [6 empty] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation"] | [18 empty] | Installed a charcoal filter 9/29/20 | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 10/01/2020 | 12:00 AM
07/07/2020 |  | RoutineScheduled | SWT-02-1168 | Spotsylvania | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["SludgeScum Accumulation" ,"Attached Growth Medium"] |  | NA | [15 empty] | Will be sent separately | Inspected | We recommend pumping the septic tank, aerobic treatment unit, and pump tank due to scum and solids accumulation. We also recommend replacing the damaged riser lid on the septic tank. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/09/2021 | 03:25 PM
08/17/2020 |  | RoutineScheduled | 182-16-0032 | Rockingham | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Central Shenandoah | Onsite Wastewater Services - May Supply | 1942001022 | Sara | Tusing | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/28/2021 | 05:41 AM
06/12/2020 |  | RoutineScheduled | 12-192-022 | Tazewell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. |  | Denny | Deel |  |  | NORWECO |  | Pump | Gravity | Trenches | Not Applicable | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Effluent Screens","Level Sensor Operation"] | ["Level Sensor Operation","Disinfection","BlowerCompressorAerator Operation","Control Operation","Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
09/12/2020 |  | RoutineScheduled | 109-19-0184 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 2.000000 | 3000 | EcoPod |  | Pump | Gravity | Trenches |  |  | ["None"] | ["None"] | [18 empty] | System is running. Restaurant is not completely rebuilt to date. Limited flow going to system. Cleaned blower filter. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 09/18/2020 | 07:03 PM
09/18/2020 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Gravity | Gravity |  | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | A septic inspection was done on a conventional pump system. The state requires that all conventional septic tanks must be pumped out EVERY 5 years and filed with the state and county. The septic control panel is a exterior demand dose. There is 1 pvc cleanout near the house. The sewer line was camera snaked and was clear. The septic tank has a plastic riser on the inlet side and was pumped out. The pump tank, concrete riser, pump, floats and force main were inspected. The 4 port concrete splitter and both 6 port concrete d-boxes were dug up they were 10"-12" under the ground. All 8 header lines were camera snaked and were clear. The drain field was probed and was dry. At time of inspection all components were in working condition. | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 |  | 04/14/2021 | 04:27 PM
12/28/2020 |  | Routine, Scheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Biomicrobics MicroFAST |  |  |  |  | UV Light |  | ["Blower/Compressor/Aerator Operation"] | ["Blower/Compressor/Aerator Operation"] |  | Acceptable | Clear | [15 empty] | Spin filter cleaned. Pump Amps 7.64 ETM 770 hrs Cycles 3149 Water Meter Reading 2119400 Septic Sludge 6" Scum 8" ATU Sludge 18" Scum 0 Pump Sludge 2" Scum 0 On 15 mins 05 secs Off 2 hrs | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 12/28/2020 | Jan 1 1900 10:06AM
08/14/2020 |  | RoutineScheduled | 07-113-265 | Buchanan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Effluent Screens"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
11/04/2020 |  | RoutineScheduled |  | Shenandoah | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Dispersal System Operation" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"Dispersal System Operation" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [7 empty] | 11/04/2020 |  | 212.000000 | [5 empty] | Will be sent separately | Inspected | Replaced blower Replaced air filters Replaced spin clean filter and spin plate | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance |  | 04/26/2021 | 09:04 AM
07/08/2020 | Alternative | RoutineScheduled | 151-05-509 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Church View Septic Service Inc. | 1942001302 | Charles | Langford | 1.000000 | 1000 | Puraflo |  | Pump | Gravity | Pad | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
05/12/2020 |  | Reportable Incident | 179-06-0461-SWP | Stafford | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Client called with alarm. Replaced ON/OFF float, cleaned dirty filter. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
04/27/2020 |  | RoutineScheduled |  | Fairfax | This AOSS is functioning as designed and in accord | Approved | EHD - Fairfax | J&G Septic |  | James | Kleindl | 2.000000 | 1500 |  |  | pump | pressure | pad | n/a |  | [] | [] |  | None | Clear | [16 empty] | This AOSS is functioning as designed and in accord |  | 05/20/2020 | 12:00 AM
05/11/2020 |  | RoutineScheduled | {FIPSCode}-STS-15876 | Prince William | This AOSS is functioning as designed and in accord | Approved | EHD - Prince William | WasteMaster | 1942-001062 | Tim | Jenkins | 2.000000 |  |  |  | Pump |  | Discharge | Chlorine |  | [] | [] |  | Musty | Clear | 7.600000 |  |  | 1.900000 |  | 05/11/2020 |  | 11.000000 |  |  | 27.000000 |  |  | Will be sent separately |  |  | This AOSS is functioning as designed and in accord |  |  | 12:00 AM
12/10/2020 |  | RoutineScheduled | {FIPSCode}-STS-31763 | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | None | Clear | 7.720000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12/17/2020 | 02:55 PM
09/08/2020 |  | RoutineScheduled | 061-16-468 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
06/10/2020 |  |  | 06-142-0020 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Puraflo | [6 empty] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 09/17/2020 | 12:00 AM
06/30/2020 |  | RoutineScheduled | 069-03-0243 | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Combs Wastewater Management LLC | 1942001353 | Amy | Combs | 2.000000 | 1000 |  |  | Pump | Gravity | Trenches | Not Applicable | 600.000000 | [] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12/28/2020 | 03:00 PM
06/24/2020 |  | Routine/Scheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Loudoun | POWELLS PLUMBING, INC. | 1942001036 | Kurt | Holthaus | 1.000000 | 428 | Clearstream |  | Pump | Drip | Drip Tubing |  | 450.000000 | ["Blower/Compressor/Aerator Operation"] | ["Blower/Compressor/Aerator Operation"] | N/A | [17 empty] | Annual Inspection - Serviced spin filter and blower. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 06/26/2020 | 03:28 PM
05/28/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/27/2021 | 01:26 PM
07/14/2020 |  | Follow-Up | 179-STS-87735 | Stafford | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [9 empty] | 17.000000 | [5 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
05/13/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/27/2021 | 01:26 PM
06/22/2020 |  | RoutineScheduled | 177-06-0198-SP | Spotsylvania | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Control Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | ["Control Operation" ,"Distribution Pump Operation" ,"Attached Growth Medium" ,"Effluent Screens" ,"Level Sensor Operation" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | YES | [15 empty] | Will be sent separately | Inspected | Septic tank needs pumped, lots of grease. Recommend changing toilet paper brand. Infiltration at pump tank and septic tank. Proposal to be sent again to homeowner for repairs. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
11/16/2020 |  | RoutineScheduled | {FIPSCode}-STS-2389 | Frederick | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Norweco Singulair ATU | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Attached Growth Medium" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"Attached Growth Medium" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/26/2021 | 09:04 AM
02/05/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Fairfax | Hott, Joshua D. | 1942001301 | Joshua | Hott | 1.000000 | 1875 | Septic Tank Only | Puraflo | Pump | Distribution Box | Aggregate Trench | None |  | ["None"] | ["None"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/18/2020 | Jan 1 1900 3:29PM
12/03/2020 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 2705051738 | Joshua | Hott | 1.000000 | 2750 | Septic | Puraflo | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
04/09/2020 |  | Routine/Scheduled |  | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Pump | Distribution Box | Aggregate Bed | None |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Recirculation Pump","Sludge/Scum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Recirculation Pump","Sludge/Scum Accumulation"] | N/A |  |  | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/09/2020 | Jan 1 1900 1:00PM
03/13/2020 |  | Routine, Scheduled |  | Prince William County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Orenco Advantex |  |  |  |  | None |  | ["Effluent Screens","Level Sensor Operation"] | ["Effluent Screens"] |  | Good | Good | [15 empty] | [Comments]: Needs float replacement.Pump Amps 11.58 ETM 416687h Cycles 9999999Pump Amps 12,78 ETM 044126h Cycles 11077Septic Sludge 7" Scum 0ATU Sludge 6" Scum 0Pump Sludge 1" Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/13/2020 | 12:23 PM
04/14/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | SES MidAtlantic LLC | 1942001203 | James | Green | 1.000000 |  | EcoPod | none | Gravity | Gravity | Trenches | UV |  | ["BlowerCompressorAerator Operation" ,"Disinfection"] | ["BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. Needs new UV Bulb and test tube. | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 |  | 04/15/2021 | 09:00 AM
05/17/2020 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Eco Virginia | 1942001235 | William | Poindexter | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation" ,"Effluent Screens"] | ["Effluent Screens" ,"Distribution Pump Operation"] | YES | [15 empty] | Will be sent separately | Inspected | Replaced Puraflo dosing pump | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 |  | 06/03/2021 | 05:53 AM
08/05/2020 |  |  | 12-125-066 | Dickenson | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 08/05/2020 |  | 4.610000 |  |  | 1.100000 |  |  | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 08/05/2020 | 12:00 AM
06/09/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Home owner has landscaping around pods and there is no access in or around the pod lids inside landscaped area. Informed home owner if they can walk in and walk around the pods then we are able to inspect. | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 |  | 04/14/2021 | 04:27 PM
11/11/2020 |  |  | {FIPSCode}-STS-8430 | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 2705110225 | Larry | Royston | [9 empty] | ["None"] | ["None"] | YES | [16 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12/05/2020 | 12:00 AM
12/08/2020 |  | RoutineScheduled | 01-192-354 | Tazewell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | CLEARSTREAM |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
04/25/2020 |  |  | 05-192-199 | Tazewell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. |  | Denny | Deel |  |  | WHITEWATER |  | Gravity | Gravity | Discharge | Chlorination |  | ["BlowerCompressorAerator Operation","Disinfection","Control Operation"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
12/02/2020 |  | RoutineScheduled | 061-18-111 | Fauquier | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001068 | David | Stewart |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Attached Growth Medium" ,"Control Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Level Sensor Operation"] | ["Auxiliary Filter" ,"Attached Growth Medium" ,"Control Operation" ,"Dispersal System Operation" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Recirculation Pump"] | YES | [15 empty] | Will be sent separately | Inspected | Replaced ARV box lid. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
01/03/2020 |  | Routine, Scheduled | 136-18-0034 | Gloucester County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers | PINNIX, JOEL S | 1934000193 | JOEL | PINNIX |  |  | Septic Tank Only | Septic Tank Only | None | None | None | None | [22 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/13/2020 | 03:46 PM
07/21/2020 |  | Reportable Incident | 2000-143-0098 | Henrico | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Payment | EHD - Henrico | Stamie E. Lyttle Co. | 1942001470 | Eric | Tambourine | [9 empty] | [] | [] | [19 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 07/21/2020 | 12:00 AM
06/10/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Septic tank needs pumped | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 |  | 04/14/2021 | 04:27 PM
03/20/2020 |  | RoutineScheduled | 69090249 | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Combs Wastewater Management LLC | 1942001353 | Amy | Combs | 3.000000 | 1500 |  |  | Pump | Gravity | Drip |  | 600.000000 | [] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Effluent Screens","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12/28/2020 | 12:00 AM
11/14/2020 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | McKim Construction | 1942001330 | Michelle | McKim | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 11/14/2020 | Jan 1 1900 1:40PM
04/09/2020 |  | Routine, Scheduled | 179-07-0321-SP | Stafford County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Puraflo | None | Pump | Distribution Box | Aggregate Trench |  |  | ["Control Operation","Distribution Pump Operation","Level Sensor Operation"] | ["Control Operation","Distribution Pump Operation","Level Sensor Operation"] | [18 empty] | [Comments]: Pump tank in high level due to corroded check valve and cracked pump adapter. Owner unaware because neither alarm was working (both breakers tripped). Found damaged wiring (apparently by insects) in junction box at pump tank. Repaired wiring and tested. Alarm float for outside panel had failed in the "on" position. Replaced both alarm float switches and verified inside and outside alarms working correctly. Replaced brass check valve and pump adapter. Pump rate at 49.1 after repairs. No ponding water in peat, but lots of worms and wet further down. Peat is considered to be in okay condition, reevaluate next year. Lid was not secure on sample box. Replaced top 6" riser that had been damaged by mower. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/27/2020 | 04:14 AM
02/05/2020 |  | Routine, Scheduled | 234-14-381 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesapeake | R & K Septic, Inc. |  | John | Butt, Jr |  |  | Clearstream ATU |  | Pump | Distribution Box |  | None |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] |  |  | 7.19 | 8.240000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/05/2020 | Jan 1 1900 11:00AM
12/02/2020 |  | RoutineScheduled | {FIPSCode}-STS-19857 | Wise | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | JET |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Effluent Screens"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
09/05/2020 |  | Routine, Scheduled | 153-STS-20186 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Puraflo |  |  |  |  | None |  | ["Effluent Screens"] | ["Effluent Screens"] | [18 empty] | Pump Amps 9.80 ETM 380 hrs Cycles 18980 Septic Sludge 10" Scum 0.50 Pump Sludge 1" Scum 0 Puraflo Modules need BOD sampling. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 08/07/2020 | 09:28 AM
09/23/2020 |  | Follow-Up |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Three floats were replaced. The system appears to be functioning as designed at this time. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/27/2021 | 01:26 PM
06/30/2020 |  | RoutineScheduled | 182-99-0112 (LEGACY ALT. SYSTEM) | Rockingham | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Central Shenandoah | Onsite Wastewater Services - May Supply | 1942001022 | Sara | Tusing | 1.000000 |  | none | none | Pump | Gravity |  | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | INSPECTION BY DS | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/28/2021 | 05:41 AM
12/09/2020 |  | RoutineScheduled | 07-118-0042 | Charles City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | GeoEnvironmental Services, Inc. | 1942001010 | Peter | Mamunes | 1.000000 |  | Septic Tank Only |  | Pump | Pressure | Trenches |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["SludgeScum Accumulation","Effluent Screens","Level Sensor Operation","Distribution Pump Operation","Dispersal System Operation","Control Operation","BlowerCompressorAerator Operation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | Jan 1 1900 12:45PM
04/15/2020 | Alternative | Routine/Scheduled | 136-15-0231 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | Serviced system. Checked the pump, panel, & floats (ok). Cleaned the filter and the diffuser in the Clearstream and cleaned the filter in the aerator | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 04/15/2020 | 12:00 PM
04/06/2020 |  | Routine, Scheduled | 175-05-0735 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Biomicrobics MicroFAST |  |  |  |  | None |  | ["Blower/Compressor/Aerator Operation"] | ["Blower/Compressor/Aerator Operation"] |  | Good | Clear | [15 empty] | Spin filter cleaned. Pump Amps 12.54 Water Meter Reading 937830 Septic Sludge 5" Scum 8" ATU Sludge 13" Scum 0 Pump Sludge 8" Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/06/2020 | 03:07 PM
03/25/2020 |  | Routine, Scheduled | 91A03-1-G | Frederick County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Lord Fairfax | PLAUGER, DARRIN F | 1942001173 | DARRIN | PLAUGER |  |  | Orenco Advantex | Septic Tank Only | None | None | None | None |  | ["None"] | ["None"] |  | None | Clear | 7.700000 | [6 empty] | 24.000000 |  |  | 8.300000 |  |  |  |  | [Comments]: System functioning in accordance with regulations. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/25/2020 | 10:54 AM
02/26/2020 |  | Routine, Scheduled | C19-180-0002 | Roanoke County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Alleghany-Roanoke | Conner, Timothy Wayne | 1942001003 | Timothy | Conner | 1.000000 | 1000 | Whitewater ATU | None | Gravity | Distribution Box | Aggregate Trench | None | [19 empty] | Attached to this report |  | [Lab Comments]: NEXT SAMPLE WILL BE DUE 2025. [Comments]: EVERYTHING APPEARS TO BE FUNCTIONING PROPERLY AT THIS TIME. NEXT INSPECTION WILL BE DUE IN 2021. VENIS File Names: tracker sample report 2020.pdf | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/13/2020 | Jan 1 1900 3:44PM
05/13/2020 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 | Pending Payment | EHD - Loudoun | WasteMaster, Inc. | 1942001062 | Tim | Jenkins | 1.000000 |  | Delta Environmental Products, DF Series | Delta Environmental Products, DF Series | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 |  | 06/21/2021 | 10:37 AM
11/03/2020 |  | Routine/Scheduled |  | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Ecoflo |  | Pump |  |  | None |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  |  | 7.680000 | 5.700000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 11/03/2020 | Jan 1 1900 9:15AM
06/25/2020 |  | RoutineScheduled |  | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 2705051738 | Joshua | Hott |  |  |  |  | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
01/14/2020 |  | Routine, Scheduled | 15-142-0040 | Hanover County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chickahominy | SHAW, WILLIAM A, JR. | 1934000449 | WILLIAM | SHAW |  |  | Septic Tank Only | Septic Tank Only | None | None | None | None |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/14/2020 | Jan 1 1900 1:32PM
04/07/2020 |  | RoutineScheduled | VAG401165 | Augusta | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Central Shenandoah | Onsite Wastewater Services - May Supply | 1942001022 | Sara | Tusing | 1.000000 |  | none | none | Gravity | Gravity |  | Chlorination |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 05/28/2021 | 05:41 AM
06/19/2020 |  | RoutineScheduled | 2004-143-0206 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Onsite Maintenance Team | 1942001039 | Corey | Braxton | 3.000000 |  | Best 1 |  | Pump | Gravity | Trenches |  | 200.000000 | [] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation"] | YES | Musty | Clear | 6.100000 | 3.000000 |  |  | turbidity 22 | [11 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 06/19/2020 | 12:00 AM
02/17/2020 |  | Routine, Scheduled | 179-17-0408-SP | Stafford County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | None | Pump | Distribution Box | Aggregate Trench |  |  | ["Attached Growth Medium","None","Recirculation Pump"] | ["Attached Growth Medium","None","Recirculation Pump"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/02/2020 | 11:52 AM
11/21/2020 |  | RoutineScheduled | 2044-02-153 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Wastemaster Inc |  | Timothy | Jenkins | 2.000000 |  | PuraFlo |  | Pump | Gravity | Discharge | Chlorination |  | [] | [] |  | Musty | Clear | 7.300000 |  |  | 2.200000 | [12 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12/09/2020 | 01:25 PM
06/11/2020 |  | RoutineScheduled | 137-STS-25545 | Orange | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Ecoflo | none | Pump | Gravity | Drip | Not Applicable |  | ["SludgeScum Accumulation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Control Operation" ,"Dispersal System Operation" ,"Attached Growth Medium" ,"Auxiliary Filter"] | ["SludgeScum Accumulation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Attached Growth Medium" ,"Auxiliary Filter" ,"Control Operation" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | YES | [15 empty] | Will be sent separately | Inspected | augured peat, replaced ARV box, installed spring check valve on return and installed ball valve & pressure gauge on return. Too much water flowing onto tank to do proper drawdown. Need low flow kit and bleach system. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
12/04/2020 | Alternative | Routine/Scheduled | 151-10-0066 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 2.000000 | 2000 | Ecoflo |  | Pump | None | Aggregate Bed |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12/04/2020 | 05:00 PM
05/29/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim |  |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/14/2021 | 04:27 PM
03/13/2020 |  | Follow-Up | SWP-98-140 | Spotsylvania County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | None | None | Pump |  |  |  |  | ["Dispersal System Operation","Distribution Pump Operation"] | ["Dispersal System Operation","Distribution Pump Operation"] | [18 empty] | [Comments]: Replaced both check valves in dripfield. Only 1 zone pressurized each test cycle. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/16/2020 | 06:19 AM
10/06/2020 |  | RoutineScheduled | 04-197-176 | Wise | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | Advantex |  | Gravity | Gravity | Trenches | Not Applicable | 200.000000 | ["Control Operation","Dispersal System Operation","Level Sensor Operation","Recirculation Pump"] | ["Control Operation","Dispersal System Operation","Level Sensor Operation","Recirculation Pump"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 10/06/2020 | 12:00 AM
01/24/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Fairfax | Creighton, Cameron Ellis | 1942001137 | Cameron | Creighton |  |  | Biomicrobics MicroFAST | None | Pump | Distribution Box | Aggregate Trench | None | [22 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/25/2020 | Jan 1 1900 8:31AM
07/08/2020 |  | RoutineScheduled |  | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 2705051738 | Joshua | Hott |  |  | Septic | Puraflo | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
06/16/2020 |  | Reportable Incident | SD-12-31 | Fauquier | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | On site for low level alarm in discharge tank. Everything working correctly at this time. Return line pressure gauge showing 58 psi while drip cycle in progress. Lowered RO float in drip tank about an inch and shortened the standard run time by 1 minute. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
12/23/2020 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump | Drip | Elevated Sand Mound | UV Light |  | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  |  | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 12/23/2020 | Jan 1 1900 2:00PM
09/23/2020 |  | Routine, Scheduled | 175-14-0372 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Biomicrobics MicroFAST |  |  |  |  | None |  | ["Blower/Compressor/Aerator Operation"] | ["Blower/Compressor/Aerator Operation"] |  | Acceptable | Clear | [15 empty] | Pump Amps 9.03 ETM 47 hrs 9 mins Cycles 1473 Septic Sludge 10" Scum 4" ATU Sludge 6" Scum 0 Pump Sludge 2" Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 09/23/2020 | 09:40 AM
02/12/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS should now return to normal function after having provided the above stated routine maintenance. | Paid | EHD - Fairfax | SEAMON, CHARLIE L | 1942001108 | CHARLIE | SEAMON |  |  | Septic Tank Only | Microfast | Gravity | Distribution Box | Aggregate Trench | None |  | ["BlowerCompressorAerator Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Dispersal System Operation"] | [18 empty] | [Comments]: Performance Inspection: Microfast Gravity to Drainfield. Septic/ATU-9"sludge 3"scum ATU-12"sludge. Recommend pump out in 3 months due to solids. Blower air filter cleaned. Noted drainfield box out of adjustment, top 2 drainfield lines taking more water. Adjusted speed levelers for equal distribution. | This AOSS should now return to normal function after having provided the above stated routine maintenance. |  | 03/05/2020 | Jan 1 1900 6:38AM
01/10/2020 |  | Reportable Incident |  | Warren County | This AOSS should now return to normal function after having provided the above stated routine maintenance. | Paid | EHD - Lord Fairfax | POWELLS PLUMBING, INC. | 1942001036 | Kurt | Holthaus |  |  | Microfast | [6 empty] | ["Control Operation"] | ["Control Operation"] | [18 empty] | [Comments]: Rewired junction box for Microfast blower. | This AOSS should now return to normal function after having provided the above stated routine maintenance. |  | 01/10/2020 | 03:44 PM
01/20/2020 |  | Routine, Scheduled | 42375 | Frederick County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Lord Fairfax | Ferguson, Jeremy | 1942001008 | Jeremy | Ferguson | 1.000000 | 1000 | Puraflo | Septic Tank Only | Pump | Distribution Box | Aggregate Trench | None |  |  | ["Dispersal System Operation","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | [Comments]: System is in compliance with approved plans and health department regulations. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/20/2020 | 02:01 PM
05/07/2020 | Alternative | Routine/Scheduled | 166-14-059 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1250 | Microfast | None | Pump | Distribution Box | Aggregate Trench | None |  |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | The Septic Tank Riser has been sealed with spray foam, and is leaking; the Discharge Tank was found with a crack that runs along the ceiling of the Tank from inlet to outlet side and towards the bottom of the Tank; the Distribution Box has been warped and the Lid no longer seals properly | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 06/26/2020 | 03:30 PM
10/28/2020 |  | RoutineScheduled | SWP-05-46 | Stafford | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Rappahannock | Wastemaster Inc |  | Timothy | Jenkins | 2.000000 |  | Advantex |  | Pump | Pressure | Drip |  |  | [] | [] | [18 empty] | In for service and inspection. Found tank level high. Wiring in junction box under water and burned up Drained water and remade wiring connections but still not working. Circuit board bad. Replaced circuit board. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 11/05/2020 | 11:05 AM
07/27/2020 |  | Follow-Up |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim |  |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Inspected the drain field | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/14/2021 | 04:27 PM
12/08/2020 |  | RoutineScheduled | 099-06-0352-SR | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Wastemaster Inc |  | Timothy | Jenkins | 2.000000 |  | Advantex |  | Pump | Pressure | Drip |  |  | [] | [] | [18 empty] | In for annual inspection and service. Cleaned and tested all operating properly at this time. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12/18/2020 | 11:20 AM
05/19/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | EcoPod | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/27/2021 | 01:26 PM
05/07/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Septic tank is scheduled to be pumped. Recommend pumping scum off ATU surface at the same time. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/27/2021 | 01:26 PM
06/22/2020 |  | RoutineScheduled | 177-11-0030-SR | Spotsylvania | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 2.000000 |  | Orenco Advantex | none | Pump | Gravity | Pad | Not Applicable |  | ["Attached Growth Medium" ,"Control Operation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | ["Control Operation" ,"Dispersal System Operation" ,"Distribution Pump Operation" ,"Attached Growth Medium" ,"Effluent Screens" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | YES | [15 empty] | Will be sent separately | Inspected | Heavy roots at old septic tank. Roots at inlet wedge lid and inlet pipe on new septic tank. Roots at inlet pipe and wedge lid on pump tank. Contact installer to resolve root issue. One of two panel ports are broken. We flushed LPD rate is good. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
07/03/2020 |  | Reportable Incident | SD-00-111 | Fauquier | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Distribution Pump Operation" ,"SludgeScum Accumulation"] | ["Control Operation" ,"Distribution Pump Operation" ,"SludgeScum Accumulation"] | NA | [15 empty] | Will be sent separately | Inspected | 7/2/20 - Pump tank in high level, pump breaker tripped. Reset, pump pulling high amps. Pulled original pump from 03/20. Pump tank cleaned out by Butler & Eicher to facilitate repairs. 7/3/20 - Replaced failed E191 pump with 1/2 hp turbine style pump and cool guide per engineer at American Mfg. New pump running at 4.54 amps. High drip rate on zone 2 (lower). No effluent surfacing. Suspect zone 1 check valve may not be fully closing, but could not verify. Zone 1 was initially not working. Replaced failed solenoid. Peak count at 12579 and high level at 138. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
01/08/2020 |  | Routine, Scheduled |  | Prince William County | This AOSS should now return to normal function after having provided the above stated routine maintenance. | Paid | EHD - Prince William | SEAMON, CHARLIE L | 1942001108 | CHARLIE | SEAMON |  |  | Septic Tank Only | Microfast | Pump | Manifold | Drip Tubing | None |  | ["BlowerCompressorAerator Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation"] | [18 empty] | [Comments]: Performance Inspection: Microfast to Geoflo Drip Septic/ATU-8"sludge 0"scum/ ATU-14"sludge/ Pump Tank-0"sludge. Microfast ATU needs pump out due to sludge level and media clogging. 2 Zone zoner is craced and needs replacement (owner to have repair by others) Recommend insulation of hydraulic unit and zoner housing. Recommend replacement of blower | This AOSS should now return to normal function after having provided the above stated routine maintenance. |  | 01/16/2020 | 06:07 AM
03/06/2020 |  | Routine, Scheduled | 15-100-0313 | Accomack County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Eastern Shore | DUER, PETE C | 1942001051 | PETE | DUER | 1.000000 | 500 | Septic Tank Only | EcoPod | Pump | None | None | None |  | ["None"] | ["None"] | [18 empty] | [Comments]: Aoss Inspection. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/10/2020 | 11:21 AM
12/10/2020 | Alternative | Initial Visit | 157-13-0054 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 |  |  | Pump | Distribution Box | Gravel-Less Bed |  | 450.000000 |  | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | [17 empty] | Eljen Synthetic Sand Filter / Absorption Bed Primary Septic Tank - normal level - effluent screen serviced. Pump Tank - normal level - pump, float sensors & controls operating. Distribution Box intact - no indications of surfacing present. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 12/11/2020 | 07:15 AM
01/19/2020 |  | Routine, Scheduled | 093-05-0217 | Isle of Wight County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Western Tidewater | R & K Septic, Inc. |  | Craig | Van Holten |  |  | Clearstream ATU |  | Pump | Distribution Box |  | None |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/19/2020 | Jan 1 1900 2:00PM
09/02/2020 |  | RoutineScheduled | 175-09-0462 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 | Approved | EHD - Prince William | Ace Contracting Services Inc | 1942001120 | Lawrence | Fellenz Jr. |  |  | Puraflo | none | Gravity | Gravity |  | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 |  | 06/29/2021 | 10:39 PM
08/14/2020 |  | Reportable Incident | 07-103-0173 | Amelia | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Piedmont | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | Owner called due to the alarm going off. Serviced system. Checked the pump, panel, & floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. Installed a re-build kit on the aerator. Hooked up the alarm in the Clearstream - was not hooked up. The timer is set to 1.75 minutes every 2.25 hours. Did not take the initial sample. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 08/14/2020 | Jan 1 1900 12:00PM
01/08/2020 |  | Routine, Scheduled | 179-18-0413-SWP | Stafford County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Orenco Advantex | None | Pump | Distribution Box | Aggregate Trench |  |  | ["Effluent Screens"] | ["Effluent Screens"] | [18 empty] | [Comments]: 90-Day Inspection | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/04/2020 | 07:46 AM
03/18/2020 |  | Routine, Scheduled | SD-14-263 | Fauquier County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Puraflo | None | Pump | Distribution Box | Aggregate Trench |  |  | ["Control Operation","Distribution Pump Operation","Level Sensor Operation"] | ["Control Operation","Distribution Pump Operation","Level Sensor Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/01/2020 | 06:33 AM
04/03/2020 |  | RoutineScheduled | 182-11-0165 | Rockingham | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Central Shenandoah | Onsite Wastewater Services - May Supply | 1942001022 | Sara | Tusing | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Pressure | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/28/2021 | 05:41 AM
02/12/2020 |  | Routine, Scheduled | 179-15-0418-SWP | Stafford County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | None | Pump | Distribution Box | Aggregate Trench |  |  | ["Attached Growth Medium","None","Recirculation Pump"] | ["Attached Growth Medium","None","Recirculation Pump"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/02/2020 | 11:52 AM
05/13/2020 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Eco Virginia | 1942001235 | William | Poindexter | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 |  | 06/03/2021 | 05:53 AM
08/31/2020 |  | RoutineScheduled | SWP-04-260 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Drainfield Solutions | 2705163102 | Michele | Ware | [9 empty] | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","Septic Tank Baffles","SludgeScum Accumulation","Other"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 10/01/2020 | 12:00 AM
04/24/2020 |  | RoutineScheduled | 171-15-249 | Shenandoah | This AOSS should now return to normal function aft | Approved | EHD - Lord Fairfax | Valley Soil & Environmental Consulting, LLC | 1942001218 | John | Lam | 1.000000 | 1000 |  |  | Pump | Gravity | Trenches | N/A |  | ["BlowerCompressorAerator Operation","Distribution Pump Operation"] | ["BlowerCompressorAerator Operation","Distribution Pump Operation"] | NA | Low | [15 empty] | Inspected | Blower: 3.04 amps, pump: 11.57 amps; clean FAST blower housing and filter; pump control panel alarm buzzer not working; diagnosed missing relay; installed correct relay and new alarm buzzer | This AOSS should now return to normal function aft |  | 05/11/2020 | 12:21 PM
09/30/2020 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump | Distribution Box |  | None |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  | 3.76 | 6.170000 | [15 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 09/30/2020 | Jan 1 1900 12:15PM
10/26/2020 |  | RoutineScheduled | 2004-143-0183 | Henrico | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | Advantex |  | Pump | Gravity | Trenches |  |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Recirculation Pump"] | YES | [17 empty] | We replaced the pump on 10/26/2020. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 11/17/2020 | 12:00 AM
11/02/2020 |  | RoutineScheduled |  | Greene | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Payment | EHD - Blue Ridge | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/26/2021 | 09:04 AM
03/26/2020 |  | Routine, Scheduled | 182-11-0262 | Rockingham County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Central Shenandoah | [7 empty] | Septic Tank Only | None | None | None | None | [21 empty] | [Comments]: the system is working properly | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/27/2020 | 30-12-1899 03:47 PM
09/14/2020 |  | Reportable Incident | 136-09-0108 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | Clearstream | None | Pump | Distribution Box | Aggregate Trench | None | 450.000000 | ["Distribution Pump Operation"] |  | N/A | Musty | Clear | [15 empty] | Pumped Pump station for repair. Alarm event - Found discharge pump ME-40 has failed - impellor broken off inside of pump - replaced with new Liberty 280 System pumped during service - requires "other" maintenance as outlined in 05/2020 report. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 09/15/2020 | 01:50 PM
04/20/2020 | Alternative | RoutineScheduled | 115-00-0509 | Campbell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | Acres of Virginia, Inc. | 1942001044 | Melvin | Collins | 1.000000 | 1500 | Septic Tank |  | Pump | Pressure | Trenches | Not Applicable | 450.000000 | ["None"] | ["None"] | YES | [17 empty] | New pump, box now located inside. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 06/24/2020 | 12:20 PM
09/08/2020 |  | Routine/Scheduled | 800-04-0294 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Western Tidewater | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1500 | Orenco Advantex | None | Pump | Distribution Box | Aggregate Trench | None | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | None | Clear | [15 empty] | Minor Repairs Concrete riser on discharge tank removed - new plastic riser & electrical splice box installed. New float sensors and discharge pump installed - plumbing replaced inside of discharge tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 09/09/2020 | Jan 1 1900 7:15AM
06/01/2020 |  | RoutineScheduled | 175-01-0486 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | [9 empty] | ["Dispersal System Operation"] | ["Dispersal System Operation"] | [18 empty] | Septic had 4" sludge and 0" scum ATU had 0" sludge and 0" scum. Pump tank hadn 4"m sludge. Cleaned air filter for blower. Sealed possible leaks in ATU at air line and riser. Repaired broken pipe at zoner. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  |  | 12:00 AM
11/24/2020 | Alternative | Initial Visit | 073-STS-105270 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | None | None | Pump | Distribution Box | Aggregate Trench | None | 450.000000 |  | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | [17 empty] | Initial Visit - COSS Pump to Gravity Primary Septic Tank - normal operating level Pump Tank - normal operating level - pump, float sensors & controls operating properly. Distribution Box - intact - all laterals accepting effluent. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 11/25/2020 | 08:00 AM
05/13/2020 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Aquarobic Services | 1934000142 | Michael | Blake |  |  | none | none | Pump | Gravity | Mound | Not Applicable |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected | Routine inspection. Replaced air filter. Single-point aeration has developed at inlet end of tank - repair is required. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 07/01/2022 | 10:30 AM
10/06/2020 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [11 empty] | N/A | [9 empty] | 25.000000 |  | 4.000000 | [6 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 10/12/2020 | Jan 1 1900 8:30AM
02/21/2020 |  | Routine, Scheduled | 109-11-0147 | Bedford County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Central | WAUGH, IAIN C | 1942001512 | IAIN | WAUGH | 1.000000 | 1000 | Septic Tank Only | Orenco Advantex | Pump | Distribution Box | Aggregate Trench | None |  | ["Effluent Screens"] | ["Effluent Screens"] | [18 empty] | [Comments]: Septic tank 2.5"-scum 8" Sludge Recirc zone 10" Sludge Discharge Zone 12" Sludge Alarm opperational, All floats good both pumps good, ran in test mode cleaned septic filter | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/05/2020 | 08:56 PM
10/13/2020 |  | Reportable Incident | 2014-143-0137 | Henrico | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Henrico | Old Dominion Onsite, Inc. | 1942001549 | Russell | Revis | [9 empty] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump"] | N/A | [17 empty] | Replaced motherboard, installed program ax20b1 and adjusted settings appropriately. Checked pump and float function, cleaned effluent filter, spinners and manifold. Pumped recirc chamber down to operating level. System is now working properly. Settings: Recirc time off 23.9 On 0.8 Override off time 11.8 On 0.8 Discharge demand dose | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 10/13/2020 | 09:33 AM
11/13/2020 |  | RoutineScheduled |  | Rockingham | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | none | none | Pump | Gravity |  | Not Applicable |  | ["Control Operation"] | ["Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Recommend uncovering septic tank and installing risers | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/26/2021 | 09:04 AM
06/25/2020 |  | Routine/Scheduled | 12-120-0305A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. |  |  | Clearstream |  | Pump |  |  |  |  | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | Rebuilt blower | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 06/25/2020 | Jan 1 1900 12:30PM
11/05/2020 |  | Routine/Scheduled | 18-163-0067 | New Kent | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["Control Operation","Distribution Pump Operation","Effluent Screens"] | ["Control Operation","Distribution Pump Operation","Effluent Screens"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 11/05/2020 | Jan 1 1900 12:00PM
12/21/2020 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump | Drip | Elevated Sand Mound | UV Light |  | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 12/21/2020 | Jan 1 1900 10:00AM
04/06/2020 |  | Routine, Scheduled | 175-11-0292 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green | [9 empty] | ["Effluent Screens"] | ["Effluent Screens"] | [18 empty] | Pump 1 Amps 8.30 ETM 94519 Cycles 10067 Septic Sludge 7" Scum 3" Pump Sludge 2" Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/06/2020 | 10:50 AM
12/22/2020 |  | Routine, Scheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | EZ Treat Sandfilter |  |  |  |  | None |  | ["Attached Growth Medium","Effluent Screens","Recirculation Pump"] | ["Attached Growth Medium","Effluent Screens","Recirculation Pump"] | [18 empty] | Pump Amps EZ Treat 6.76 Pump Amps 11.58/10.91 Septic Sludge 12" Scum 0.50 ATU Sludge 4" Scum 0 Pump Sludge 2" Scum 0 Control panel demand. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 12/22/2020 | Jan 1 1900 1:48PM
12/24/2020 | Alternative |  | 151-10-0133 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | obsidian onsite services | 1942001177 | joel | pinnix | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
07/23/2020 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump | Drip | Elevated Sand Mound | UV Light |  | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  |  | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 07/23/2020 | Jan 1 1900 1:30PM
11/27/2020 |  | RoutineScheduled |  | Warren | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Lord Fairfax | Onsite Wastewater Services - May Supply | 1942001627 | Drew | Shull | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | inspection BY ds | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/28/2021 | 05:41 AM
03/27/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Paid | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Delta Environmental Products, DF Series |  |  |  |  | None |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation"] | ["BlowerCompressorAerator Operation","Control Operation"] |  | Good | Clear | [15 empty] | [Comments]: Pressure reducing valves in drainfield needs replacing.Pump 1 Amps 11.2 ETM 2874 h Cycles 24097Pump 2 Amps 10.9Water Meter Reading 390240Septic Sludge 4" Scum 1"ATU Sludge 0 Scum 0.50Pump Sludge 3" Scum 0.50 | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 03/27/2020 | Jan 1 1900 12:37PM
03/04/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Fairfax | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Orenco Advantex | Orenco Advantex | Pump | Distribution Box | Aggregate Trench |  |  | ["Control Operation","Distribution Pump Operation","Level Sensor Operation"] | ["Control Operation","Distribution Pump Operation","Level Sensor Operation"] | [18 empty] | [Comments]: Annual inspection and 5-year BOD sampling. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/06/2020 | Jan 1 1900 5:29AM
02/25/2020 |  | Follow-Up | 099-10-0022-SWP | King George County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001350 | Mike | Cook | 1.000000 |  | Orenco Advantex | None | Pump | Distribution Box | [15 empty] | 87.000000 | [8 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/03/2020 | 11:00 AM
01/21/2020 |  | Routine, Scheduled | 41989 | Frederick County | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Rejected | EHD - Lord Fairfax | Ferguson, Jeremy | 1942001008 | Jeremy | Ferguson | 1.000000 | 1250 | Biomicrobics MicroFAST | Septic Tank Only | Pump | Drip | Drip Tubing | None |  | ["BlowerCompressorAerator Operation","Level Sensor Operation"] | ["Control Operation","SludgeScum Accumulation"] | [18 empty] | [Comments]: The blower line needs repaired and the alarm float is no operational. Also needs pumped out. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 01/22/2020 | 05:17 PM
05/05/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | The septic ATU and pump tank need pumped out. The K-Rain needs replaced broken. | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 |  | 04/14/2021 | 04:27 PM
08/05/2020 |  | Reportable Incident | 179-06-0012-SWP | Stafford | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  | ["SludgeScum Accumulation"] |  | NA | [15 empty] | Will be sent separately | Inspected | High level alarm after heavy rain. Pump tank down to about 3" of effluent because owners had been running pump manually. Groundwater infiltration observed at pump tank midseam in 2 corners, inlet wedge lid, and riser joint. Septic tank also had infiltration at inlet wedge lid and riser joint. Could not confirm if any leaks at pipe penetrations or midseam because tank was full (normal level). Added enough water back to pump tank to test flow rate on pump. Recommend moving swingset off of Puraflo modules so that they can be inspected. Septic tank needs pumped out due to scum and sludge levels. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
11/03/2020 |  | RoutineScheduled | 2090-04-153 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Wastemaster Inc |  | Timothy | Jenkins | 2.000000 |  | PuraFlo |  | Pump | Gravity | Discharge | Chlorination |  | [] | [] |  | Musty | Clear | 7.400000 |  |  | 2.200000 | [12 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 11/20/2020 | 12:10 PM
09/25/2020 |  | Routine, Scheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Puraflo |  |  |  |  | None |  | ["Effluent Screens"] | ["Effluent Screens"] | [18 empty] | Pump 1 Amps 9.29 ETM 90579 Cycles 31193 Pump 2 Amps 9.17 ETM 92255 Cycles 31141 Septic Sludge 12" Scum 0 Pump Sludge 3" Scum 0 Puraflo peat getting low. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 09/25/2020 | Jan 1 1900 12:16PM
11/17/2020 |  | Routine/Scheduled | 08-160-0052 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Delta Environmental Products, DF Series |  | Pump | Drip | Drip Tubing | None | 224.000000 | ["None"] | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 11/17/2020 | 03:30 PM
08/11/2020 |  | RoutineScheduled | SP-02-616 | Stafford | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Ecoflo | none | Pump | Gravity | Pad | Not Applicable |  | ["Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Attached Growth Medium" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Level Sensor Operation"] | ["Attached Growth Medium" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | YES | [15 empty] | Will be sent separately | Inspected | Remote alarm; OK. 6? of ponding water in pod, raked & OK. Peat replacement will be needed next year. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
05/12/2020 |  | RoutineScheduled |  | Warren | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Dispersal System Operation"] | ["Control Operation" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Dispersal System Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced zone valve at time of inspection | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance |  | 04/26/2021 | 09:04 AM
04/23/2020 |  | Routine/Scheduled | {FIPSCode}-STS-11314 | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | Serviced system. Checked the pump, panel, & floats (ok). CLeaned the UV light bulb. Changed the diffuser in the Clearstream, changed the filter, and changed the mesh screen in the spinfilter. The valve boxes need to be raised up and need new tops. The timer is set to 10 minutes every 1 hour. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 04/23/2020 | Jan 1 1900 12:00PM
12/03/2020 |  | Routine/Scheduled |  | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump | Drip | Elevated Sand Mound | UV Light |  | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  |  | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 12/03/2020 | Jan 1 1900 10:30AM
12/21/2020 |  | Reportable Incident | 175-04-0420 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green | [9 empty] | ["Dispersal System Operation"] | ["Dispersal System Operation"] | [18 empty] | Replaced solenoids & cleaned hydraulic unit. | This AOSS should now return to normal function after having provided the above state routine maintenance |  | 12/21/2020 | 04:00 PM
09/08/2020 |  | RoutineScheduled | 69140169 | Frederick | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Rejected | EHD - Lord Fairfax | Greenway Engineering | 1942001008 | Jeremy | Ferguson | 1.000000 | 1000 | Norweco | none | Pump | Pressure | Drip | Not Applicable |  | ["Control Operation","SludgeScum Accumulation","Level Sensor Operation"] | ["Control Operation","SludgeScum Accumulation"] | YES | [17 empty] | Recommended to have septic pumped. Timer enable float needs replaced. Approved once completed. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. |  | 09/09/2020 | 03:40 PM
09/02/2020 |  | Routine/Scheduled | 2014-143-0114 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Old Dominion Onsite, Inc. | 1942001134 | John | Ewing | 1.000000 | 1250 | Clearstream ATU |  | Pump | Manifold | Drip Tubing | None | 150.000000 | ["Blower/Compressor/Aerator Operation","Distribution Pump Operation"] |  | N/A | [17 empty] | Compressor filter was changed. Discharge off time was changed from 4 hours to 8 based on low level of effluent in discharge pump chamber. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 09/02/2020 | 11:14 AM
07/31/2020 | Alternative | RoutineScheduled | {FIPSCode}-STS-54259 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | KC Forge Environmental Service, LLC | 1942001034 | Kent | Cuthbertson | 4.000000 | 10,000 gal |  |  | Pump | Pressure | Drip | Not Applicable | 3938.000000 | ["None"] | ["None"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 09/14/2020 | 07:03 PM
11/02/2020 |  | RoutineScheduled |  | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Great Falls Septic Service, Inc. | 1942001301 | Joshua | Hott | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
10/20/2020 |  | RoutineScheduled | 05-160-0245 | Montgomery | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - New River | King's Alternative Septic | 1942001112 | William | King, II | 2.000000 | 1500 | Biomicrobics Microfast 0.5 |  | Pump | Pressure | Drip | Not Applicable | 250.000000 | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [17 empty] | Replaced spin filter, system is working correctly. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 10/26/2020 | 12:00 AM
09/25/2020 |  | Routine, Scheduled | 175-02-0229 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Orenco Advantex |  |  |  |  | None |  | ["Effluent Screens","Recirculation Pump"] | ["Recirculation Pump"] | [18 empty] | Pump Amps 11.30 ETM 439595 mins Cycles 878824 Pump Amps 10.58 ETM 39345 mins Cycles 9221 Septic Sludge 16" Scum 0 Pump Sludge 2" Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 09/25/2020 | 09:45 AM
07/27/2020 |  | RoutineScheduled | SWP-04-273 | Spotsylvania | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | ["BlowerCompressorAerator Operation" ,"Auxiliary Filter" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/09/2021 | 03:25 PM
10/03/2020 |  | RoutineScheduled | 2060-98-153 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Wastemaster Inc |  | Timothy | Jenkins | 2.000000 |  | Recirculating Sandfilter |  | Pump | Gravity | Discharge | Chlorination |  | [] | [] |  | Musty | Clear | 6.400000 |  |  | 1.300000 | [12 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 10/20/2020 | 09:20 AM
08/14/2020 |  | Initial Visit | 2016-143-0244 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Henrico | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | EZ Treat Sandfilter | None | Pump | Drip | Drip Tubing | None | 600.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | None | Clear | [15 empty] | Initial visit Primary septic tank in higher than normal operating level - probable surface/ground water infiltration. Processing tank in higher than normal operating level - probable surface/ground water infiltration - Recirc Pump serviced. EZ Treat module - Flushed dispersal laterals and media. Pump Tank - water level higher than normal operating level - surface/groundwater infiltration / excessive return from drip field air release vents - discharge pump serviced. float sensors and controls operating properly. Drip Controls - manual headworks - drip screen serviced. Air release vents found below finished grade - flooded due to excessive rains. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 08/17/2020 | 07:15 AM
02/06/2020 |  | Routine, Scheduled |  | Loudoun County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Loudoun | Triple R Construction Co., Inc. | 1934000238 | Charles | Seamon | 1.000000 |  | Biomicrobics MicroFAST | None | Pump | Distribution Box | Aggregate Trench |  |  | ["BlowerCompressorAerator Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation"] | [10 empty] | 15.000000 | [7 empty] | [Comments]: Septic/Microfast needs pump out due to sludge levels and rags in the tank. BOD is15 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/25/2020 | 11:44 AM
08/14/2020 |  | RoutineScheduled | 17-113-088 | Buchanan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Effluent Screens"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Effluent Screens"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
01/21/2020 |  | Routine, Scheduled | 2006-143-0199 | Henrico County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Henrico |  |  |  |  | 1.000000 |  |  | Ecoflo | Pump | Distribution Box | Aggregate Trench |  |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/03/2020 | 05:52 AM
12/30/2020 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Joe Blevins Equipment Rental, Inc | 2705013926 | Joel | Blevins | 2.000000 | 1500 | Microfast |  | Pump | Gravity | Trenches | Not Applicable |  | ["None"] | ["None"] | NA | Musty | Cloudy | [15 empty] | The ditches are dry and cleaned the air filter. No sludge in treatment tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12/31/2020 | 12:00 AM
02/05/2020 |  | Routine, Scheduled |  | Prince William County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Prince William | Aquarobic Services | 1934000142 | Michael | Blake |  |  | None | None | Pump |  |  |  |  | ["Auxiliary Filter","Distribution Pump Operation","Level Sensor Operation"] | ["Auxiliary Filter","Distribution Pump Operation","Level Sensor Operation"] |  | YES | YES | [15 empty] | [Comments]: Evidence of dirt and moisture penetration observed at manway seals and at hole drilled in mechanical manway. Noticed buildup in one side of filterbed manifold. Recommend owner add rootkill asap to try to prevent roots from clogging the manifold. Aeration heavier on one side of the tank. Recommend a pump-out and cleaning after manway seals are repaired. Aeration can then be verified with clean water fill. Alarm float tested bad, replaced it. Also replaced the air filter. Terminal strip in j-box is heavily corroded and should be replaced. Effluent leak observed at manway. Repaired broken pvc connection and replaced cracked bulkhead adapter. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/27/2020 | 05:54 AM
12/07/2020 |  | RoutineScheduled | 87-183-170 | Russell |  |  | EHD - Cumberland Plateau | SEPTIC Inc | [17 empty] | 6.510000 | 6.290000 |  | 1.040000 |  | 12/07/2020 |  | 11.700000 |  |  | 0.000000 |  |  | Attached to this report |  | Uploading monitoring results-data entered by EHS from info provided by SEPTIC Inc |  |  |  | 12:00 AM
05/19/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/14/2021 | 04:27 PM
10/26/2020 |  | RoutineScheduled | 033-07-0299-SP | Caroline | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Attached Growth Medium" ,"Control Operation" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | ["Attached Growth Medium" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Control Operation" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | YES | [15 empty] | Will be sent separately | Inspected | Applied root kill to distribution box and retimed. Roots at septic tank and pump tank wedge lids. Small leak at pump tank outlet pipe. Pump line has settled. Proposal for repairs to be sent to homeowner. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
02/11/2020 |  | Routine, Scheduled | 06-172-0504AR | Powhatan County | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Chesterfield | Mathews Soil Consultants, Inc. | 1942001521 | Jason | Mathews |  |  | Ecoflo | Ecoflo | Pump | Distribution Box | Aggregate Bed | [22 empty] | [Comments]: The septic tank was pumped out today.The peat moss in the Ecoflo has deteriorated into mud, with effluent ponding on top. This peat should be replaced.The pump tank junction box is damaged and should be replaced. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 03/16/2020 | Jan 1 1900 11:26AM
05/19/2020 |  | Routine/Scheduled |  | Loudoun | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Loudoun | POWELLS PLUMBING, INC. | 1942001036 | Kurt | Holthaus | 1.000000 | 500 | Norweco Singulair ATU |  | Pump | Distribution Box | Aggregate Trench |  | 600.000000 | ["Blower/Compressor/Aerator Operation","Effluent Screens","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Effluent Screens","Sludge/Scum Accumulation"] | N/A | [17 empty] | Annual Inspection - Pumped trash side of Norweco, serviced blower and effluent screen(s). | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 06/19/2020 | 09:32 AM
01/27/2020 |  | Routine, Scheduled | 234-13-346 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesapeake | R & K Septic, Inc. |  | John | Butt, Jr |  |  | Clearstream ATU |  | Pump | Drip | Elevated Sand Mound | UV Light |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] |  |  |  | 7.280000 | 5.000000 | [13 empty] | [Comments]: Replaced: aerator, UV Bulb, UV Quartz, 2-6" risers, flat lid, air sensor. Wired for air sensor. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/27/2020 | Jan 1 1900 2:30PM
07/30/2020 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump | Drip | Elevated Sand Mound | UV Light |  | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  |  | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 07/30/2020 | Jan 1 1900 1:45PM
03/18/2020 |  | Routine, Scheduled |  | Loudoun County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | None | Pump | Distribution Box | Gravel-Less Trench | [23 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/12/2020 | 02:21 PM
04/14/2020 |  | RoutineScheduled | 179-STS-87307 | Stafford | This AOSS is not functioning as designed or in acc | Approved | EHD - Rappahannock | Culpeper Home Services | 2705167318 | Russell | Furr | 1.000000 | 1000 |  |  | Gravity | Gravity | Trenches | n/a |  | [] | [] | [17 empty] | Inspected | Like for Like 1000 gallon tank replacement, distribution box replacement, gravel, drains, 5" steel sleeve under driveway | This AOSS is not functioning as designed or in acc |  | 04/17/2020 | 11:52 AM
11/10/2020 |  | RoutineScheduled | 07-197-A5 | Wise | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | EHD - Lenowisco | Wise County Health Dept. |  |  |  | 1.000000 | 1000 |  |  | Gravity | Gravity | Discharge | Chlorination | 450.000000 | ["None"] | ["None"] | [17 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 11/11/2020 | 12:00 AM
07/24/2020 |  | Routine, Scheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green |  |  |  |  | Pump | Manifold | Aggregate Trench | None |  | ["Effluent Screens"] | ["Effluent Screens"] | [18 empty] | Pump Amps 16.2/19.7 Septic Sludge 7" Scum 0.25 Pump Sludge 0 Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 07/24/2020 | Jan 1 1900 1:50PM
08/20/2020 |  | Routine/Scheduled | 234-08 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesapeake | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1500 | Orenco Advantex | Orenco Advantex | Pump | Distribution Box | Aggregate Trench | None | 750.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | None | Clear | [15 empty] | Routine Service Conducted. Primary septic tank in normal operating level Processing Tank in normal operating level - RSV, Recirc. Pump and Effluent screen serviced. Treatment Modules - both modules flushed - media drapes serviced, distribution grid serviced. Discharge tank - normal operating level - pump serviced, float sensors, and controls operating properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 08/27/2020 | Jan 1 1900 7:30AM
06/29/2020 |  | RoutineScheduled | 154-07-0243 | Louisa | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Blue Ridge | Wastemaster Inc |  | Timothy | Jenkins | 2.000000 |  | ATU |  | Gravity | Gravity | Discharge | UV |  | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 04:35 PM
12/10/2020 | Alternative | Routine/Scheduled | 157-15-0065 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | Delta Environmental Products, UC Series |  | Pump | Manifold | Aggregate Trench | None | 450.000000 |  | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | Musty | Clear | [15 empty] | Routine Service Primary Septic Tank - normal level Aeration Tank - normal level - compressor serviced. U.V. Disinfection - operating - bulb and quartz crystal serviced. Pump Tank - normal level - pump, Pressure Bell & controls operating. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 12/11/2020 | 07:15 AM
06/10/2020 |  | Routine/Scheduled | 196-05-228 | Westmoreland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1500 | Orenco Advantex |  | Pump | Distribution Box | Aggregate Trench | None | 600.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | Musty | Clear | [15 empty] | Annual service conducted. Processing tank at normal levels - Effluent screen serviced, High Head turbine pump serviced - distribution laterals and media serviced, Discharge tank in normal operating level | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 07/12/2019 | 07:00 AM
08/10/2020 |  |  | 15-113-038 | Buchanan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 08/10/2020 |  | 19.800000 | [5 empty] | Attached to this report |  | TSS: BDL | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 08/10/2020 | 12:00 AM
11/25/2020 |  | Routine/Scheduled | 2010-143-0033 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Henrico | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. | 3.000000 |  | Clearstream ATU |  | Pump |  |  |  |  | ["Control Operation","Dispersal System Operation","Distribution Pump Operation"] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 11/25/2020 | 01:00 PM
07/29/2020 |  | RoutineScheduled | 05-113-031 | Buchanan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["Control Operation","BlowerCompressorAerator Operation","Disinfection","Effluent Screens"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
01/11/2020 |  | Routine, Scheduled | 03-163-0221 | New Kent County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chickahominy | Braxton, Corey Vance | 1942001039 | Corey | Braxton | 1.000000 |  | Orenco Advantex | Orenco Advantex | Pump | Distribution Box | None | None |  |  | ["Attached Growth Medium","Control Operation","Effluent Screens","Level Sensor Operation"] |  | None | 21.6 | 7.100000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/18/2020 | Jan 1 1900 5:49PM
09/08/2020 |  | Reportable Incident | 175-17-0369 | Prince William | This AOSS should now return to normal function after having provided the above state routine maintenance | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green | [9 empty] | ["Disinfection"] | ["Disinfection"] | [18 empty] | Installed Salcor UV Bulb. | This AOSS should now return to normal function after having provided the above state routine maintenance |  | 09/08/2020 | 04:00 PM
07/16/2020 |  | Routine, Scheduled | 175-04-0011 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Delta Environmental Products, DF Series |  |  |  |  | None |  | ["Blower/Compressor/Aerator Operation"] | ["Blower/Compressor/Aerator Operation"] |  | Good | Clear | [15 empty] | Needs ATU float. Spin filter cleaned. Pump Amps 9.16 ETM 3413 Cycles 45056 Water Meter Reading 1617160 Septic Sludge 11" Scum 0.50 ATU Sludge 10" Scum 8" Pump Sludge 6" Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 07/16/2020 | 02:20 PM
12/16/2020 |  | Initial Visit | 179-STS-88002 | Stafford | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Level Sensor Operation"] | ["Control Operation" ,"Level Sensor Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Recirc high level count at 4, low level 7. Reset temporary counts to zero. Drip panel high level count at 6. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
10/06/2020 |  | Routine/Scheduled |  | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [11 empty] | N/A | [9 empty] | 16.000000 |  | 15500.000000 | [5 empty] | Replaced UV control panel | This AOSS should now return to normal function after having provided the above state routine maintenance |  | 10/12/2020 | Jan 1 1900 8:30AM
06/29/2020 | Alternative |  | SD-05-10 | Fauquier | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Rappahannock-Rapidan | McKim Construction | 1942001330 | Michelle | McKim | [9 empty] | [] | ["Auxiliary Filter","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [19 empty] | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 10/23/2020 | 11:55 AM
10/20/2020 | Alternative | Follow-Up | 32318 | Shenandoah | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Lord Fairfax | Valley Soil & Environmental Consulting, LLC | 1942001218 | John | Lam | 1.000000 | 500 | Multi-Flo | Single pass sandfilter | Gravity | Pressure |  | Chlorination | 0.000000 | ["Control Operation","Disinfection","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Control Operation","Disinfection","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | NA | [16 empty] | Pumped Out | Trash tank prior to Multi-Flo unit pumped out; biosolids removed from surface of sandfilter and subsurface cleaned under pressure to remove biosolids; new filter socks (30) installed in Multi-Flo unit; new Orenco S2 control panel for the spray irrigation system installed; new electrical wiring in conduit and splice box installed from control panel to the pump tank; new system control floats installed; Intermatic timer installed in NEMA 4X box and properly wired to operate in conjunction with the pump control floats; pressure tank and pressure switch removed from spray pump system and found not necessary for proper system operation; spray pump inlet screen cleaned; added chlorine tablets to the tablet feeder tube | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 11/11/2020 | 12:00 AM
04/21/2020 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump | Drip | Elevated Sand Mound | UV Light |  | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/21/2020 | Jan 1 1900 3:00PM
12/17/2020 | Alternative | Initial Visit | 157-04-301 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1500 | Orenco Advantex |  | Pump | Distribution Box | Aggregate Trench | None | 450.000000 |  | ["Attached Growth Medium","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | None | Clear | [15 empty] | Initial Visit Processing Tank - normal level - RSV, Recirc pump & effluent screen serviced. Treatment Module - media drapes & spray grid serviced - hinges and piston rods broken Pump Tank - normal level - pump, float sensors & controls operating Distribution Box - intact - all laterals in high level - slow drainage. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 12/18/2020 | 12:00 PM
04/29/2020 |  | Initial Visit | SHUN-B46HV9 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Western Tidewater | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | Serviced system. Checked the pump, panel, & floats (ok). Cleaned the filter and diffuser in the Clearstream and cleaned the filter in the aerator. The timer is set to 1 minute every 1 hour. Owner wants a 6 x 24 riser for the pump tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 04/29/2020 | Jan 1 1900 12:00PM
10/05/2020 |  | Routine/Scheduled | 2019-126-079 (OSEW&S) | Dinwiddie | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Crater | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. |  |  | Clearstream ATU |  | Pump |  |  |  |  | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | Grab Bod sample | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 10/05/2020 | Jan 1 1900 10:00AM
12/08/2020 |  | RoutineScheduled | 153-STS-20379 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Wastemaster Inc |  | Timothy | Jenkins | 2.000000 |  | ATU | Recirculating Sandfilter | Pump | Gravity | Discharge | Chlorination |  | [] | [] |  | Musty | Clear | 7.400000 |  | 40.000000 | 2.200000 | [12 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 02:10 PM
08/20/2020 |  | Routine/Scheduled |  | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | POWELLS PLUMBING, INC. | 1942001036 | Kurt | Holthaus | 1.000000 | 1000 | Puraflo |  | Pump | Manifold | Drip Tubing |  | 300.000000 | ["Effluent Screens"] | ["Effluent Screens"] | N/A | [17 empty] | Annual Inspection - Serviced spin filter and effluent screen(s). | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 09/04/2020 | 01:29 PM
02/28/2020 |  | Routine, Scheduled | SWP-05-172 | Spotsylvania County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | None | None | Pump | Drip | Drip Tubing |  |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation","Distribution Pump Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation","Distribution Pump Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/06/2020 | 02:45 PM
09/18/2020 |  |  |  | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | McKim Construction | 1942001330 | Michelle | McKim | 2.000000 |  |  |  | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 11/13/2020 | Jan 1 1900 10:40AM
08/07/2020 |  | RoutineScheduled | 2014-143-0163 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Onsite Maintenance Team | 1942001039 | Corey | Braxton | 3.000000 |  |  |  | Pump |  |  |  | 300.000000 | [] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation"] |  | Musty | Clear | 6.400000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 08/07/2020 | 12:00 AM
03/24/2020 |  | Routine, Scheduled | 08-183-181 | Russell County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Cumberland Plateau | DEEL, DENNY M | 1942001097 | DENNY | DEEL |  |  | Norweco Singulair ATU | None | Gravity | None | Alternative Discharge | Chlorine | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens"] |  | Musty | Clear | [15 empty] | [Comments]: 5 blue crystals, 10 biomax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/13/2020 | Jan 1 1900 9:37AM
11/03/2020 | Alternative | Reportable Incident | 150-06-379 | King William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | EcoPod |  | Pump | Distribution Box | Aggregate Trench | None | 450.000000 | ["Blower/Compressor/Aerator Operation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | Pungent | Clear | [15 empty] | Alarm event Septic tank high level - effluent screen serviced - risers leaking. Aeration Tank - Compressor failed - requires replacement - Pump Tank - bad wire connection - repaired - pump, float sensors and controls operating properly. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 11/04/2020 | 07:45 AM
01/02/2020 |  | Routine, Scheduled |  | Warren County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Lord Fairfax | POWELLS PLUMBING, INC. | 1942001036 | Kurt | Holthaus | 1.000000 | 1060 | Orenco Advantex |  | Pump | Drip | Drip Tubing |  | 450.000000 | ["Effluent Screens"] | ["Effluent Screens"] | [18 empty] | [Comments]: Annual Inspection - Serviced spin filter and effluent screen(s). | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/02/2020 | 03:02 PM
09/29/2020 | Alternative | Routine/Scheduled | 157-11-0089 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | Clearstream |  | Pump | Distribution Box | Aggregate Trench | None | 600.000000 |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | Musty | Clear | [15 empty] | Routine service Primary Septic Tank - normal operating level Aeration tank - normal operating level - compressor serviced. Pump Tank - normal operating level - pump, float sensors & controls operating properly. Distribution box intact - all laterals accepting effluent. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 10/07/2020 | 08:30 AM
09/30/2020 |  | Routine, Scheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | EZ Treat Sandfilter |  |  |  |  | None |  | ["Dispersal System Operation","Effluent Screens"] | ["Dispersal System Operation","Effluent Screens"] |  | Acceptable | Clear | [15 empty] | Pump Amps 10.37 ETM 67 hrs 19 mins Cycles 4241 Pump Amps 9.05 Septic Sludge 15" Scum 1" Pump Sludge 5" Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 09/30/2020 | Jan 1 1900 1:09PM
05/08/2020 |  | RoutineScheduled | 2130-09-153 | Prince William | This AOSS is functioning as designed and in accord | Approved | EHD - Prince William | Wastemaster | 1965-001817 | Tim | Jenkins | 2.000000 |  |  | UV | Pump |  | Discharge | UV |  | [] | [] |  | Musty | Clear | 7.300000 |  |  |  |  | 05/08/2020 | [10 empty] | This AOSS is functioning as designed and in accord |  | 05/08/2020 | 07:40 AM
09/11/2020 |  | Routine/Scheduled | 06-160-0081 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Delta Environmental Products, DF Series |  | Gravity | Distribution Box |  | None |  | ["None"] | ["Blower/Compressor/Aerator Operation","Sludge/Scum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 09/11/2020 | 09:30 AM
12/22/2020 |  | Routine, Scheduled | 175-13-0521 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Clearstream ATU |  |  |  |  | None |  | ["Blower/Compressor/Aerator Operation"] | ["Blower/Compressor/Aerator Operation"] |  | Acceptable | Clear | [5 empty] | 12/22/2020 | Pump tank | 3.000000 | [7 empty] | Pump Amps 10.14 ETM 5885 Cycles 1175 Septic Sludge 11" Scum 0 ATU Sludge 7" Scum 0 Pump Sludge 2" Scum 0 On 3 mins 42 secs Off 8 hrs 28 secs | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 12/22/2020 | 12:33 PM
05/07/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/14/2021 | 04:27 PM
04/28/2020 |  | Routine/Scheduled | 08-120-0020A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesterfield | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1500 | Orenco Advantex | None | Pump | Drip | Drip Tubing | UV Light |  |  | ["Attached Growth Medium","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | [17 empty] | In the Processing Tank, the current RSV was found clogged (this specific cage design has a reputation for frequent clogging), the Recirculation Pump will meet its expected life expectancy in three years, and the Recirculation Floats have exceeded their life expectancy; the Discharge Pump will meet its life expectancy in three years, and the Discharge Floats have exceeded their life expectancy | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 05/20/2020 | Jan 1 1900 2:56PM
12/10/2020 |  | Routine, Scheduled | 175-16-0244 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | EZ Treat Sandfilter |  |  |  |  | None |  | ["Effluent Screens"] | ["Effluent Screens"] |  | Acceptable | Clear | [15 empty] | Pump Amps8.66 Septic Sludge 14" Scum 0 Pump Sludge 3" Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 12/10/2020 | 09:16 AM
01/28/2020 |  | Follow-Up |  | Loudoun County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Loudoun | POWELLS PLUMBING, INC. | 1942001036 | Kurt | Holthaus | 1.000000 | 500 | Norweco Singulair ATU |  | Pump | Distribution Box | Aggregate Trench |  |  | ["Dispersal System Operation","SludgeScum Accumulation"] | ["Dispersal System Operation","SludgeScum Accumulation"] | [18 empty] | [Comments]: Pumped Norweco and drain field has been mowed. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/28/2020 | 12:28 PM
09/22/2020 |  | Follow-Up | 061-STS-21184 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Soils, Inc. | 1940001392 | Markham | Smith | 2.000000 | 1500 | Mirofast 0.50 in a Hanover 1500 top seam tank |  | Pump | Pressure | Drip |  |  | [] | ["SludgeScum Accumulation","Septic Tank Baffles","BlowerCompressorAerator Operation","Attached Growth Medium","Control Operation"] | NA | [7 empty] | 12/22/2020 | Sample Chamber | 3.000000 | [8 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 09/25/2020 | 08:25 AM
12/21/2020 |  | RoutineScheduled | 157-14-0096 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Church View Septic Service Inc. | 1942001302 | Charles | Langford | 1.000000 | 1200 | ECOPOD |  | Pump | Gravity | Pad | Not Applicable |  | ["None"] | ["None"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 01/08/2021 | 12:00 AM
11/02/2020 |  | RoutineScheduled | 107-17-0040 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Onsite Wastewater Services - May Supply | 1942001627 | Drew | Shull | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity |  | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 05/28/2021 | 05:41 AM
02/19/2020 |  | Initial Visit | 109-19-0239 | Bedford County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Central | WAUGH, IAIN C | 1942001512 | IAIN | WAUGH | 1.000000 | 1500 | Septic Tank Only | Orenco Advantex | Pump | Distribution Box | Aggregate Trench | None |  | ["Control Operation"] | ["Control Operation"] | [18 empty] | [Comments]: Set setting for recirculation pump to 18 min off and .8 min on. Ran system in test mode, tightened union fitting for spray head. Alarm tested ok, Initial high water quickly pumped water to normal levels after running in test mode for the first time | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/19/2020 | 12:43 PM
06/29/2020 |  | RoutineScheduled | SWP-03-172 | Stafford | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Effluent Screens" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Effluent Screens" ,"Recirculation Pump"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 |  | 04/09/2021 | 03:25 PM
05/13/2020 |  | RoutineScheduled | 06-197-025 | Wise | This AOSS is functioning as designed and in accord | Approved | EHD - Lenowisco | Septic Inc |  | Denny | Deel |  |  |  |  | Gravity | D-Box | Aggregate Bed | None | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","Effluent Screens"] | ["BlowerCompressorAerator Operation","Control Operation","Effluent Screens"] | true | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accord |  |  | 12:00 AM
08/01/2020 |  | RoutineScheduled | 171-09-0319 | Pittsylvania | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Pittsylvania-Danville | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1000 | MultiFlo ATU |  | Pump | Pressure | Drip |  |  | ["Distribution Pump Operation"] | ["Distribution Pump Operation"] | [18 empty] | 6" of solids in septic tank. Discharge pump not operational and needs to be replaced. Adequate aeration. Cleaned drip field manifold spin filter. Tested discharge pump controller. Tested alarms. Replaced discharge pump on 8-10-2020. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 10/15/2020 | 07:03 PM
01/26/2020 |  | Reportable Incident | {FIPSCode}-STS-1098 | Chesapeake | This AOSS should now return to normal function after having provided the above stated routine maintenance. | Approved | EHD - Chesapeake | R & K Septic, Inc. |  | Craig | Van Holten |  |  | Clearstream ATU | [6 empty] | ["Dispersal System Operation","Level Sensor Operation"] | ["Dispersal System Operation","Level Sensor Operation"] | [18 empty] | [Comments]: Replaced float | This AOSS should now return to normal function after having provided the above stated routine maintenance. |  | 01/26/2020 | Jan 1 1900 10:00AM
09/30/2020 |  | RoutineScheduled | SWP-05-345 | Stafford | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 2.000000 |  | Ecoflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Attached Growth Medium" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | ["Distribution Pump Operation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Attached Growth Medium" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | YES | [15 empty] | Will be sent separately | Inspected | 1st septic tank inlet wedge lid and concrete outlet riser is leaking. 2nd septic tank added outlet tee. Inlet wedge lid & outlet riser is leaking. Raked peat; water went away. Drainfield needs mowing and samplings removed. Proposal for repairs to be sent to homeowner. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
08/13/2020 | Alternative | Routine/Scheduled | 128-14-0067 | Essex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | Serviced system. Checked the pump, panel, & floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. Removed the spinfilter screen - going to an LPD. Installed orifice in the return line. Removed the sock from the Clearstream. The drainfield has visible wetness - owner is going to get some dirt for it. The timer is set to 30 seconds every 20 minutes. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 08/13/2020 | 12:00 PM
03/04/2020 |  | Routine, Scheduled | 179-14-0158-SR | Stafford County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | None | Pump | Distribution Box | Aggregate Trench | UV Light |  | ["Attached Growth Medium","Disinfection","None","Recirculation Pump"] | ["Attached Growth Medium","Disinfection","None","Recirculation Pump"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/06/2020 | 02:45 PM
08/31/2020 |  | RoutineScheduled | 175-10-0089 | Prince William | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Effluent Screens" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Effluent Screens" ,"Recirculation Pump"] | YES | [15 empty] | Will be sent separately | Inspected | Gum should not be flushed into your septic system. | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 |  | 04/09/2021 | 03:25 PM
01/27/2020 |  | Initial Visit | 182-19-0179 | Rockingham County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Central Shenandoah |  |  |  |  | 1.000000 | 1500 |  | Orenco Advantex | Pump | Drip | Drip Tubing | None |  | ["Control Operation"] | ["Control Operation"] | [18 empty] | [Comments]: AX20RT3 POD 432968 Recirc Pump-off 15min On .8min ETM-2.51Hr Cycle COunt-509 Discharge Pump- Demand Dose ETM-19min Cycle Count 7 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/31/2020 | 30-12-1899 03:10 PM
03/27/2020 |  | Routine, Scheduled |  | Loudoun County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | None | None | Pump | Manifold | [24 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/12/2020 | 02:21 PM
03/06/2020 |  | Follow-Up |  | Fairfax County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Fairfax | BLEVINS, JOEL R, SR | 1934000415 | JOEL | BLEVINS |  |  | Microfast | Septic Tank Only | None | None | None | None | [11 empty] | 03/06/2020 | pump tank | 35.000000 | [5 empty] | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/23/2020 | Jan 1 1900 10:32AM
02/19/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS should now return to normal function after having provided the above stated routine maintenance. | Paid | EHD - Fairfax | SEAMON, CHARLIE L | 1942001108 | CHARLIE | SEAMON |  |  | Septic Tank Only | Microfast | Pump | Manifold | Aggregate Bed | None |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | [10 empty] | 22.000000 | [7 empty] | [Comments]: Performance Inspection and BOD Sample:Microfast to Pad. Septic-6"sludge 6"scum/Microfast- 0" sludge Pump tank-0"sludge.No pump out needed at this time.Blower air filter cleaned. P1 cnts-48 ETM-3h 1m/ P2 cnts-47 ETM-2h 8m/ Peak-6/ High-3. No break out or spongy areas at the pad site WATER WAS FLOWING FROM THE HOUSE, NO ONE HOME. | This AOSS should now return to normal function after having provided the above stated routine maintenance. |  | 03/12/2020 | Jan 1 1900 6:40AM
03/06/2020 |  | Initial Visit | SR-02-2001 | Spotsylvania County | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Rappahannock | Old Dominion Onsite, Inc. |  | John | Ewing | 1.000000 | 1500 | Microfast |  | Pump | Manifold | Drip Tubing |  | 150.000000 | ["Control Operation"] | [19 empty] | [Comments]: Control panel for drip dispersal pump system is not operating automatically. The control panel needs to be replaced. Homeowner reports the old original drainfield is currently being used for dispersing effluent. | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 03/06/2020 | 09:22 AM
10/26/2020 |  | RoutineScheduled |  | Shenandoah | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Puraflo | none | Pump | Gravity |  | Not Applicable |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/26/2021 | 09:04 AM
12/22/2020 | Alternative | RoutineScheduled | 128-07-032 | Essex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Church View Septic Service Inc. | 1942001302 | Charles | Langford | 1.000000 | 1250 | Ecoflo | [6 empty] | [] | [] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 01/07/2021 | 12:00 AM
05/18/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/14/2021 | 04:27 PM
06/26/2020 |  | Routine, Scheduled | SD-11-225 | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Biomicrobics MicroFAST |  | Pump | Drip | Drip Tubing | None |  | ["Blower/Compressor/Aerator Operation"] | ["Blower/Compressor/Aerator Operation"] |  | Good | Clear | [15 empty] | Spin filter cleaned. Pump Amps 9.85 ETM 638 hrs 42 mins Cycles 5130 Septic Sludge 3" Scum 4" ATU Sludge 4" Scum 0 Pump Sludge 3" Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 06/26/2020 | 09:51 AM
09/03/2020 |  | Routine, Scheduled | 175-16-0478 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | EZ Treat Sandfilter |  |  |  |  | None |  | ["Effluent Screens"] | ["Effluent Screens"] | [18 empty] | Pump Amps 8.79 Septic Sludge 11" Scum 1" Pump Sludge 6' Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 09/03/2020 | 03:34 PM
06/17/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | SES MidAtlantic LLC | 1942001203 | James | Green | 1.000000 |  | Delta Environmental Products, DF Series | none | Gravity | Gravity | Trenches | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/15/2021 | 09:00 AM
10/22/2020 |  | Routine/Scheduled | 2007-143-0225 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Old Dominion Onsite, Inc. | 1942001549 | Russell | Revis | [9 empty] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation"] | N/A | [17 empty] | Cleaned effluent filter, inspected peat, and checked float and pump operation. System appears to be working well. Noted a few flushable wipes and one dish rag or wash cloth wrapped up in effluent filter. We recommend discontinuing the disposal of these items through your septic system, or more frequent pump outs may be required. System functioning well, and peat was in great shape. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 10/22/2020 | 02:47 PM
11/04/2020 |  | RoutineScheduled | 175-07-0421 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic Tank/ EZ-Treat Recirculation | Pump Tank | Pump | Gravity | Trenches | Not Applicable |  | ["None"] | ["None"] | NO | [9 empty] | 28.000000 | [7 empty] | Septic-2"sludge 0"scum/ EZ-Treat-0"sludge/ Pump tank-0"sludge/ No pump out needed/ Counts: Discharge Pump-19 ETM-1h 45m/High-4/Peak (n/a)/ EZ-Treat Counts: Pump-2626 ETM-137.02/ No breakout or spongy areas on the drainfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
07/27/2020 |  | RoutineScheduled | {FIPSCode}-STS-8707 | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | ["None"] | ["None"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 07/28/2020 | 12:00 AM
08/27/2020 |  | Routine/Scheduled | 15-120-0166A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesterfield | Old Dominion Onsite, Inc. | 1942001503 | Jason | Hackler | [9 empty] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump"] | N/A | [17 empty] | Cleaned effluent filter and flushed manifold. Housing for filter was damaged on arrival, fixed with glue and primer. Checked pump and flat operation. Sewer like is not properly connected at clean out, this needs to be dug up and reset. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 08/27/2020 | Jan 1 1900 10:46AM
04/02/2020 |  | RoutineScheduled | 107-11-0219 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Onsite Wastewater Services - May Supply | 1942001022 | Sara | Tusing | 2.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 05/28/2021 | 05:41 AM
06/04/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Payment | EHD - Loudoun | Great Falls Septic Service, Inc | 1942001301 | Josh | Hott | 1.000000 |  | Puraflo | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/27/2021 | 11:51 AM
02/05/2020 |  | Routine, Scheduled | {FIPSCode}-STS-2292 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesapeake | R & K Septic, Inc. |  | John | Butt, Jr |  |  | Clearstream ATU |  | Pump | Distribution Box | Aggregate Bed | None |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] |  |  | 2.06 | 6.240000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/05/2020 | Jan 1 1900 3:45PM
06/17/2020 |  | RoutineScheduled | 124-STS-2379 | Louisa | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Rejected | EHD - Blue Ridge | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Ecoflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation"] | ["Distribution Pump Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Routine inspection. Fair amount of ponding, went away after raking the peat. Also a fair amount of grease on top - discussed with owner. Found crack in top of pod with stains. Ran garden hose about a minute to confirm that is was a source of infiltration. Needs fiberglass patch. Recommended removing leaf piles from drainfield to facilitate inspections. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
05/06/2020 |  | Follow-Up |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Homeowner/HOA contacted McKim Construction for repair. Air release valves were replaced. The system appears to be functioning as designed. Recommend regularly mowing drainfield area | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/27/2021 | 01:26 PM
12/15/2020 |  | Routine/Scheduled |  | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump |  | Elevated Sand Mound | UV Light |  | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  |  | 8.410000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 12/15/2020 | Jan 1 1900 9:00AM
04/02/2020 |  | Routine, Scheduled |  | Prince William County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Prince William | JENKINS, TIMOTHY R | 1942001062 | TIMOTHY | JENKINS | 0.000000 |  | Aquarobic Mini Plant | Septic Tank Only | None | None | Alternative Discharge | UV Light |  | ["None"] | ["None"] |  | Musty | Clear | 6.800000 |  |  |  |  | 04/02/2020 | Effluent | 0.000000 |  | 1.000000 | 1.600000 | [5 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/16/2020 | 11:13 AM
06/18/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/27/2021 | 01:26 PM
05/04/2020 |  | RoutineScheduled | 113-18-074 | Madison | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Sheetz | 19420001050 | Troy | Jenkins | 2.000000 | 1500 | Septic Tank Only | Septic Tank Only |  | Pressure | Drip |  | 945.000000 | ["None"] | ["None"] |  |  |  | 7.290000 |  |  |  |  | 05/04/2020 | Sample Tap | 4.000000 |  |  |  | 4.760000 |  | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 06/15/2020 | 02:30 AM
08/26/2020 |  | RoutineScheduled | SD-12-145 | Fauquier | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Rappahannock-Rapidan | Battlefield Soil And Septic LLC | 1942001084 | Josh | Johnston | 2.000000 | 2250 | Advantex ax20RT |  | Pump | Pressure | Drip | Not Applicable | 300.000000 | [] | ["Auxiliary Filter","Control Operation","Distribution Pump Operation","Recirculation Pump","Septic Tank Baffles","Effluent Screens","Level Sensor Operation"] |  | None | Clear | [16 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 09/03/2020 | 02:20 PM
08/21/2020 |  | Routine/Scheduled | 199-03-0042 | York | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Peninsula | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1500 | Orenco Advantex |  | Pump | Distribution Box | Aggregate Bed | None | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | None | Clear | [15 empty] | Annual service conducted. Processing tank in normal operating level - RSV, Recirc. pump and effluent screen serviced. Treatment Module - media drapes and distribution grid serviced. Discharge tank in normal operating level - discharge pump serviced, float sensors and controls operational. Distribution box located and inspected - normal level - all laterals accepting effluent. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 08/27/2020 | Jan 1 1900 8:15AM
06/25/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Recommend putting ball valves on the manifolds to even the flow. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/27/2021 | 01:26 PM
03/30/2020 |  | RoutineScheduled | 182-15-0166 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | SEAL’S CONSTRUCTION & SEPTIC TANK SERVICE, INC. | 1934000144 | Charles | Seal |  |  | tank only | MicroFast | Gravity | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter"] | ["Auxiliary Filter"] | NA | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 03/30/2020 | 12:00 AM
06/23/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/14/2021 | 04:27 PM
03/09/2020 |  | Routine, Scheduled |  | Rockbridge County | This AOSS should now return to normal function after having provided the above stated routine maintenance. | Paid | EHD - Central Shenandoah | AYRES, HUNTER E | 1942001166 | HUNTER | AYRES | 1.000000 | 1000 | Septic Tank Only | Septic Tank Only | Pump | Manifold | Aggregate Trench | None |  | ["Control Operation","SludgeScum Accumulation"] | ["Control Operation","SludgeScum Accumulation"] | [18 empty] | [Pumpout Comments]: septic tank and pump tank pumped and cleaned. [Comments]: Septic tank and pump tank pumped and cleaned. Spin filter and parts replaced. New contacter replaced in control panel. No apparent leaks in system or drain field area. Lids properly secured. | This AOSS should now return to normal function after having provided the above stated routine maintenance. |  | 03/16/2020 | 09:10 AM
12/22/2020 | Alternative | Routine/Scheduled | 151-17-0042 | Lancaster | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Thomas W. Beasley Septic Contractor | 1944001751 | Thomas | Beasley | 3.000000 | 3000 | EcoPod |  | Pump | Distribution Box | Aggregate Bed |  |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12/22/2020 | 05:00 PM
12/04/2020 |  | RoutineScheduled | SD-06-77 | Culpeper | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Ecoflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation" ,"Level Sensor Operation" ,"Control Operation"] | ["Distribution Pump Operation" ,"Level Sensor Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Routine inspection. Pod ponding badly again, holding 2-3" of water. Suspect too much water coming in is causing the peat to compact and not drain properly. Verified septic tank inlet (wedge) lid leaks badly by running water from a garden hose over the lid for a few minutes. Strongly advised replacing the buried concrete lid with a plastic riser and lid which would also provide a way to check for unintentional water flow from the house. Also recommended a video inspection of the sewer line from the house, and the conveyance line from septic tank to Ecoflo pod. Either line could be damaged and allowing groundwater into the septic system. Continued ponding will lead to premature peat failure. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
10/21/2020 |  | RoutineScheduled | 13-197-A1 | Wise |  | Approved | EHD - Lenowisco | VDH |  | Brad | Stallard | [12 empty] | None | Clear | 7.500000 | 5.000000 | [13 empty] | No lab samples collected |  |  |  | 12:00 AM
11/16/2020 |  | Routine/Scheduled | 07-118-0085 | Charles City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chickahominy | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1500 | Orenco Advantex |  | Pump | Distribution Box | Aggregate Trench | None | 600.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | None | Clear | [15 empty] | Routine Service Processing Tank - normal operating level - RSV, Recirc Pump & Effluent screen serviced. Treatment Module - media drapes & spray grid serviced. Discharge tank - normal operating level - pump, float sensors & controls operating properly. Distribution box intact - all laterals accepting effluent. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 11/17/2020 | Jan 1 1900 7:15AM
12/04/2020 |  | RoutineScheduled | 179-18-0447-SWP | Stafford | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Septic Works LLC | 1942001080 | michael | smith | 1.000000 |  | Orenco Advantex | none | Gravity | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/25/2021 | 08:10 AM
02/19/2020 |  | Routine, Scheduled | {FIPSCode}-STS-18760 | Frederick County | This AOSS should now return to normal function after having provided the above stated routine maintenance. | Approved | EHD - Lord Fairfax | Cubbage, Harrison Lee, II | 1942001021 | Harrison | Cubbage | 1.000000 | 1000 | Septic Tank Only | Sandfilter, High rate | Pump | Distribution Box | Aggregate Trench | None |  | ["Attached Growth Medium","Control Operation","Level Sensor Operation"] | ["Control Operation","Level Sensor Operation"] |  | Musty | Clear | [15 empty] | [Comments]: Repairs completed to electrical supply Pump Tank Sludge 6" Scum 0" | This AOSS should now return to normal function after having provided the above stated routine maintenance. |  | 03/29/2020 | 01:04 PM
02/04/2020 |  | Routine, Scheduled | 234-13-73 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesapeake | R & K Septic, Inc. |  | John | Butt, Jr |  |  | Clearstream ATU |  | Pump | Drip | Elevated Sand Mound | UV Light |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] |  |  | 9.62 | 7.960000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/04/2020 | Jan 1 1900 11:00AM
09/25/2020 |  | Routine, Scheduled | 124-STS-2379 | Fairfax | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Biomicrobics MicroFAST |  |  |  |  | UV Light |  | ["Blower/Compressor/Aerator Operation"] |  |  | Acceptable | Clear | [15 empty] | Toe of mound is soft. Blower airline fitting cracked. Spin filter cleaned. Pump Amps 8.17 ETM 404 hrs 5 mins Cycles 2630 Water Meter Reading 194700 Septic Sludge 13" Scum 2" ATU Sludge 17' Scum 0 Pump Sludge 0 Scum 0 | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 09/25/2020 | Jan 1 1900 10:55AM
05/13/2020 |  | RoutineScheduled | 179-07-0224-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Effluent Screens" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Effluent Screens" ,"Recirculation Pump"] | YES | [15 empty] | Will be sent separately | Inspected | We recommend clearing the vines away from the cleanout at the Distribution Box. | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 |  | 04/09/2021 | 03:25 PM
07/21/2020 |  | Initial Visit | 179-STS-87509 | Stafford | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Septic Works LLC | 1942001080 | michael | smith | 1.000000 |  | EZ Treat Sandfilter | none | Gravity | Gravity | Drip | UV |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/25/2021 | 08:10 AM
05/21/2020 | Alternative | Routine/Scheduled | 136 05 198 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | Ecoflo | None | Pump | Distribution Box | Aggregate Trench | None |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | In the Pump Tank, the Pump and Floats have exceeded life expectancy, and the electrical Junction Box wiring is starting to corrode and the Box is no longer water-tight; | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 06/04/2020 | 04:46 PM
03/04/2020 |  | Routine, Scheduled | 03-165-0213 | Northampton County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Eastern Shore | DUER, PETE C | 1942001051 | PETE | DUER | 1.000000 | 1250 | Septic Tank Only | Puraflo | Pump | None | None | None |  | ["None"] | ["None"] | [18 empty] | [Comments]: Aoss Inspection | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/27/2020 | 01:52 PM
02/21/2020 |  | Routine, Scheduled | 109-05-0588 | Bedford County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Central | WAUGH, IAIN C | 1942001512 | IAIN | WAUGH | 1.000000 | 300 | Septic Tank Only | Microfast | Pump | Manifold | Spray Irrigation | Chlorine |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | [18 empty] | [Pumpout Comments]: Pumped last year [Comments]: Septic tank 2" Scum 12" Sludge, Fast -12" sludge Pump Tank 6" Sludge, Pump Opperational Timed Dose at night. Pump run-4025 Count/ 363 Hour Cleaned Blower Filter, Blower Alarm GOod, Pump Tank alarm Good, Sprinker spray pattern good Owner Replaces Chlorine tabs as needed | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/06/2020 | 08:57 PM
08/13/2020 |  | Routine, Scheduled | 175-03-0441 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Aquarobic Mini Plant |  | Pump | Manifold | Elevated Sand Mound | None |  | ["Blower/Compressor/Aerator Operation"] | ["Blower/Compressor/Aerator Operation"] |  | Good | Tan | [15 empty] | Pump Amps 5.58 Septic Sludge 5" Scum 0 System good. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 08/13/2020 | 04:20 PM
04/29/2020 |  |  | 175-10-0117 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | [9 empty] | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | [8 empty] | 04/29/2020 |  | 11.000000 | [7 empty] | Septic/ATU had 4" sludge and 2" scum ATU had 6" sludge Pump tank had 0" sludge Cleaned air filter for blowere W/M- 0555,016 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
03/24/2020 |  | Reportable Incident |  | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump | Drip | Elevated Sand Mound | UV Light |  | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | Replaced: Screen filter, aerator, pump w/ WE20, UV cord, UV bulb, UV quartz. Installed float tree for floats. | This AOSS should now return to normal function after having provided the above state routine maintenance |  | 03/24/2020 | Jan 1 1900 10:45AM
03/04/2020 |  | Routine, Scheduled |  | Loudoun County | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Paid | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | None | None | Pump | Distribution Box | Aggregate Bed | [22 empty] | [Comments]: pump tank needs pumped out | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 04/12/2020 | 02:21 PM
03/12/2020 |  | Routine, Scheduled |  | Prince William County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Puraflo |  | Pump |  |  | None |  | ["Effluent Screens"] | ["Effluent Screens"] |  | Good | [16 empty] | [Comments]: Recommend BOD Sample on Puraflo Modules.Pump Amps 10.92 ETM 34632h Cycles 11000Septic Sludge 10" Scum 1"Pump Sludge 1" Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/12/2020 | 04:15 PM
09/23/2020 |  | Routine/Scheduled | 08-137-0191 | Goochland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chickahominy | Miller's Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1500 | Orenco Advantex |  | Pump | Distribution Box | Aggregate Trench | None | 600.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | None | Clear | [15 empty] | Routine service Processing tank - normal operating level - RSV, recirc pump and effluent screen serviced. Treatment Module - media drapes and spray grid serviced. Discharge tank - normal operating level - discharge pump serviced, float sensors and controls operating properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 10/05/2020 | Jan 1 1900 12:45PM
10/15/2020 |  | Reportable Incident |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Eco Virginia | 1942001235 | William | Poindexter | 1.000000 |  | Delta Environmental Products, UC Series | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation"] | ["Distribution Pump Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced Puraflo dosing pump and alarm light bulb | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 |  | 06/03/2021 | 05:53 AM
01/27/2020 |  | Follow-Up | 033-09-0097-SR | Caroline County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | EcoPod | None | Pump | Drip | Drip Tubing | [14 empty] | 19.000000 | [8 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/11/2020 | 06:36 AM
05/04/2020 |  | RoutineScheduled | 08-183-278 | Russell | This AOSS is functioning as designed and in accord | Approved | EHD - Cumberland Plateau | Septic Inc |  | Denny | Deel |  |  |  |  | Gravity | None | Alternative Discharge | Chlorine | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens"] | true | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accord |  |  | 12:00 AM
01/22/2020 |  | Follow-Up | 234-17-0040 | Chesapeake | This AOSS should now return to normal function after having provided the above stated routine maintenance. | Approved | EHD - Chesapeake | R & K Septic, Inc. |  | Tina | Van Holten | [9 empty] | ["Disinfection"] | ["Disinfection"] | [18 empty] | [Comments]: Replaced UV Bulb & UV Ballast | This AOSS should now return to normal function after having provided the above stated routine maintenance. |  | 01/22/2020 | Jan 1 1900 3:00PM
08/20/2020 |  | RoutineScheduled | 179-18-0379-SP | Stafford | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Septic Works LLC | 1942001080 | michael | smith |  |  | Orenco Advantex | none | Gravity | Gravity | Drip | Not Applicable |  | ["SludgeScum Accumulation" ,"Dispersal System Operation"] | ["Dispersal System Operation" ,"SludgeScum Accumulation"] | NA | [15 empty] | Will be sent separately | Inspected | Return air release broken full of debris. repaired air release not able to get some small rocks out of pipe. Excessive build of of toilet paper in septic tank | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/25/2021 | 08:10 AM
11/03/2020 | Alternative | RoutineScheduled | 171-06-0302 | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | [6 empty] | Fast | [6 empty] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 11/03/2020 | 12:00 AM
05/12/2020 |  | Routine/Scheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Loudoun | POWELLS PLUMBING, INC. | 1942001036 | Kurt | Holthaus | 1.000000 | 1000 |  |  | Pump | Drip | Drip Tubing |  | 450.000000 | ["Control Operation","Effluent Screens"] | ["Control Operation","Effluent Screens"] | N/A | [17 empty] | Annual Inspection - Replaced alarm buzzer, serviced spin filter and effluent screen(s). | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 05/13/2020 | 09:46 AM
04/20/2020 |  | RoutineScheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Greenway Engineering | 1942001008 | Jeremy | Ferguson | 1.000000 | 1500 | LPD | none | Pump | Gravity | Trenches | Not Applicable |  | ["Level Sensor Operation","SludgeScum Accumulation","Effluent Screens"] | ["Level Sensor Operation","SludgeScum Accumulation","Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 07/21/2020 | 11:30 AM
08/27/2020 |  | Routine/Scheduled | 136-10-0298 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 500 | Clearstream | None | Pump | Manifold | Aggregate Trench | None | 450.000000 |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | Musty | Clear | [15 empty] | Routine service conducted Trash Tank - normal operating level Aeration Tank - normal operating level - diffuser serviced - compressor serviced. Discharge tank - pump serviced - | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 08/28/2020 | 03:30 PM
05/12/2020 |  | RoutineScheduled | {FIPSCode}-STS-24675 | Wise | This AOSS is functioning as designed and in accord | Approved | EHD - Lenowisco | Septic Inc |  | Denny | Deel |  |  |  |  | Gravity | None | Alternative Discharge | Chlorine | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens"] | true | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accord |  |  | 12:00 AM
02/18/2020 |  | Routine, Scheduled | 185-STS-15313 | Tazewell County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Cumberland Plateau | DEEL, DENNY M | 1942001097 | DENNY | DEEL |  |  |  | Septic Tank Only | None | None | None | None | [11 empty] | 02/18/2020 |  | 9.050000 |  |  | 2.200000 |  |  | Attached to this report |  | [Lab Comments]: 2020 YEARLY MONITORING RESULTS [Comments]: UPLOADING MONITORING ONLY VENIS File Names: CarstonFord2020.pdf | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/18/2020 | Jan 1 1900 2:11PM
08/04/2020 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | FIVE STAR SEPTIC INC | 1944001248 | AARON | GOINS |  |  |  |  | Pump | Pressure | Drip |  |  | ["None"] | ["None"] | NO | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 05/06/2021 | Jan 1 1900 1:30PM
12/22/2020 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump | Distribution Box |  | None |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  | 2.09 | 4.880000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 12/22/2020 | Jan 1 1900 11:00AM
02/14/2020 |  | Routine, Scheduled | 08-118-0043 | Charles City County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Chickahominy | PARSLEY, JAMES MICHAEL | 194001106 | JAMES | PARSLEY | 1.000000 | 1000 | Whitewater ATU | Septic Tank Only | Pump | Distribution Box | Aggregate Trench | None |  | ["None"] | ["Effluent Screens"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/21/2020 | Jan 1 1900 3:53PM
11/05/2020 |  | RoutineScheduled | DTAR-999PPS | Craig | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Alleghany-Roanoke | King's Alternative Septic | 1942001112 | William | King, II | 1.000000 | 1000 | Biomicrobics Microfast 0.5 |  | Gravity | Gravity | Trenches | Not Applicable |  | ["None"] | ["None"] | NA | [17 empty] | System is working correctly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 11/17/2020 | 12:00 AM
10/28/2020 |  | Routine/Scheduled |  | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | EcoPod |  | Pump |  |  | None |  | ["Attached Growth Medium","Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Attached Growth Medium","Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  |  | 7.000000 | 4.000000 | [13 empty] | Replaced aerator 12/22/20 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 12/22/2020 | Jan 1 1900 3:30PM
09/02/2020 |  | Routine/Scheduled | 19-120-0237 | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. |  |  | Aqua Klear |  | Pump |  |  |  |  | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [9 empty] | 13.000000 | [7 empty] | Grab Bod sample | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 09/02/2020 | Jan 1 1900 9:30AM
12/09/2020 |  |  | 133 08 0030 | Franklin | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - West Piedmont | Western Virginia Water Authority | 1942001145 | Michael | Doss |  |  |  |  | Pump | Pressure | Drip | UV |  | ["None"] | ["None"] | YES | Musty | Clear | [5 empty] | 12/09/2020 | Sample Chamber |  |  | 1.000000 | 2.800000 | 3.100000 |  | Attached to this report |  |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 01/13/2021 | 09:15 AM
01/03/2020 |  | Routine, Scheduled | {FIPSCode}-STS-2804 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesapeake | R & K Septic, Inc. |  | Robbie | Van Holten |  |  | Clearstream ATU |  | Pump | Distribution Box |  | None |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] |  |  |  | 6.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/03/2020 | Jan 1 1900 1:15PM
11/24/2020 |  | Pump-Out Only | 2007-141-077 | Halifax |  |  | EHD - Southside | Matthews Sanitation Services, LLC |  |  | Matthews | [33 empty] | 12:00 AM
05/12/2020 |  | Follow-Up |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | The septic and pump tank were pumped out and the riser was replaced. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/14/2021 | 04:27 PM
01/03/2020 |  | Routine, Scheduled |  | Warren County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Lord Fairfax | Cubbage, Harrison Lee, II | 1942001021 | Harrison | Cubbage | 1.000000 | 1500 | Septic Tank Only | Orenco Advantex | Pump | Drip | Drip Tubing | None |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation"] |  | Musty | Clear | [15 empty] | [Comments]: Recirc Pump- Off 19.7min On .3min ETM-1361.8Hr Cycle Count-74900 Discharge Pump- Off 2hrs On 12min ETM-2110.8Hr Cycle Count-37112 Sludge/Scum Accumulations: Comp.1-13"/1" Comp.2-6"/1" Pump Tank-4"/0" | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/18/2020 | 12:03 PM
10/22/2020 |  | Routine/Scheduled | 2016-143-0203 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | Old Dominion Onsite, Inc. | 1942001549 | Russell | Revis | [9 empty] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Level Sensor (Float) Operation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Level Sensor (Float) Operation"] | N/A | [17 empty] | Cleaned air filter, checked float and pump operation. Inspected distribution box where recent repair was made to the force main, which is functioning well. No leaks in drain field. System working correctly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 10/22/2020 | 12:45 PM
06/07/2020 |  | RoutineScheduled | 187090100 | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Randy's Complete Water & Wastewater Services | 1942001335 | Randy | Gray | 1.000000 | 1000 | Puroflo |  | Pump | Gravity | Trenches | Not Applicable |  | ["None"] | ["None"] | NA |  | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 09/02/2020 | 09:00 PM
12/08/2020 |  | Routine/Scheduled | 10-142-0158 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chickahominy | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1500 | Hoot | None | Pump | Drip | Drip Tubing | None | 450.000000 |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | Musty | Clear | [15 empty] | Alarm - Routine - no service agreement - no service since 2018. Septic tank / trash tank - normal level Aeration tank - normal level - compressor serviced. Pump Tank - high level - cause clogged drip disk filter - serviced - pump serviced - sensor probe and controls operating properly. Pumped system out of high level with system pump to drip field. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 12/09/2020 | Jan 1 1900 10:15AM
12/07/2020 | Alternative | Initial Visit | 133-STS-105622 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers | Miller's Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | None | None | Gravity | Distribution Box | Aggregate Trench | None | 450.000000 | ["Dispersal System Operation"] | ["Dispersal System Operation","Effluent Screens","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | [17 empty] | Initial visit - COSS gravity distribution Primary septic tank - normal level - effluent screen serviced. Distribution box - Plastic - Fractured in bottom, requires replacement - all laterals appear to be accepting effluent. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 12/09/2020 | 09:15 AM
02/05/2020 |  | Routine, Scheduled |  | Mathews County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Three Rivers | MEAGHER, WILLIAM J | 1942001190 | WILLIAM | MEAGHER | 1.000000 | 1000 | Septic Tank Only | Clearstream | Pump | Distribution Box | Gravel-Less Trench | None | [22 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/06/2020 | 10:41 AM
08/05/2020 |  | Routine/Scheduled |  | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Pump | Distribution Box |  | None |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Recirculation Pump","Sludge/Scum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Recirculation Pump","Sludge/Scum Accumulation"] | N/A |  |  | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 08/05/2020 | Jan 1 1900 11:15AM
09/08/2020 |  | RoutineScheduled | 187070087 | Warren | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Lord Fairfax | Onsite Wastewater Services - May Supply | 1942001627 | Drew | Shull | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/28/2021 | 05:41 AM
04/29/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/14/2021 | 04:27 PM
03/04/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Puraflo |  |  |  |  | None |  | ["Effluent Screens"] | ["Effluent Screens"] | [18 empty] | [Comments]: Puraflo peat - GoodPump 1 Amps 13.93 ETM 141h 31m Cycles 14792Pump 2 Amps 14.45 ETM 138h 05m Cycles 14922Septic Sludge 7" Scum 0Pump Sludge 3" Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/04/2020 | Jan 1 1900 4:31PM
10/01/2020 |  | RoutineScheduled | 177-08-0015-SWP | Spotsylvania | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Effluent Screens"] | ["Effluent Screens" ,"Attached Growth Medium"] | YES | [15 empty] | Will be sent separately | Inspected | Roots are growing into the Puraflo Modules. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/09/2021 | 03:25 PM
06/25/2020 |  | RoutineScheduled | 195-Discharge-30134 Aistrop Road | Washington | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Mount Rogers | S.E.P.T.I.C., Inc. |  | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Effluent Screens"] | ["BlowerCompressorAerator Operation","Control Operation","Effluent Screens","Disinfection"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
07/11/2020 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Gravity | Gravity |  | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | A walk over inspection was done on a convention gravity. Realtor requested a walk over inspection. The septic tank was dug up it was 6" under the ground. The tank was pumped out and inspected and was found in good condition. The drain field was probed and dry. At time of inspection it appears the septic system is in working condition | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 |  | 04/14/2021 | 04:27 PM
09/04/2020 |  | Follow-Up | 179-08-0212-SP | Stafford | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Bio Barrier | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Installed junction box in tank to prevent gasses from deteriorating panel. Chemically treated Fast unit and cleaned media. Pump out of septic tank and pump tank by others. Refilled with clean water to proper level. Resealed outlet pipe on pump tank. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
07/30/2020 |  | RoutineScheduled | 07-113-124 | Buchanan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Effluent Screens"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
09/19/2020 |  | RoutineScheduled | 139-06-145 | Page | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | dovel enterprises |  | jerry | dovel | 2.000000 | 1000 | 1000 |  | Pump | Pressure | Drip |  |  | [] | [] | YES | Septic | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 10/09/2020 | 12:00 AM
07/28/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | SES MidAtlantic LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/15/2021 | 09:00 AM
07/03/2020 |  | Initial Visit | 03-143-0199 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Henrico | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | Puraflo |  | Gravity | None | Aggregate Bed | None | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | [17 empty] | Septic tank pumped empty to facilitate peatmoss biofilter replacement. Initial visit - service conducted. Septic tank concrete riser access is severely degraded - requires replacement - did not open for evaluation and service due to condition. Pump tank in normal operating level - found evidence of infiltration at base of riser access. Discharge pump, float sensors and controls operating properly. Peatmoss Biofilter is severely degraded - requires replacement - severe ponding evident. No indications of surfacing at absorption bed. 08/20/2020 - Peatmoss Biofilter replacement conducted. Control panel replaced with new Orenco S1 Controls, new plastic riser installed on primary septic tank (concrete crock/lid removed) | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 08/27/2020 | 07:30 AM
05/27/2020 |  | Initial Visit | 264-18-245 | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chesapeake | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [9 empty] | 4.000000 |  | 1.000000 | [5 empty] | Serviced system. Checked the pump, panel, & floats (ok). Cleaned the filter and the diffuser in the Clearstream, cleaned the disc filter in the Clearstream, and cleaned the UV light bulb (Norweco UV unit). Changed the filter in the aerator. The septic tank needs additional risers on it so it can be inspected in the future. The return line is above the ground (needs to be addressed). This needs to be covered by soil or lowered above grade. The timer is set to 8 minutes every 2 hours. Took initial BOD & Fecal samples. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 05/27/2020 | Jan 1 1900 12:00PM
09/29/2020 |  | Reportable Incident | 2014-143-0137 | Henrico | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Henrico | Old Dominion Onsite, Inc. | 1942001549 | Russell | Revis | [9 empty] | ["Control Operation"] | ["Control Operation"] | N/A | [17 empty] | Control panel appears to have had its software wiped. Reinstalled software, system appears to have returned to normal function. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 09/29/2020 | 12:45 PM
11/30/2020 |  | RoutineScheduled | 2003-143-0182 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C&W Hanover Septic | 1942001281 | William | Shaw |  |  | EcoFlo | [6 empty] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 01/04/2021 | 12:00 AM
09/05/2020 |  | Reportable Incident |  | Chesapeake | This AOSS should now return to normal function after having provided the above state routine maintenance | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU | [6 empty] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation"] | N/A | [17 empty] | Replaced pump relay and aerator Replaced UV control panel | This AOSS should now return to normal function after having provided the above state routine maintenance |  | 10/13/2020 | Jan 1 1900 4:30PM
04/16/2020 |  | Reportable Incident | 04-142-0511 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1500 | Orenco Advantex |  | Pump | Gravity | Trenches | Not Applicable | 600.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump","Septic Tank Baffles","Sludge/Scum Accumulation"] | NA | Musty | Clear | [15 empty] | Pumped processing tank to effect repairs. Replaced damaged surge box with 10' of 4" PVC piping - replaced crushed header lines with new. Replaced damaged building sewer with new. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 04/27/2020 | Jan 1 1900 9:00AM
05/11/2020 |  | Routine/Scheduled | 17-118-0001 | Charles City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chickahominy | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. |  |  | Clearstream ATU |  | Pump |  |  |  |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 05/11/2020 | Jan 1 1900 2:30AM
11/16/2020 |  | Follow-Up |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | D-box was parge | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/14/2021 | 04:27 PM
09/30/2020 |  | RoutineScheduled | SP-04-669 | Spotsylvania | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation" ,"Distribution Pump Operation" ,"Attached Growth Medium" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation"] | ["Attached Growth Medium" ,"Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | NA | [15 empty] | Will be sent separately | Inspected | We recommend mowing the drip dispersal area and maintaining in a mowed condition. | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 |  | 04/09/2021 | 03:25 PM
05/14/2020 |  | Routine/Scheduled | 13-174-0056 | Prince George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Crater | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. |  |  | Norweco Singulair ATU |  | Pump | Drip |  |  |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 05/14/2020 | Jan 1 1900 2:00AM
07/24/2020 |  | RoutineScheduled | 069-17-0033 | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | Combs Wastewater Management LLC | 1942001353 | Amy | Combs | 2.000000 | 1500 |  | Norweco | Pump | Pressure | Drip | Not Applicable | 450.000000 | [] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | YES | None | [17 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 PM
10/20/2020 |  | RoutineScheduled |  | Fauquier | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Rappahannock-Rapidan | Soils, Inc. | 1942001004 | Markham | Smith | 2.000000 | 1500 | MicroFAST 0.50 in a Hanover 1500 top seam tank |  | Pump | Gravity | Trenches | Not Applicable | 65.620000 | [] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Septic Tank Baffles","Control Operation","SludgeScum Accumulation"] | YES | [17 empty] | PuroFlo pods are saturated | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 10/09/2020 | 07:00 AM
12/18/2020 |  | RoutineScheduled | 175-02-0293 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Prince William | Dominion Septic, Inc | 1942001125 | Tom | Jackson |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation" ,"Distribution Pump Operation" ,"Level Sensor Operation" ,"Recirculation Pump" ,"SludgeScum Accumulation"] | ["Distribution Pump Operation" ,"Level Sensor Operation" ,"Recirculation Pump" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Routine inspection. Advantex recirc tank needs pumped. Owner to make arrangements. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
05/09/2020 |  | RoutineScheduled | 175-09-0136 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Wastemaster | 1965-001817 | Tim | Jenkins | 2.000000 |  |  | Polishing Sandfilter | Pump |  | Discharge | UV |  | [] | [] |  | Musty | Clear | 6.800000 | [14 empty] | Recommend Pumping out ATU. Recommend replacing sprinkler heads | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 05/09/2020 | 10:30 AM
01/10/2020 |  | Routine, Scheduled | 04-137-0189 | Goochland County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chickahominy | Mathews Soil Consultants, Inc. | 1942001521 | Jason | Mathews |  |  | Orenco Advantex | None | Pump |  |  |  |  | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Dispersal System Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Auxiliary Filter","Control Operation","Dispersal System Operation","Recirculation Pump"] | [18 empty] | [Comments]: The treatment system will need to pumped out at next year’s service.The logo unit in the control panel appears to be working intermittently and may need to be replaced in the future. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/03/2020 | Jan 1 1900 6:47AM
08/13/2020 |  | Routine, Scheduled | 175-18-0388 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Biomicrobics MicroFAST |  | Pump | Drip | Drip Tubing | UV Light |  | ["Blower/Compressor/Aerator Operation","Level Sensor (Float) Operation"] | ["Blower/Compressor/Aerator Operation"] |  | Good | Good | [15 empty] | Needs timer float. Spin filter cleaned. Pump Amps 10.16 ETM 151 hrs Cycles 1383 Water Meter Reading 52260 Septic Sludge 8" Scum 3" ATU Sludge 13" Scum 0 Pump Sludge 0 Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 08/13/2020 | 03:25 PM
12/18/2020 |  | RoutineScheduled | 175-09-0307 | Prince William | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Prince William | Dominion Septic, Inc | 1942001068 | David | Stewart |  |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Recirculation Pump" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Control Operation" ,"Attached Growth Medium" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Level Sensor Operation"] | ["Attached Growth Medium" ,"Control Operation" ,"Septic Tank Baffles" ,"SludgeScum Accumulation" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Recirculation Pump"] | YES | [15 empty] | Will be sent separately | Inspected | Grease clog in inlet tee; we cleared. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
04/15/2020 |  | RoutineScheduled |  | Shenandoah | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter"] | ["Control Operation" ,"Auxiliary Filter"] | NA | [7 empty] | 04/15/2020 |  | 50.000000 | [5 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/26/2021 | 09:04 AM
07/29/2020 |  | Reportable Incident |  | Isle Of Wight | This AOSS should now return to normal function after having provided the above state routine maintenance | Pending Payment | EHD - Western Tidewater | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | None | None | Gravity | Distribution Box | Aggregate Trench | None | 450.000000 |  | ["Dispersal System Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | [17 empty] | Septic tank pumped by Goodman's septic service to facilitate repairs. Install - Maintenance/Repair Replaced conveyance line with new 4" PVC Replaced distribution box with new 8 port concrete Replaced / spliced header lines with 4" PVC | This AOSS should now return to normal function after having provided the above state routine maintenance |  | 08/07/2020 | Jan 1 1900 7:15AM
05/13/2020 |  | RoutineScheduled |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 | Pending Payment | EHD - Loudoun | WasteMaster, Inc. | 1942001062 | Tim | Jenkins | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 |  | 06/21/2021 | 10:37 AM
05/06/2020 |  | RoutineScheduled | 187-16-0380 | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Combs Wastewater Management | 1942001217 | Gabriel | Fahnestock | 2.000000 | 1500 |  | Norweco Singulair | Pump | Pressure | Drip | Not Applicable | 450.000000 | ["Effluent Screens","Dispersal System Operation","Control Operation","BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation","Control Operation","Effluent Screens","Dispersal System Operation"] | true | None | Dark Brown | [14 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 05/20/2020 | 09:00 AM
12/09/2020 | Alternative | RoutineScheduled | 166-15-100 | Northumberland | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | Church View Septic Service Inc. | 1942001302 | Charles | Langford | 1.000000 | 1500 | Aquasafe | Aquasafe | [5 empty] | [] | ["Auxiliary Filter"] | [18 empty] | System is overloaded due to excess rain. Checked all tanks for leaks and resealed some areas of concern. Its just a very wet area. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12/21/2020 | 12:00 AM
01/28/2020 |  | Routine, Scheduled | 13-120-0079AR | Chesterfield | This AOSS should now return to normal function after having provided the above stated routine maintenance. | Approved | EHD - Chesterfield | Old Dominion Onsite, Inc. |  | Jason | Hackler | 1.000000 | 1000 | Aquaworx Remediator |  | Gravity | Distribution Box | Aggregate Trench | None |  | ["Attached Growth Medium","BlowerCompressorAerator Operation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation"] | [18 empty] | [Comments]: Replaced bugs and filter. Water level is up in riser. System may need pump out in next 6 months. Extension cord unplugged upon arrival. Recommend hard wiring the aerator. Lab results not reported by Operator, EHS chose "No" in order to allow saving updated entry. | This AOSS should now return to normal function after having provided the above stated routine maintenance. |  | 01/28/2020 | Jan 1 1900 1:16PM
10/27/2020 |  | Follow-Up | 061-STS-21344 | Fauquier | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [7 empty] | 10/27/2020 |  | 10.000000 | [5 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
08/06/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 | Pending Payment | EHD - Loudoun | Great Falls Septic Service, Inc | 1942001301 | Josh | Hott | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Need to install 3 distribution boxes. | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 |  | 04/27/2021 | 11:51 AM
12/09/2020 | Alternative | Routine/Scheduled | 171-13-0065 | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | POWELLS PLUMBING, INC. | 1942001036 | Kurt | Holthaus | 1.000000 | 1250 | Microfast |  | Pump | Distribution Box | Aggregate Trench |  | 450.000000 | ["Blower/Compressor/Aerator Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | Annual Inspection - Pumped septic tank and serviced blower. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12/29/2020 | 01:50 PM
09/24/2020 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump | Drip | Elevated Sand Mound | UV Light |  | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  |  | 6.530000 | 6.100000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 09/24/2020 | Jan 1 1900 7:00AM
09/17/2020 | Alternative | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | McKim Construction | 1942001330 | Michelle | McKim | 3.000000 | 1500 | 1500 pump tank | 1250 pump tank | Pump | Gravity | Trenches | Not Applicable |  | [] | ["Control Operation","Distribution Pump Operation","Dispersal System Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 10/26/2020 | Dec 30 1899 9:30AM
03/03/2020 |  | Routine, Scheduled | 179-13-0067-SWP | Stafford County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001350 | Mike | Cook |  |  | Orenco Advantex | None | Pump | Drip | Drip Tubing |  |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/18/2020 | 06:42 AM
09/30/2020 |  | RoutineScheduled |  | Augusta | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation" ,"Recirculation Pump"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation" ,"Recirculation Pump"] | NA | [15 empty] | Will be sent separately | Inspected | Repaired recirc pump supply Replaced audible alarm | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance |  | 04/26/2021 | 09:04 AM
02/25/2020 |  | Follow-Up | 099-18-0080 SWP | King George County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001350 | Mike | Cook | 1.000000 |  | Biomicrobics MicroFAST | None | Gravity | Distribution Box | [15 empty] | 12.000000 | [8 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/03/2020 | 11:00 AM
10/27/2020 |  | RoutineScheduled | {FIPSCode}-STS-23623 | Scott | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | JET |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Effluent Screens"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
06/09/2020 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten | [9 empty] | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  |  | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 06/09/2020 | Jan 1 1900 9:00AM
09/25/2020 |  | RoutineScheduled | SWP-05-188 | Stafford | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Ecoflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation" ,"Level Sensor Operation"] | ["Level Sensor Operation" ,"Distribution Pump Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Septic filter housing is cracked/fatigued from lack of support. Monitor for now. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
06/23/2020 |  | Routine, Scheduled | 175-17-0518 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Biomicrobics MicroFAST |  | Pump | Drip | Drip Tubing | None |  | ["Blower/Compressor/Aerator Operation"] | ["Blower/Compressor/Aerator Operation"] |  | Good | Clear | [15 empty] | Spin filter cleaned. Pump Amps 7.58 ETM 198 hrs 06 mins Cycles 1088 Water Meter Reading 55600 Septic Sludge 14" Scum 2" ATU Sludge 15 " Scum 0 Pump Sludge 1" Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 06/23/2020 | 12:30 PM
07/14/2020 |  | Initial Visit | 124-STS-2379 | Hanover | This AOSS should now return to normal function after having provided the above state routine maintenance | Rejected | EHD - Chickahominy | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | Delta Environmental Products, UC Series | None | Pump | Drip | Drip Tubing | None | 450.000000 |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | NA | Pungent | Discolored | [15 empty] | Alarm event called in 07/10/2020 - found aeration compressor had failed - scheduled return visit to replace. 07/14/2020 - new GAST blower installed. Septic tank in normal operating level Processing tank in normal operating level - aeration re-established. Discharge tank in normal operating level - serviced discharge pump. Drip headworks serviced - drip screen serviced. | This AOSS should now return to normal function after having provided the above state routine maintenance |  | 07/16/2020 | Jan 1 1900 12:30PM
08/20/2020 |  | RoutineScheduled | 69140316 | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Greenway Engineering | 1942001008 | Jeremy | Ferguson | 1.000000 | 1500 | Microfast | none | Pump | Pressure | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | [18 empty] | blower panel replaced and has been pumped out now approved. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 09/24/2020 | 10:00 AM
08/10/2020 |  | Routine, Scheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Biomicrobics MicroFAST |  | Pump | Drip | Drip Tubing | UV Light |  | ["Blower/Compressor/Aerator Operation"] | ["Blower/Compressor/Aerator Operation"] | [18 empty] | ATU needs pumping. Spin filter cleaned. Pump Amps 8.26 ETM 752 hrs 5 mins Cycles 4554 Water Meter Reading 266700 Septic Sludge 11" Scum 3" ATU Sludge 20" Scum 0 Pump Sludge 2" Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 08/10/2020 | Jan 1 1900 2:30PM
09/16/2020 |  | RoutineScheduled | SWP-04-543 | Stafford | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Rappahannock | Battlefield Soil And Septic LLC | 1942001084 | Josh | Johnston | 1.000000 | 1250 | Puraflo |  | Pump | Gravity | Trenches | Not Applicable | 300.000000 | [] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Effluent Screens"] | YES | Musty | Dark Brown | [16 empty] | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 09/22/2020 | 12:00 AM
01/15/2020 |  | RoutineScheduled | 06-113-051 | Buchanan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | DEEL, DENNY M | 1942001097 | DENNY | DEEL |  |  | Norweco Singulair ATU | None | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens"] |  | Musty | Clear | [15 empty] | [Comments]: Installs Own Tablets | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 02/05/2020 | Jan 1 1900 4:19PM
07/22/2020 |  | RoutineScheduled | SD-06-072 | Orange | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Wastemaster Inc |  | Timothy | Jenkins | 2.000000 |  | ATU |  | Gravity | Gravity | Discharge | Chlorination |  | ["SludgeScum Accumulation"] | [] |  | Musty | Clear | 7.100000 |  |  | 1.800000 | [11 empty] | Recommend having system pumped out due to thick scum layer. EHS entered visit from data history | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 02:40 PM
10/24/2020 |  | RoutineScheduled |  | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Rappahannock-Rapidan | Wastemaster Inc |  | Timothy | Jenkins | 2.000000 |  | ATU |  |  | Gravity | Discharge | Chlorination |  | [] | [] |  | Musty | Clear | 7.200000 |  |  | 2.200000 | [12 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 11/06/2020 | 11:25 AM
07/11/2020 |  | RoutineScheduled | 109-12-0345 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1000 | Advantex |  | Gravity | Gravity | Trenches |  |  | ["None"] | ["None"] | [18 empty] | 6" of solids in septic tank. Flushed treatment unit spray manifold. Cleaned septic tank filter. Tested floats, pump and alarm. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 09/29/2020 | 07:03 PM
11/02/2020 |  | RoutineScheduled | 2015-143-0069 | Henrico | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Henrico | C & E Mechanical Corporation |  | Louis | Timberlake | 1.000000 | 1000 | EcoPod |  | Pump | Gravity | Pad |  |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["SludgeScum Accumulation","Distribution Pump Operation","Level Sensor Operation","Effluent Screens","Dispersal System Operation","Control Operation","BlowerCompressorAerator Operation"] | YES | [16 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12/03/2020 | 02:20 PM
06/25/2020 | Alternative | Routine/Scheduled | 38086 | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | POWELLS PLUMBING, INC. | 1942001036 | Kurt | Holthaus | 1.000000 | 1000 |  |  | Pump | Manifold | Aggregate Trench |  | 450.000000 | ["Effluent Screens"] | ["Effluent Screens"] | N/A | [17 empty] | Annual Inspection - Serviced effluent screen(s). | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 06/26/2020 | 01:21 PM
06/03/2020 |  | RoutineScheduled | SP-04-246 | Stafford | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump" ,"Attached Growth Medium" ,"Auxiliary Filter"] | ["Effluent Screens" ,"Recirculation Pump" ,"Distribution Pump Operation" ,"Attached Growth Medium" ,"Auxiliary Filter"] | YES | [15 empty] | Will be sent separately | Inspected | We recommend replacing two Orenco lids on the the Septic Tank, the Advantex Pod Vent, the broken LB box on the Recirculation Tank and the psi gauge in the Headworks Box. We would also recommend replacing the fabric for the Advantex System. | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 |  | 04/09/2021 | 03:25 PM
12/22/2020 |  | RoutineScheduled | 195-Discharge-14227 Peaceful Valley Rd. | Washington | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Mount Rogers | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Effluent Screens"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
04/16/2020 |  | Routine, Scheduled | SD-05-120 | Fauquier County | This AOSS should now return to normal function after having provided the above stated routine maintenance. | Approved | EHD - Rappahannock-Rapidan | JENKINS, TIMOTHY R | 1942001062 | TIMOTHY | JENKINS | 1.000000 |  | Aero-flo ATU | Sandfilter, Non-recirculating | Pump | Drip | Alternative Discharge | Chlorine |  | ["Recirculation Pump","SludgeScum Accumulation"] | ["None"] | [18 empty] | [Pumpout Comments]: System Requires Pumping [Comments]: No Discharge ATU Airline was rubbed thru on concrete edge. Temporary repair with duct tape. System Requires Pumping, | This AOSS should now return to normal function after having provided the above stated routine maintenance. |  | 04/23/2020 | 12:20 PM
03/30/2020 |  | Routine, Scheduled | 04-192-221 | Tazewell County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Cumberland Plateau | DEEL, DENNY M | 1942001097 | DENNY | DEEL |  |  |  | None | Gravity | None | Alternative Discharge | Chlorine | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens"] |  | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/30/2020 | Jan 1 1900 5:03PM
01/28/2020 |  | Routine, Scheduled | 11-120-0314A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesterfield | Madison Environmental LLC |  | Larry | Madison, Jr. |  |  | Bionest |  | Pump |  |  |  |  | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | [18 empty] | Lab results not reported by Operator, EHS chose "No" in order to allow saving updated entry. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/28/2020 | Jan 1 1900 12:00PM
03/30/2020 |  | RoutineScheduled | 185-STS-17514 | Tazewell | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. |  | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
08/17/2020 | Alternative | Reportable Incident | 151-09-0169 | Lancaster | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Three Rivers | obsidian onsite services |  | joel | pinnix | [9 empty] | [] | ["Other"] | [18 empty] | High wate alarm - all components normal. Maybe due to excess rain events. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  |  | 12:00 AM
01/07/2020 |  | Follow-Up |  | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Ashleys Septic Service | 1930332 | Shane | Majewski | 1.000000 | 750 |  |  | Pump | Gravity | Drip | UV | 450.000000 | ["Distribution Pump Operation"] | ["Distribution Pump Operation"] | NA | [16 empty] | Pumped Out | (Microfast system with Textile Filter/ Work done: January 6/20- replace #1 Pump. Feb 4 replace all Floats, June 10 - Replace UV Light/ Fix 90% pipe in Dist box, Put little air pump in Sample box, Fix leak in pump tank around incoming and outgoing pipe | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 09/01/2020 | Jan 1 1900 12:00AM
12/16/2020 |  | RoutineScheduled | VAG408413 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Central Shenandoah | Onsite Wastewater Services - May Supply | 1942001627 | Drew | Shull | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | None | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/17/2022 | 06:40 AM
11/11/2020 |  | Routine, Scheduled | 175-05-0536 | Prince William | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Approved | EHD - Prince William | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Delta Environmental Products, DF Series |  |  |  |  | None |  | ["Blower/Compressor/Aerator Operation"] |  |  | Acceptable | Clear | [15 empty] | Compressor is bad. Replaced lid on septic tank 11/10/2020. Pump Amps 12.50 ETM 210.05 Cycles 2190 Septic Sludge 13" Scum 1" ATU Sludge 16" Scum 0 Pump Sludge 0 Scum 0 | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 11/11/2020 | 02:35 PM
10/19/2020 |  | RoutineScheduled | 13-142-0223 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | GeoEnvironmental Services, Inc. | 1942001010 | Peter | Mamunes | 1.000000 | 1000 | Elgin Sandfilter |  | Pump | Pressure | Mound |  |  | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","SludgeScum Accumulation","Level Sensor Operation"] | ["Control Operation","Dispersal System Operation","Distribution Pump Operation","SludgeScum Accumulation","Level Sensor Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 10/26/2020 | Jan 1 1900 3:45PM
06/23/2020 |  | RoutineScheduled | 107-03-0565 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Onsite Wastewater Services - May Supply | 1942001022 | Sara | Tusing | 1.000000 |  | Orenco Advantex | none | Pump | Gravity |  | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | inspection Ds | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 05/28/2021 | 05:41 AM
02/17/2020 |  | Routine, Scheduled | 093-05-0421 | Isle of Wight County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Western Tidewater | R & K Septic, Inc. |  | Craig | Van Holten |  |  | Orenco Advantex |  | Pump |  |  | None |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/17/2020 | Jan 1 1900 4:00PM
03/27/2020 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump | Drip | Elevated Sand Mound | UV Light |  | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  | 9.27 | 7.770000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/27/2020 | Jan 1 1900 1:00PM
04/15/2020 |  | Routine, Scheduled | 06-142-0078 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chickahominy | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Ecoflo | None | Pump | Distribution Box | Trenches | Not Applicable |  | ["Attached Growth Medium","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["Attached Growth Medium","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [18 empty] | [Comments]: The effluent filter (inside piece is broken). Peat will need to be replaced possibly within the next year. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/27/2020 | Jan 1 1900 4:14AM
07/01/2020 |  | RoutineScheduled | 061-STS-24498 | Fauquier | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Level Sensor Operation"] |  | NA | [15 empty] | Will be sent separately | Inspected | Flow rates for both pumps are much slower than design. Lines apparently have never been flushed and re-balanced. Balancing (globe) valves need to be taken apart and cleaned. If flow rates don't improve substantially, the pumps should be replaced (24 years old). Concrete lid for pump tank is rotten and cracked, needs replaced. Eventually found 10 caps for lateral ends (3 covered by sod). Not sure if these 10 include 2 new lines proposed back in 1996 when LPD malfunctioned. Float switches are very old and still functioning, but set at about 2" apart. Plans called for a 15" drawdown. Dose may have been reduced to help alleviate the malfunction. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
06/23/2020 |  |  | 12-113-145 | Buchanan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel | [9 empty] | [] | [] | [8 empty] | 06/23/2020 |  | 19.200000 |  |  | 1.000000 |  |  |  |  | SYSTEM WILL NOT ALLOW ATTACHMENTS TO BE UPLOADED | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
04/08/2020 |  | Routine/Scheduled |  | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Pump | Distribution Box |  | None |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Recirculation Pump","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Recirculation Pump","Sludge/Scum Accumulation"] | N/A |  |  | 7.000000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/08/2020 | Jan 1 1900 2:30PM
12/17/2020 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Whitewater ATU |  | Pump |  |  |  |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  |  | 7.260000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 12/17/2020 | Jan 1 1900 8:00AM
09/14/2020 |  | Routine/Scheduled | 136-05-0845 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | Puraflo |  | Pump | None | Aggregate Bed | None | 450.000000 |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | Musty | Clear | [15 empty] | Routine service Septic tank - normal operating level - effluent screen serviced. Pump Tank - normal operating level - pump, float sensor and controls operating properly PuraFlo Modules - FOUR - peatmoss biofilter replaced 2019 - good condition - raked / turned all four modules. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 09/15/2020 | 02:00 PM
03/03/2020 |  | Routine, Scheduled | 12-142-0048 | Hanover County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chickahominy | Madison Environmental LLC |  | Larry | Madison, Jr. |  |  | Biomicrobics MicroFAST |  | Pump |  |  |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/03/2020 | Jan 1 1900 9:30AM
09/01/2020 |  | Routine/Scheduled | 17-120-0498A | Chesterfield | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chesterfield | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. |  |  | Clearstream ATU |  | Pump |  |  |  |  | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 09/01/2020 | Jan 1 1900 11:00AM
12/15/2020 |  | Routine/Scheduled |  | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Pump | Distribution Box |  | None |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Recirculation Pump","Sludge/Scum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Recirculation Pump","Sludge/Scum Accumulation"] | N/A |  | 5.61 | 6.540000 | 4.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 12/22/2020 | Jan 1 1900 10:00AM
07/20/2020 |  | RoutineScheduled | 033-12-0067-SWP | Caroline | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | EZ Treat Sandfilter | none | Pump | Gravity | Drip | Not Applicable |  | ["Attached Growth Medium" ,"Auxiliary Filter" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump" ,"Dispersal System Operation" ,"SludgeScum Accumulation"] | ["Attached Growth Medium" ,"Auxiliary Filter" ,"Effluent Screens" ,"Recirculation Pump" ,"Dispersal System Operation" ,"Distribution Pump Operation"] | YES | [15 empty] | Will be sent separately | Inspected | The EZ Set riser & lid on the Septic Tank are damaged and should be replaced. We recommend pumping the Septic Tank & the Clarifying Tank due to to scum & sludge accumulation. The high level float was not working properly and has been replaced. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/09/2021 | 03:25 PM
07/07/2020 |  | RoutineScheduled | XS-98-511 | Stafford | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001068 | David | Stewart | 1.000000 |  | Puraflo | none | Pump | Gravity | Pad | Not Applicable |  | ["Control Operation" ,"Attached Growth Medium" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Level Sensor Operation" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | ["Effluent Screens" ,"Level Sensor Operation" ,"Control Operation" ,"Distribution Pump Operation" ,"Attached Growth Medium" ,"Septic Tank Baffles" ,"SludgeScum Accumulation"] | YES | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
04/09/2020 |  | RoutineScheduled | 10-142-0081 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Chickahominy | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | [10 empty] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | NA | [17 empty] | At the time of maintenance, the service expert reported that all components were functioning properly and the system was operational. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 04/09/2020 | Jan 1 1900 10:29AM
01/13/2020 |  | Initial Visit | 099-STS-86749 | King George County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson |  |  | Orenco Advantex | None | Pump |  |  |  |  | ["Control Operation"] | ["Control Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/15/2020 | 10:52 AM
05/11/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | Norweco Singulair ATU | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | The distribution box is holding the correct level, but has a substantial amount of cracks. The homeowner is contacting contractors for repair. | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 |  | 05/27/2021 | 01:26 PM
10/24/2020 |  | RoutineScheduled | 047-19-138 | Culpeper | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock-Rapidan | Wastemaster Inc |  | Timothy | Jenkins | 2.000000 |  | Recirculating Sand Filter |  | Pump | Gravity | Discharge | Chlorination |  | [] | [] |  | Musty | Clear | 6.700000 |  |  | 1.800000 | [12 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 11/06/2020 | 11:25 AM
03/24/2020 |  | Routine, Scheduled |  | Loudoun County | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements | Paid | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | None | None | Pump | Manifold | [23 empty] | [Comments]: septictank and pump tank need pumped out | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements |  | 04/12/2020 | 02:21 PM
11/20/2020 |  | Routine/Scheduled | 06-177-1036 | Pulaski | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Biomicrobics MicroFAST |  | Pump | Distribution Box |  | None |  | ["None"] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 11/20/2020 | 02:00 PM
05/11/2020 |  | Follow-Up |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 2.000000 |  | Biomicrobics MicroFAST | Biomicrobics MicroFAST | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Replaced lid on microfast and replaced the 4x4 electric box | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/14/2021 | 04:27 PM
01/14/2020 |  | Routine, Scheduled | 04-142-0110 | Hanover County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chickahominy | SHAW, WILLIAM A, JR. | 1934000449 | WILLIAM | SHAW |  |  | Septic Tank Only | Septic Tank Only | None | None | None | None |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/14/2020 | Jan 1 1900 1:37PM
04/10/2020 |  | Routine, Scheduled |  | York County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Peninsula | Madison Environmental LLC | 1934 000061 | Larry | Madison, Jr. |  |  | Whitewater ATU |  | Pump | Distribution Box |  |  |  | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Level Sensor Operation","Septic Tank Baffles","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/10/2020 | Jan 1 1900 1:00AM
01/16/2020 |  | Routine, Scheduled |  | Loudoun County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | None | Pump | Distribution Box | Aggregate Trench | [22 empty] | [Comments]: pod 4 and 5 need the drain lines unclogged | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/02/2020 | 04:43 AM
05/07/2020 |  | Reportable Incident | 196-05-573 | Westmoreland | This AOSS should now return to normal function aft | Approved | EHD - Three Rivers | [13 empty] | ["Recirculation Pump"] | ["Recirculation Pump"] | [19 empty] | This AOSS should now return to normal function aft |  |  | 12:00 AM
04/29/2020 |  | RoutineScheduled |  | Shenandoah | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  | ["Control Operation" ,"Auxiliary Filter" ,"Dispersal System Operation"] | ["Control Operation" ,"Auxiliary Filter" ,"Dispersal System Operation"] | NA | [7 empty] | 04/29/2020 |  | 11.000000 | [5 empty] | Will be sent separately | Inspected | Corrected timer settings in panel Repaired recirc pipe in pod | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance |  | 04/26/2021 | 09:04 AM
08/21/2020 |  | Initial Visit | 136-04-705 | Gloucester | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Three Rivers | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | Clearstream | None | Pump | Manifold | Aggregate Trench | None | 450.000000 |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | Pungent | Clear | [15 empty] | Initial Visit - Alarm Primary septic tank in normal operating level Aeration tank in normal operating level - compressor in alarm due to failed diaphragms - rebuilt on property - restored to proper operation. Discharge tank in normal operating level - pump, float sensors and controls operating properly. No indications of surfacing over LPP field. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 08/27/2020 | 09:00 AM
08/03/2020 |  | Reportable Incident |  | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU | [6 empty] | ["Blower/Compressor/Aerator Operation","Control Operation"] | ["Blower/Compressor/Aerator Operation","Control Operation"] | N/A | [17 empty] | Replaced aerator | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 08/03/2020 | Jan 1 1900 4:20PM
05/09/2020 |  | RoutineScheduled | 2050-03-153 | Prince William | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Prince William | Wastemaster | 1965-001817 | Tim | Jenkins | 2.000000 |  |  |  | Pump |  | Discharge | Chlorination |  | [] | [] |  | Musty | Clear | 7.900000 |  |  | 2.200000 | [11 empty] | HRS 814.26 CTS 37107 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 05/09/2020 | 10:00 AM
09/17/2020 |  | RoutineScheduled |  | Rockingham | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/26/2021 | 09:04 AM
12/07/2020 |  | Reportable Incident | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance | Approved | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green | [9 empty] | ["Dispersal System Operation"] | ["Dispersal System Operation"] | [18 empty] | Replaced 2 normally closed solenoids. | This AOSS should now return to normal function after having provided the above state routine maintenance |  | 12/07/2020 | Jan 1 1900 4:00PM
02/17/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Biomicrobics MicroFAST |  | Pump | Drip | Drip Tubing | None |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] |  | Good | Clear | [15 empty] | [Comments]: Spin filter cleaned.Pump 1 Amps 10.47Pump 2 Amps 10.58Water Meter Reading 320180Septic Sludge 5" Scum 2"ATU Sludge 10" Scum 0.50Pump Sludge 1" Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/17/2020 | Jan 1 1900 11:15AM
05/13/2020 |  | Reportable Incident | SWP-98-140 | Spotsylvania | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | none | none | Pump | Gravity | Drip | Not Applicable |  | ["Distribution Pump Operation" ,"SludgeScum Accumulation"] | ["Distribution Pump Operation"] | NA | [15 empty] | Will be sent separately | Inspected | High level alarm. Drip rate down to .1 gpm. Pump intake was completely clogged. Drip rate back to normal rates after cleaning intake and disc filters. Pump tank should be pumped out. Recommended installation of effluent filter in septic tank and a cool guide assembly in the pump tank. Replaced cord set on drip pump (insulation damaged). | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
08/24/2020 |  | RoutineScheduled | 04-197-A1 | Wise | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lenowisco | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | JET |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","Disinfection"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
07/30/2020 | Alternative | RoutineScheduled | 128-11-053 | Essex | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers |  |  | joel | pinnix | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
05/05/2020 |  | Follow-Up |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | SES MidAtlantic LLC | 1942001203 | James | Green | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Trenches | Not Applicable |  | ["Distribution Pump Operation"] | ["Distribution Pump Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced gasket in camlock. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/15/2021 | 09:00 AM
05/21/2020 |  | RoutineScheduled | SWP-05-353 | Stafford | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Recirculation Pump"] | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/09/2021 | 03:25 PM
06/15/2020 |  | RoutineScheduled | 069050306 | Frederick | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Rejected | EHD - Lord Fairfax | Greenway Engineering | 1942001008 | Jeremy | Ferguson | 1.000000 | 1500 | Microfast | none | Pump | Pressure | Mound | Not Applicable |  | ["BlowerCompressorAerator Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Level Sensor Operation","SludgeScum Accumulation"] | NA | [17 empty] | Needs pumped up | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. |  | 08/03/2020 | 03:40 PM
02/15/2020 |  | Reportable Incident | 177-11-0011-SP | Spotsylvania County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson |  |  | Orenco Advantex | None | Pump | Drip | Drip Tubing |  |  | ["Auxiliary Filter","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Auxiliary Filter","Control Operation","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | [Comments]: On site for high level alarm. Water level was within a few inches of all lids. Met pumped, removed recirc pump, floats, biotube filter and pump vault to facilitate pumping and to inspect tanks. Cleaned very dirty biotube filter and RSV. Observed steady flow of water into the discharge tank through the 2" inlet pipe. No water should have been flowing as the RSV was not yet reinstalled. Fiber optic camera showed what looked like roots at bullhorn connection. Need to uncover and inspect 2" piping starting at the RSV. Fimco zoner leaked a little during test cycle. Not enough to cause surfacing, but may need to be replaced. High level alarm float for discharge tank was stuck half way on. Suctioned out water from splice box and alarm float started working correctly. Advised owner that additional alarms will occur with rain until repairs are made. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/19/2020 | 05:59 AM
11/03/2020 |  | Routine/Scheduled | 085-STS-31789 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chickahominy | Miller’s Septic Service | 1942001063 | K.R. Trapper | Davis | 1.000000 | 1000 | Orenco Advantex |  | Pump | Distribution Box | Aggregate Trench | None | 450.000000 |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump","Septic Tank Baffles","Sludge/Scum Accumulation"] | N/A | None | Clear | [15 empty] | 180 day system inspection. Primary Septic Tank - normal operating level - effluent screen serviced. Processing Tank - recirc - media drapes serviced, spray grid serviced, recirc pump serviced. Processing Tank - Discharge - pump serviced - float sensors and controls operating properly. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 11/04/2020 | Jan 1 1900 7:15AM
12/11/2020 |  | RoutineScheduled | {FIPSCode}-STS-27740 | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Inboden Environmental Services, Inc | 1942001173 | Darrin | Plauger | [9 empty] | [] | [] |  | None |  | 8.010000 | 6.980000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12/21/2020 | 02:50 PM
10/13/2020 |  | RoutineScheduled | SD-13-115 | Culpeper | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock-Rapidan | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | none | none | Gravity | Gravity |  | UV |  | ["BlowerCompressorAerator Operation" ,"Attached Growth Medium" ,"Disinfection"] | ["Disinfection" ,"BlowerCompressorAerator Operation" ,"Attached Growth Medium"] | NA | [15 empty] | Will be sent separately | Inspected | Sample taken today. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/09/2021 | 03:25 PM
09/29/2020 |  | Routine/Scheduled |  | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump | Distribution Box | Aggregate Bed | None |  | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  |  | 7.000000 | 5.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 09/29/2020 | Jan 1 1900 9:45AM
04/30/2020 |  | RoutineScheduled |  | Fairfax | This AOSS is functioning as designed and in accord | Approved | EHD - Fairfax | Great Falls Septic Service | 1942001301 | Joshua | Hott | 1.000000 | 1500 |  | Puraflo | Pump | Distribution Box | Aggregate Trench | None | 500.000000 | ["Effluent Screens"] | ["Effluent Screens","None"] |  | Low | [17 empty] | This AOSS is functioning as designed and in accord |  |  | 12:00 AM
08/17/2020 |  | Follow-Up | 132-04-0198 | Fluvanna | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Blue Ridge | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Norweco Singulair ATU | none | Pump | Gravity | Drip | Not Applicable |  | ["Auxiliary Filter" ,"Distribution Pump Operation" ,"SludgeScum Accumulation"] | ["Distribution Pump Operation" ,"Auxiliary Filter" ,"SludgeScum Accumulation"] | NA | [15 empty] | Will be sent separately | Inspected | Pump tank in high level earlier in the day. Spin filter very dirty due to heavy sludge in tanks - installed new filter. Cleaned pump intake and installed 6" pump stand to protect pump from future sludge accumulations. Met Moore's Plumbing and Septic on site to oversee pump-out of both tanks. Note: Biokinetics filter housing is showing its age: screen is torn in several spots, inner rubber/foam grommet is torn, and one locking tab is missing. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
11/03/2020 |  | RoutineScheduled | 179-17-0410-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  | ["Attached Growth Medium" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump"] | ["Attached Growth Medium" ,"Distribution Pump Operation" ,"Effluent Screens" ,"Recirculation Pump"] | YES | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 |  | 04/09/2021 | 03:25 PM
07/13/2020 |  | RoutineScheduled | 109-13-0354 | Bedford | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central | The Creighton Companies, LLC | 1942001001 | J.J. | Keith | 1.000000 | 1500 | Delta, DF Series |  | Gravity | Gravity | Trenches |  |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | [18 empty] | 12" of solids in septic tank. 8" of solids in treatment unit. Cleaned blower air filter. Blower GFCI was tripped, reset. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 09/29/2020 | 07:03 PM
04/03/2020 |  | Initial Visit | S 800-18-0293 | Suffolk | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Western Tidewater | Farmer’s Septic Service, Inc. |  | Ross | Cole | 1.000000 | [8 empty] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [10 empty] | 44.000000 | [7 empty] | [Comments]: Owner called due to the alarm going off - they had a running toilet when we arrived. Serviced system. Checked the pump, panel, & floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. There is no riser on the inlet end of the pump tank - needs one. The timer is set to 2 minutes every 2 hours. Took initial BOD sample. NOTE: BOD lab was high - system should function properly after service. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/03/2020 | Jan 1 1900 12:00PM
01/18/2020 |  | Routine, Scheduled |  | Warren County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Lord Fairfax | DOVEL, JERRY A | 1942001116 | JERRY | DOVEL | 1.000000 |  | Biomicrobics MicroFAST | Septic Tank Only | None | Drip | None | None | [22 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/08/2020 | 07:17 PM
07/29/2020 |  | RoutineScheduled |  | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | Triple R Construction Co., Inc. | 1942001108 | Charles | Seamon | 2.000000 |  | Septic Tank | Pump Tank | Pump | Pressure | Drip | Not Applicable |  | ["Dispersal System Operation"] | [] | NO | [17 empty] | Septic Tank-7"sludge 0"scum/ Pump Tank-2"sludge (No pump out needed) Counts: Peak-00000/High-000016/ Water meter-183530.38 System needs 1"check valve for zone #2/ Recommend a Zoeller 5000 septic filter upgrade. Check Valve and filter fixed on 8/5/2020 | This AOSS should now return to normal function after having provided the above state routine maintenance. |  |  | 12:00 AM
07/15/2020 |  | RoutineScheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintanence requirements | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Splitter box broken and upper d-box is cracked | This AOSS is not functioning as designed or in accordance with the performance/maintanence requirements |  | 04/14/2021 | 04:27 PM
03/09/2020 |  | Routine, Scheduled | 175-03-0033 | Southampton County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Western Tidewater | R & K Septic, Inc. |  | Craig | Van Holten |  |  | Whitewater ATU |  | Pump | Distribution Box |  | None |  | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/09/2020 | Jan 1 1900 3:00PM
06/24/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Payment | EHD - Loudoun | Great Falls Septic Service, Inc | 1942001301 | Josh | Hott | 1.000000 |  | Biomicrobics MicroFAST | none | Gravity | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/27/2021 | 11:51 AM
01/06/2020 |  | Routine, Scheduled | 179-15-0168-SP | Stafford County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Orenco Advantex | None | Pump | Distribution Box | Aggregate Trench |  |  | ["Attached Growth Medium","Effluent Screens","None","Recirculation Pump"] | ["Attached Growth Medium","Effluent Screens","None","Recirculation Pump"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/04/2020 | 07:46 AM
09/24/2020 |  | RoutineScheduled | 110-Discharge-6299 Wilderness Rd. | Bland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Mount Rogers | S.E.P.T.I.C., Inc. | 1942001097 | Denny | Deel |  |  | NORWECO |  | Gravity | Gravity | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Effluent Screens"] | ["BlowerCompressorAerator Operation","Disinfection","Control Operation","Effluent Screens"] | YES | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
03/30/2020 |  | Routine, Scheduled |  | Loudoun County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | None | None | Pump | Manifold | [24 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/12/2020 | 02:21 PM
05/12/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Pad | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Air release valve on one mound is broken and has unregulated flow of effluent on surface. Offered to repair - waiting on homeowner response./ | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 |  | 05/27/2021 | 01:26 PM
02/19/2020 |  | Routine, Scheduled | {FIPSCode}-STS-1688 | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Virginia Beach | R & K Septic, Inc. |  | John | Butt, Jr |  |  |  |  | Pump | Distribution Box |  | None |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] |  |  |  | 7.250000 | 4.000000 | [13 empty] | [Comments]: Re-wired junction box. Replaced top float in pump tank. Connected conduit to junction box where it had broke. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/19/2020 | Jan 1 1900 2:00PM
12/16/2020 |  | Reportable Incident | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Ashleys Septic Service | 1930332 | Shane | Majewski | 1.000000 | 1500 | [7 empty] | ["BlowerCompressorAerator Operation"] | [] | NA | [17 empty] | Tree fell onto Pump Chamber- Replace Blower/Cover/ UV Lighting, Plastic lid | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12/02/2020 | Jan 1 1900 12:00AM
10/28/2020 |  | RoutineScheduled | 099-07-0153-SWP | King George | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Rappahannock | Wastemaster Inc |  | Timothy | Jenkins | 2.000000 |  | PuraFlo |  | Pump | Pressure | Pad |  |  | ["SludgeScum Accumulation"] | [] | [18 empty] | In for service and inspection. Peat in good condition with compaction to grid. No ponding or wet spots. Recommend pumping trash tank. Recommend cleaning brush from PuraFlo pods and drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 11/05/2020 | 11:15 AM
05/08/2020 |  | Routine/Scheduled | 08-160-0052 | Montgomery | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - New River | Advanced Environmental & Septic, LLC | 1942001042 | Rodney | Rice | 1.000000 |  | Delta Environmental Products, DF Series |  | Pump | Drip | Drip Tubing | None | 189.000000 | ["None"] | ["Blower/Compressor/Aerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 05/08/2020 | 10:15 AM
07/27/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton |  |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/27/2021 | 01:26 PM
05/26/2020 |  | RoutineScheduled | 179-15-0184-SWP | Stafford | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson |  |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
08/24/2020 |  | Follow-Up | 162-17-0019 | Nelson | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Blue Ridge | Virginia Septic Service | 1942001512 | iain | waugh | 3.000000 | 3000 | Norweco |  | Pump | Pressure | Discharge | UV |  | ["Disinfection"] | ["Disinfection"] | YES | None | Clear | 7.340000 | 5.200000 |  |  | 23.0 C | 08/24/2020 | Pump Chamber | 0.000000 |  | 24.000000 | 5.200000 |  |  | Attached to this report |  |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 09/08/2020 | 01:00 PM
06/18/2020 |  | RoutineScheduled | 181-11-0073 | Rockbridge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Hunter E. Ayres, General Contractor | 1942001166 | Hunter | Ayres | 1.000000 | 1500 | Ecopod |  | Pump | Pressure | Trenches | Not Applicable |  | ["Auxiliary Filter","Effluent Screens"] | ["Auxiliary Filter","Effluent Screens"] | YES | [16 empty] | Pumped Out | Filters checked and cleaned. Pump vault cleaned. No apparent leaks in system or drain field area. Control panels functioning properly. Lids properly secured. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 07/11/2020 | 08:35 AM
08/10/2020 |  | RoutineScheduled |  | Fairfax City | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Fairfax | Catoctin Environmental |  | Cameron | Creighton | 1.000000 | 1500 | Puraflo |  | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
03/05/2020 |  | Routine, Scheduled |  | Loudoun County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | Puraflo | None | Pump | Distribution Box | Aggregate Bed | [22 empty] | [Comments]: pt needs pumped out | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/12/2020 | 02:21 PM
12/15/2020 | Alternative | RoutineScheduled | 171-05-0270 | Shenandoah | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Lord Fairfax | Onsite Wastewater Services - May Supply | 1942001627 | Drew | Shull | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  |  | ["SludgeScum Accumulation"] | NA | None | Clear | [13 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/03/2022 | 01:33 PM
03/11/2020 |  | Routine, Scheduled |  | Loudoun County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | None | None | Pump | Manifold | [23 empty] | [Comments]: There is a greener area just off the manifold. It does not appear to be an issue. The area was probed and came back dry. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/16/2020 | 11:28 AM
11/04/2020 |  | RoutineScheduled | 182-03-0361 | Rockingham | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | [6 empty] | Fast | [6 empty] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Dispersal System Operation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 11/04/2020 | 12:00 AM
12/23/2020 |  | Routine/Scheduled | 124-STS-2379 | Fairfax | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Biomicrobics MicroFAST | [6 empty] | ["Blower/Compressor/Aerator Operation"] | ["Blower/Compressor/Aerator Operation"] | N/A | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 12/23/2020 | Jan 1 1900 11:14AM
02/03/2020 |  | Routine, Scheduled |  | Nelson County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Blue Ridge | ARNOLD, ARCHIE G | 1942001291 | ARCHIE | ARNOLD | 1.000000 | 500 | Aqua Safe ATU | Septic Tank Only | Pump | Drip | Drip Tubing | None | 150.000000 | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] |  | earthy | clear | [15 empty] | [Comments]: O&M: Cleaned disk filter, replaced air filter, flushed lines. Performed typical maintenance. System working as intended. 1’ sludge in ATU, 4" in pump tank. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/24/2020 | 11:00 AM
06/26/2020 |  | Routine/Scheduled |  | Warren | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Pending Review | EHD - Lord Fairfax | POWELLS PLUMBING, INC. | 1942001036 | Kurt | Holthaus | 1.000000 | 1000 | Microfast |  | Pump | Drip | Elevated Sand Mound |  | 450.000000 | ["Blower/Compressor/Aerator Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | Annual Inspection - Serviced blower, pumped Microfast and pump chamber. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 06/29/2020 | 12:11 PM
06/22/2020 |  | Routine/Scheduled |  | Loudoun | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. | Pending Review | EHD - Loudoun | POWELLS PLUMBING, INC. | 1942001036 | Kurt | Holthaus | 1.000000 | 1200 |  |  | Pump | Manifold | Aggregate Trench |  | 600.000000 | ["Control Operation","Distribution Pump Operation","Effluent Screens"] | ["Effluent Screens"] | N/A | [17 empty] | Annual Inspection - Need to replace junction box at pump chamber and 3" treaded gate valve inside the pump chamber. Serviced effluent screen(s). | This AOSS is not functioning as designed or in accordance with the performance/maintenance requirements. |  | 07/10/2020 | 01:12 PM
10/30/2020 |  | Initial Visit | 179-STS-87780 | Stafford | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001125 | Tom | Jackson |  |  | EZ Treat Sandfilter | none | Pump | Gravity | Trenches | Not Applicable |  | ["Control Operation"] | ["Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Groundwater leaking in at topseam on both long sides of the tank. Installer offered to go over entire top seam, inside and out, with hydraulic cement. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/13/2021 | 11:22 AM
06/16/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Pump to the modules was run for several minutes. There was no effluent observed coming into the modules through any manifolds | This alternative discharging system is not functioning as designed or in accordance with the performance /maintenance requirements of 12VAC5-640 |  | 05/27/2021 | 01:26 PM
12/10/2020 |  | Initial Visit | 179-STS-87360 | Stafford | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | START UP INSPECTION | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/09/2021 | 03:25 PM
07/22/2020 |  | RoutineScheduled | 179-12-0081-SWP | Stafford | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001060 | Rob | Martin | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens" ,"Attached Growth Medium"] | ["Effluent Screens" ,"Attached Growth Medium"] | YES | [15 empty] | Will be sent separately | Inspected | The second, third and fifth Puraflo modules are holding water. If this is not corrected, the peat will become saturated and will need to be replaced. We recommend excavating by machine to uncover the manifold and remove any blockages occurring. It may be necessary to install shut-off valves in the affected modules to allow them to dry. | This AOSS is functioning as designed and in accordance with the performance/Maintenance requirements of 12VAC5-613 |  | 04/09/2021 | 03:25 PM
04/21/2020 |  | RoutineScheduled | 69130156 | Frederick | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity |  | Not Applicable |  | ["SludgeScum Accumulation" ,"Control Operation" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter"] | ["Control Operation" ,"BlowerCompressorAerator Operation" ,"Auxiliary Filter" ,"SludgeScum Accumulation"] | NA | [7 empty] | 04/21/2020 |  | 149.000000 | [5 empty] | Will be sent separately | Inspected | All tanks are being pumped Installed rebuilt blower at time of service | This alternative discharging system should now return to normal function after having provided the above stated routine maintenance |  | 04/26/2021 | 09:04 AM
05/13/2020 | Alternative | Routine/Scheduled | 157-14-0135 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | Serviced system. Checked the pump, panel, & floats (ok). Cleaned the filter and the diffuser in the Clearstream and cleaned the filter in the aerator | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 05/13/2020 | 12:00 PM
01/19/2020 |  | Routine, Scheduled | SWP-04-496 & SWP-02-989 | Spotsylvania County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001350 | Mike | Cook |  |  | Orenco Advantex | None | Pump | Distribution Box | Aggregate Trench |  |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | [18 empty] | [Comments]: replaced motherboard,contactor,and h/l alarm float. proposal will be sent to clear drain field and examine problematic drain field.(wet spot) | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/28/2020 | 01:39 PM
07/01/2020 |  | Follow-Up |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | SES MidAtlantic LLC | 1942001203 | James | Green | 1.000000 |  | Puraflo | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [7 empty] | 07/01/2020 |  | 40.000000 | [5 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/15/2021 | 09:00 AM
06/24/2020 |  | RoutineScheduled | 177-STS-86798 | Spotsylvania | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Approved | EHD - Rappahannock | EcoSeptix Alliance | 1942001101 | Joe | Malloy |  |  | Orenco Advantex | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | 90-Day Inspection | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/09/2021 | 03:25 PM
09/12/2020 |  | Routine/Scheduled |  | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Pump |  |  |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Recirculation Pump","Sludge/Scum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Recirculation Pump","Sludge/Scum Accumulation"] | N/A |  |  | 7.000000 | 3.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 09/12/2020 | Jan 1 1900 9:30AM
07/15/2020 |  | RoutineScheduled | 196-07-214 | Westmoreland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers |  |  | joel | pinnix | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
05/12/2020 |  | RoutineScheduled | 107-09-0349 | Augusta | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Onsite Wastewater Services - May Supply | 1942001022 | Sara | Tusing | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 05/28/2021 | 05:41 AM
07/27/2020 |  |  | 069051337 | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 1942001325 | Larry | Royston | [9 empty] | ["None"] | ["None"] | YES | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 07/28/2020 | 12:00 AM
04/17/2020 |  | Routine, Scheduled | 2007-143-0091 | Henrico County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Henrico | [8 empty] | Pump |  |  |  |  | ["Attached Growth Medium","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | ["Attached Growth Medium","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","Recirculation Pump","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/17/2020 | 03:30 AM
03/31/2020 |  | Routine, Scheduled | 09-184-5003 | Scott County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Lenowisco | DEEL, DENNY M | 1942001097 | DENNY | DEEL |  |  | Norweco Singulair ATU | None | Gravity | None | Alternative Discharge | Chlorine |  | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens","SludgeScum Accumulation"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection","Effluent Screens"] |  | Musty | Clear | [15 empty] | [Comments]: 5 blue crystals | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/08/2020 | Jan 1 1900 11:04AM
06/12/2020 |  | Routine/Scheduled |  | Virginia Beach | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Virginia Beach | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Orenco Advantex |  | Pump | Distribution Box |  | None |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Recirculation Pump","Sludge/Scum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Recirculation Pump","Sludge/Scum Accumulation"] | N/A |  | 4.32 | 7.350000 | 5.600000 | [13 empty] | Replaced 3 floats | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 06/12/2020 | Jan 1 1900 8:30AM
03/03/2020 |  | Routine, Scheduled | SP-03-2003 | King George County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock | Dominion Septic, Inc | 1942001350 | Mike | Cook | 1.000000 |  | Puraflo | None | Pump | Distribution Box | Aggregate Trench |  |  | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | ["Attached Growth Medium","Control Operation","Distribution Pump Operation","Level Sensor Operation","SludgeScum Accumulation"] | [18 empty] | [Comments]: replaced alarm float | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/06/2020 | 05:29 AM
01/10/2020 |  | Reportable Incident | 2006-143-0021 | Henrico County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Henrico |  |  |  |  | 1.000000 |  |  | None | Pump | Distribution Box | [23 empty] | [Comments]: Blower alarm, rebuilt blower w/ rebuild kit. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 01/15/2020 | 10:52 AM
03/03/2020 |  | RoutineScheduled |  | Warren | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Lord Fairfax | Onsite Wastewater Services - May Supply | 1942001022 | Sara | Tusing | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/28/2021 | 05:41 AM
12/09/2020 |  | Routine/Scheduled |  | Warren | This AOSS should now return to normal function after having provided the above state routine maintenance. | Pending Review | EHD - Lord Fairfax | POWELLS PLUMBING, INC. | 1942001036 | Kurt | Holthaus | 1.000000 | 1000 | Puraflo |  | Pump | Distribution Box | Aggregate Trench |  |  | ["Dispersal System Operation","Effluent Screens","Sludge/Scum Accumulation"] | ["Dispersal System Operation","Effluent Screens","Sludge/Scum Accumulation"] | N/A | [17 empty] | Real estate sale inspection - Two header lines were repaired, serviced effluent screen(s), pumped septic tank and pump chamber. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 12/30/2020 | 01:55 PM
11/12/2020 |  | Follow-Up |  | Loudoun | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 | Pending Review | EHD - Loudoun | Mckim Construction | 1942001330 | Michelle | Mckim | 1.000000 |  | none | none | Gravity | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected | Installed concrete riser \on septic tank and installed new d-box. LCH inspected. At this time the septic system is in working condition | This AOSS is functioning as designed and in accordance with the performance/maintanence requirements of 12VAC5-613 |  | 04/14/2021 | 04:27 PM
01/14/2020 |  | Follow-Up | 061-16-250 | Fauquier County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Rappahannock-Rapidan | Dominion Septic, Inc | 1942001068 | David | Stewart | 5.000000 |  | Bio Barrier | Bio Barrier | Pump | Drip | Drip Tubing |  |  | ["SludgeScum Accumulation"] | ["SludgeScum Accumulation"] | [18 empty] | [Comments]: Primary and secondary septic tanks pumped out today by Butler & Eicher. Repaired leak in zone 2, then checked various lift stations for infiltration. Verified huge leak at inlet pipe for Tancor and a hung toilet, minor leaks at other lift stations. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/25/2020 | 07:16 AM
06/12/2020 | Alternative | RoutineScheduled | 166-15-133 | Northumberland | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers |  |  | joel | pinnix | [9 empty] | [] | [] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
03/16/2020 |  | Routine, Scheduled |  | Nelson County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Blue Ridge | CLARK, MICHAEL J | 1934000023 | MICHAEL | CLARK |  |  | Septic Tank Only | Septic Tank Only | None | None | None | None |  |  | ["Auxiliary Filter","BlowerCompressorAerator Operation","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor Operation","SludgeScum Accumulation"] | [19 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/17/2020 | 04:21 AM
02/17/2020 |  | RoutineScheduled | 08-113-152 | Buchanan | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Cumberland Plateau | Septic Inc |  | Denny | Deel |  |  | Whitewater |  | Gravity |  | Discharge | Chlorination | 200.000000 | ["BlowerCompressorAerator Operation","Control Operation","Disinfection"] | ["BlowerCompressorAerator Operation","Control Operation","Disinfection"] | NA | Musty | Clear | [16 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  |  | 12:00 AM
07/27/2020 | Alternative | Routine/Scheduled | 157-13-0114 | Mathews | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Three Rivers | Farmer's Septic Service, Inc. | 1942001191 | Allen | Farmer | 1.000000 | [8 empty] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A | [17 empty] | Serviced system. Checked the pump, panel, & floats (ok). Cleaned the filter in the Clearstream. Changed the diffuser in the Clearstream and changed the filter in the aerator. The septic tank needs additional risers on it so it can be properly inspected in the future. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 07/27/2020 | 12:00 PM
07/14/2020 |  | Routine/Scheduled | 14-142-0189 | Hanover | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Chickahominy | Madison Environmental LLC | 1942001333 | Larry | Madison, Jr. |  |  | Orenco Advantex |  | Pump |  |  |  |  | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump","Sludge/Scum Accumulation"] | ["Attached Growth Medium","Control Operation","Dispersal System Operation","Distribution Pump Operation","Effluent Screens","Level Sensor (Float) Operation","Recirculation Pump","Sludge/Scum Accumulation"] | N/A | [18 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 07/14/2020 | Jan 1 1900 2:30AM
09/17/2020 |  | Reportable Incident |  | Southampton | This AOSS should now return to normal function after having provided the above state routine maintenance | Pending Payment | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU | [6 empty] | ["Blower/Compressor/Aerator Operation","Control Operation"] | ["Blower/Compressor/Aerator Operation","Control Operation"] | N/A | [17 empty] | Replaced the aerator | This AOSS should now return to normal function after having provided the above state routine maintenance |  | 09/17/2020 | Jan 1 1900 9:00AM
09/30/2020 |  | RoutineScheduled |  | Augusta | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Payment | EHD - Central Shenandoah | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Attached Growth Medium" ,"Auxiliary Filter"] | ["BlowerCompressorAerator Operation" ,"Control Operation" ,"Attached Growth Medium" ,"Auxiliary Filter"] | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/26/2021 | 09:04 AM
07/15/2020 |  | Reportable Incident |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | SES MidAtlantic LLC | 1942001203 | James | Green | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Installed new compressor. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/15/2021 | 09:00 AM
03/19/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Fairfax | SEAMON, CHARLIE L | 1942001108 | CHARLIE | SEAMON |  |  | Septic Tank Only | Microfast | Pump | Distribution Box | Aggregate Trench | None | [11 empty] | 03/19/2020 |  | 25.000000 | [5 empty] | Attached to this report |  | [Comments]: Performance Inspection and sample: Microfast pump to drainfield. Septic-6"sludge 0"scum/Microfast-0"sludge/Pump tank-0"sludge. No pump out needed at this time.Blower air filter cleaned. Counts:Peak- 5/High-7/P1-43 ETM-1h 13m/P2-36 ETM-1h 7m. No breakout or spongy areas on the drainfield. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 04/08/2020 | Jan 1 1900 4:53PM
05/05/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | SES MidAtlantic LLC | 1942001203 | James | Green | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  | ["Effluent Screens"] | ["Effluent Screens"] | YES | [15 empty] | Will be sent separately | Inspected | Components marked Fully Inspected are done so at the request of the LCHD but do not include the uncovering or physical removal of buried or submerged components such as pumps, floats, diffusers etc, nor inspection of the interior or exterior of tanks, boxes, valves or other buried components for leaks, structural defects or other abnormalities. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/15/2021 | 09:00 AM
07/21/2020 |  | RoutineScheduled | 181-08-0154 | Rockbridge | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Central Shenandoah | Onsite Wastewater Services - May Supply | 1942001022 | Sara | Tusing | 1.000000 |  | Orenco Advantex | none | Pump | Gravity | Drip | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 05/28/2021 | 05:41 AM
03/04/2020 |  | Routine, Scheduled | 131-STS-92952 | Northampton County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Approved | EHD - Eastern Shore | DUER, PETE C | 1942001051 | PETE | DUER | 1.000000 | 1250 | Septic Tank Only | Puraflo | Pump | None | None | None |  | ["None"] | ["None"] | [18 empty] | [Comments]: Aoss Inspection. | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 03/27/2020 | 02:13 PM
02/17/2020 |  | Routine, Scheduled |  | Fairfax County | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Paid | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | Biomicrobics MicroFAST |  | Pump | Drip | Drip Tubing | UV Light |  | ["BlowerCompressorAerator Operation"] | ["BlowerCompressorAerator Operation"] |  | Good | Good | [15 empty] | [Comments]: Pump Amps 9.15 ETM 761h 13m Cycles 7501Water Meter Reading 354400Septic Sludge 7" Scum 0ATU Sludge 14" Scum 0Pump Sludge 1" Scum 0 | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 02/17/2020 | Jan 1 1900 5:50PM
06/15/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/27/2021 | 01:26 PM
09/22/2020 |  | Reportable Incident |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | SES MidAtlantic LLC | 1942001203 | James | Green | 1.000000 |  | Delta Environmental Products, DF Series | none | Pump | Gravity | Drip | Not Applicable |  | ["Dispersal System Operation"] | ["Dispersal System Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Replaced Zoner. | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/15/2021 | 09:00 AM
08/05/2020 |  | RoutineScheduled |  | Shenandoah | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Payment | EHD - Lord Fairfax | Cubbage Septic Solutions LLC | 1942001021 | Harrison | Cubbage | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Pressure | Drip | Not Applicable |  | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | ["Auxiliary Filter" ,"BlowerCompressorAerator Operation" ,"Control Operation"] | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/26/2021 | 09:04 AM
07/22/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Review | EHD - Loudoun | Catoctin Environmental | 1942001137 | Cameron | Creighton | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 05/27/2021 | 01:26 PM
06/01/2020 |  | RoutineScheduled |  | Loudoun | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 | Pending Payment | EHD - Loudoun | Great Falls Septic Service, Inc | 1942001301 | Josh | Hott | 1.000000 |  | none | none | Pump | Gravity | Trenches | Not Applicable |  |  |  | NA | [15 empty] | Will be sent separately | Inspected |  | This alternative discharging system is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-640 |  | 04/27/2021 | 11:51 AM
08/10/2020 |  | Routine/Scheduled |  | Isle Of Wight | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Western Tidewater | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump | Distribution Box |  | UV Light |  | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  |  | 7.000000 | 3.000000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 08/10/2020 | Jan 1 1900 8:00AM
08/10/2020 |  | RoutineScheduled | 124-STS-2379 | Fairfax | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Fairfax | Dominion Septic, Inc | 1942001125 | Tom | Jackson | 1.000000 |  | Biomicrobics MicroFAST | none | Pump | Gravity | Drip | Not Applicable |  | ["Distribution Pump Operation" ,"Auxiliary Filter"] | ["Auxiliary Filter" ,"Distribution Pump Operation"] | NA | [15 empty] | Will be sent separately | Inspected | Pump tank in high level, but alarm light not on. Replaced alarm bulb on top of panel. Flow to drip field was almost completely stopped due to very dirty disc filters. Repaired wiring on backwash solenoid #1 (rodent damage), and replaced backwash solenoid #2. A little smoke seen curling up from the heater strip due to damage by rodents. Replaced heater strip and advised owner to take steps such as traps or poison to limit damage. Flow restored to zones. Found solenoid for zone 2 (closer to house) stuck on, replaced it. Drip rates higher than in the past, possibly due to check valves not closing completely. Did not see any effluent surfacing. Biomicrobics atu panel did not alarm when blower was shut off. Red light on Mitsubishi processor came on briefly during testing and cycle start switch did not work. Started working again while testing panel with American Mfg tech support. Green "power on" led not lit. Control panel is 20 years old and probably headed towards failure. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 04/13/2021 | Jan 1 1900 11:22AM
12/01/2020 |  | RoutineScheduled | 69150108 | Frederick | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. | Approved | EHD - Lord Fairfax | Larry Royston Septic Service, LLC | 2705110225 | Larry | Royston | [9 empty] | ["None"] | ["None"] | YES | [16 empty] | Inspected |  | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613. |  | 12/21/2020 | 12:00 AM
05/15/2020 |  | RoutineScheduled | 171-05-0560 | Pittsylvania | This AOSS should now return to normal function after having provided the above state routine maintenance. | Approved | EHD - Pittsylvania-Danville | Virginia Septic Service | 1942001512 | iain | Waugh | 1.000000 | 1500 | Puraflo |  | Pump | Gravity | Trenches | Not Applicable |  | [] | [] | NA | [16 empty] | Inspected | Sludge level-1" scum layer on top-12-24" sludge on bottom in Septic tank - Pump tank 4" sludge, Turned peat media in all pods good condition for age, tested float switches, alarm and pump. Found septic tank level at mid seam, Advised owner to preform leak down test over next few weeks to determine how bad. pump ct 94356 pump time 314.35hrs, pump draw 10.5A running to 11.76amp on start. Retuned 8-6-20 to replace float, effluent filter, pump septic tank, and seal midseam of tank with FOUTZ septic. pump time 319.33 hrsa, 105661ct, replaced all 3 floats. Owner confirmed tank holding water weeks after repair. | This AOSS should now return to normal function after having provided the above state routine maintenance. |  | 08/28/2020 | 09:30 AM
07/23/2020 |  | Routine/Scheduled |  | Chesapeake | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 | Pending Payment | EHD - Chesapeake | R & K Septic, Inc. | 1942001066 | Mary | VanHolten |  |  | Clearstream ATU |  | Pump | Drip | Elevated Sand Mound | UV Light |  | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | ["Blower/Compressor/Aerator Operation","Control Operation","Disinfection","Dispersal System Operation","Distribution Pump Operation","Level Sensor (Float) Operation","Sludge/Scum Accumulation"] | N/A |  | 2.11 | 7.720000 | 3.500000 | [14 empty] | This AOSS is functioning as designed and in accordance with the performance/maintenance requirements of 12VAC5-613 |  | 07/23/2020 | Jan 1 1900 10:30AM
04/27/2020 |  | Routine, Scheduled | 124-STS-2379 | Fairfax | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. | Approved | EHD - Fairfax | SES Mid Atlantic | 1942001203 | Michael | Green |  |  | EZ Treat Sandfilter |  |  |  |  | UV Light |  | ["Blower/Compressor/Aerator Operation","Disinfection","Effluent Screens"] | ["Blower/Compressor/Aerator Operation","Disinfection","Effluent Screens"] |  | Good | Tan | 6.370000 | 1.340000 |  |  |  | 04/27/2020 | Discharge Outlet | 5.000000 |  | 435.000000 | 43.000000 |  |  |  |  | Pump Amps 11.21 ETM 6.81 Cycles 23373 Pump Amps 9.67 Septic Sludge 3" Scum 1" ATU Sludge 2" Scum 0 Pump Sludge 0 Scum 0 | This alternative discharging system is not functioning as designed or in accordance with the performance/maintenance requirements of 12VAC5-640. |  | 04/27/2020 | Jan 1 1900 1:37PM