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September 1, 2026



Mr. David Simon
Product Specialist
Valencia Pipe Company

Dear Mr. Simon,

On June 19th, 2026 you submitted documentation on the following septic tanks for approval by the Virginia Department of Health, Office of Environmental Health, Division of Water and Wastewater Services. 

	Model Number
	Description

	87-750LO-G-2-2
	750 gallon low profile dual compartment septic tank

	87-1000LO-G-2-2
	1000 gallon low profile dual compartment septic tank

	87-1250LO-G-2-2
	1250 gallon low profile dual compartment septic tank

	87-1500LO-G-2-2
	1500 gallon low profile dual compartment septic tank



The subject tanks do not meet the following Sewage Handling and Disposal Regulations (12VAC5-610-815) criteria:
	1-2 inch difference between inverts of inlet and outlet structures (3 inches provided)
	4-8 foot liquid depth (40 inches provided)
	Minimum 12 inches freeboard (10-11.5 inches provided, varies by model)
	Inlet structure extension 6-8 inches below normal liquid level (11 inches provided)
	Outlet structure extension 8-10 inches above normal liquid level (6 inches provided)
	Inside length to normal liquid depth to width ratio between 2:1:1 and 3:1:1 (varies by model)

However, after reviewing the information provided by VPC global, the Office of Environmental Health Services approves the tank for use in Virginia when used with an NSF-certified effluent filter. 


	Sincerely,
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Ryder Bunce
Environmental Technical Services Manager
	Division of Onsite Water and Wastewater Services
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