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	July 1, 2024



Mr. Samuel C Hampsher-Monk
compliance@vpcglobal.com
VPCglobal.com

Dear Mr. Hampsher-Monk,

On May 16, 2024 you submitted documentation on the following septic tanks for approval by the Virginia Department of Health, Office of Environmental Health, Division of Water and Wastewater Services. 

	Model Number
	Description

	87-41718
	1000 Gallon Single Compartment Septic Tank Yellow

	87-41720
	1000 Gallon Two Compartment Septic Tank Yellow

	87-41758
	1500 Gallon Single Compartment Septic Tank Yellow

	87-41760
	1500 Gallon Two Compartment Septic Tank Yellow



The subject tanks do not meet the following Sewage Handling and Disposal Regulations (12VAC5-610-815) criteria:
	1-2 inch difference between inverts of inlet and outlet structures (3 inches provided)

However, after reviewing the information provided by VPC global, the Office of Environmental Health Services approves the tank for use in Virginia when used with an NSF-certified effluent filter. 


	Sincerely,

	
	
Lance Gregory
Director
	Division of Onsite Water and Wastewater Services
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